04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508809_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-337376_7SAREPTA% | Single Phase Fault with Stuck Breaker on 7SAREPTA% (337376) 345.0 kV bus a. Apply single-phase fault on 7SAREPTA% (337376) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to 7EL (337562) 345.0 kV bus CKT 1 b. 2. Disconnect 1EL (337565) 13.8 kV bus to trip transformer at 1EL DORADO2 13.8 kV bus b. 3. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-507760_SW | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508841_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508808_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508808) 138.0 kV bus a. Apply single-phase fault on LONGWD (508808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-337561_8EL | Single Phase Fault with Stuck Breaker on 8EL (337561) 500.0 kV bus a. Apply single-phase fault on 8EL (337561) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 b. 2. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-337363_3SAREPTA! | Single Phase Fault with Stuck Breaker on 3SAREPTA! (337363) 115.0 kV bus a. Apply single-phase fault on 3SAREPTA! (337363) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-507759_SW | Single Phase Fault with Stuck Breaker on SW (507759) 138.0 kV bus a. Apply single-phase fault on SW (507759) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508840_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508840) 138.0 kV bus a. Apply single-phase fault on WILKES (508840) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus b. 2. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508806_LIEBERM4 | Single Phase Fault with Stuck Breaker on LIEBERM4 (508806) 138.0 kV bus a. Apply single-phase fault on LIEBERM4 (508806) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to LONGWD (508808) 138.0 kV bus CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-338440_8PANDA% | Single Phase Fault with Stuck Breaker on 8PANDA% (338440) 500.0 kV bus a. Apply single-phase fault on 8PANDA% (338440) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 1 b. 2. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-337539_3EL | Single Phase Fault with Stuck Breaker on 3EL (337539) 115.0 kV bus a. Apply single-phase fault on 3EL (337539) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1EL (337564) 13.8 kV bus to trip transformer at 1EL DORADO1 13.8 kV bus b. 2. Disconnect 1EL (337566) 13.8 kV bus to trip transformer at 1EL DORADO3 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-507711_ARSHILL4 | Single Phase Fault with Stuck Breaker on ARSHILL4 (507711) 138.0 kV bus a. Apply single-phase fault on ARSHILL4 (507711) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 b. 2. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508562_PIRKEY | Single Phase Fault with Stuck Breaker on PIRKEY (508562) 138.0 kV bus a. Apply single-phase fault on PIRKEY (508562) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 kV bus to HALLSVLS4 (508595) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from PIRKEY (508562) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511468_LES-7-511456_OKU-7_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511468_LES-7-760938_G17-171-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511468_LES-7-511467_LES-4_3Winding | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511468_LES-7-587744_G16-091-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511456_OKU-7-762467_G18-015-TAP_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511456_OKU-7-511565_OKLAUN_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus OKLAUN (511565) 345.0 kV bus b. 2. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_587744_G16-091-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-091-TAP (587744) 345.0 kV a. Apply fault on G16-091-TAP (587744) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_760938_G17-171-TAP-511568_TERRYRD7_Ckt1 | 3 Phase fault on G17-171-TAP (760938) 345.0 kV a. Apply fault on G17-171-TAP (760938) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511468_LES-7_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511537_ARTVLTP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 b. 2. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 3. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 c. 2. Reclose branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 d. 2. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511439_LWSTAP_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511494_COMMTAP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511437_COMANC-4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511466_LES-2_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#1-1 (511416) to trip transformer at LES#1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511423_FLE_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511467_LES-4-511486_ELGINJT4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515800_GRACMNT7-514801_MINCO_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515800_GRACMNT7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515800_GRACMNT7-515802_GRACMNT4_3Winding | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRCMNT11 (515801) to trip transformer at GRCMNT11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_762467_G18-015-TAP-762216_G17-151TAP_Ckt1 | 3 Phase fault on G18-015-TAP (762467) 345.0 kV a. Apply fault on G18-015-TAP (762467) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511568_TERRYRD7-515136_SUNNYSD7_Ckt1 | 3 Phase fault on TERRYRD7 (511568) 345.0 kV a. Apply fault on TERRYRD7 (511568) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511439_LWSTAP-511488_112GORE4_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 b. 2. Drop load from bus RPPAPER4 (511512) 138.0 kV bus b. 3. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 c. 2. Reclose branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 d. 2. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511439_LWSTAP-511431_LWS_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus LWS (511431) 138.0 kV bus b. 2. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511466_LES-2-511503_LAW_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511466_LES-2-511487_ELGINJT2_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 3. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 b. 4. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 5. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 6. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 b. 7. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 8. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 c. 3. Reclose branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 c. 4. Reclose branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 d. 3. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 d. 4. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514801_MINCO-516096_NORMHLL7_Ckt1 | 3 Phase fault on MINCO (514801) 345.0 kV a. Apply fault on MINCO (514801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560078_G16-037-TAP-511553_CHISHOLM7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt1 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt2 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-511468_LES-7 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-511456_OKU-7 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-511467_LES-4 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LES#5-1 (511411) 13.8 kV bus to trip transformer at LES#5-1 13.8 kV bus b. 2. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to SHERID4 (511474) 138.0 kV bus CKT 1 b. 3. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 4. Trip branch from SHERID4 (511474) 138.0 kV bus to ARTVLTP4 (511537) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515800_GRACMNT7 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a. Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-511466_LES-2 | Single Phase Fault with Stuck Breaker on L.E.S.-2 (511466) 69.0 kV bus a. Apply single-phase fault on L.E.S.-2 (511466) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-S2 (511470) 69.0 kV bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 kV bus to LAW (511503) 69.0 kV bus CKT 1 b. 5. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-N2 (511469) 69.0 kV bus CKT 1 b. 6. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 7. Trip branch from LGORE-N2 (511469) 69.0 kV bus to FT.SILL2 (511461) 69.0 kV bus CKT 1 b. 8. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 9. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 10. Trip branch from FT.SILL2 (511461) 69.0 kV bus to PO.HILL2 (511473) 69.0 kV bus CKT 1 b. 11. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 12. Trip branch from PO.HILL2 (511473) 69.0 kV bus to ELGINJT2 (511487) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-514801_MINCO | Single Phase Fault with Stuck Breaker on MINCO (514801) 345.0 kV bus a. Apply single-phase fault on MINCO (514801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515802_GRACMNT4 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-300069_5CHOTEAU1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512656_GRDA1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-301344_5CDRCRST_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512629_DRYGULCH5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512626_MAID_3Winding | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512635_KERR_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512635_KERR_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512648_MAID-512656_GRDA1_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-512648_MAID_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. 2. Reclose branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 c. 3. Reclose branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 c. 4. Reclose branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. 2. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 d. 3. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 d. 4. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-513570_CHOUTEAUCRK516100_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-512671_HUNT_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 2. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 3. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-512700_WAGNOR_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512650_GRDA1-512750_TONECE7_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300069_5CHOTEAU1-301348_5CHOTEAU2_CktZ1 | 3 Phase fault on 5CHOTEAU1 (300069) 161.0 kV a. Apply fault on 5CHOTEAU1 (300069) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512629_DRYGULCH5-512654_PENSA_Ckt1 | 3 Phase fault on DRYGULCH5 (512629) 161.0 kV a. Apply fault on DRYGULCH5 (512629) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512714_KANSATP5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt2 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512654_PENSA_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512771_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512635_KERR-512770_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512638_CATSAGR5-512627_COLINS_Ckt1 | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 c. 2. Reclose branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 d. 2. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512638_CATSAGR5-509790_CATOOSA4_3Winding | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CATTER1 (512833) to trip transformer at CATTER1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512626_MAID-512671_HUNT_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 c. 2. Reclose branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 c. 3. Reclose branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 c. 4. Reclose branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 c. 5. Reclose branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 d. 2. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 d. 3. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 d. 4. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 d. 5. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512626_MAID-512648_MAID_3Winding | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512626_MAID-512683_AMERCAST_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 b. 2. Drop load from bus REDDEN (512698) 69.0 kV bus b. 3. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 b. 4. Drop load from bus AMERCAST (512683) 69.0 kV bus b. 5. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 c. 2. Reclose branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 c. 3. Reclose branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 d. 2. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 d. 3. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512700_WAGNOR-512697_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512700_WAGNOR-512640_OKAYGR_Ckt1 | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513570_CHOUTEAUCRK516100-512651_CLARMR_Ckt1 | 3 Phase fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV a. Apply fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301344_5CDRCRST-512648_MAID_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301344_5CDRCRST-301345_2CDRCRST_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301344_5CDRCRST-512655_TAHLQH_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300739_7BLACKBERRY-300949_7JASPER_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300739_7BLACKBERRY-532797_WOLFCRK7_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300739_7BLACKBERRY-532793_NEOSHO_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300741_5SPORTSMAN-301348_5CHOTEAU2_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt2 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509852_TNO--7-510406_NES-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509852_TNO--7-512694_CLEVLND7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509852_TNO--7-509755_WEKIWA-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512654_PENSA-512669_KETCHUM5_Ckt1 | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512654_PENSA-512628_PENSA_3Winding | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PENSA (512841) to trip transformer at PENSA 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509790_CATOOSA4-509752_INOLATP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509790_CATOOSA4-509835_TERNITP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512640_OKAYGR-505560_FT_Ckt1 | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512640_OKAYGR-512646_OKAYGR_3Winding | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OKAY1 (512848) to trip transformer at OKAY1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512697_WAGNOR-512700_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512697_WAGNOR-512801_WAGCTY12_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 b. 2. Drop load from bus WAGCTY22 (512759) 69.0 kV bus b. 3. Drop load from bus WAGCTY12 (512801) 69.0 kV bus b. 4. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 c. 2. Reclose branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 d. 2. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512697_WAGNOR-300958_2HIGHLND_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 b. 2. Drop load from bus 2WAGNERW (300972) 69.0 kV bus b. 3. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 b. 4. Drop load from bus 2COWETA (300955) 69.0 kV bus b. 5. Drop load from bus 2HIGHLND (300958) 69.0 kV bus b. 6. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 c. 2. Reclose branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 c. 3. Reclose branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 d. 2. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 d. 3. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512697_WAGNOR-512690_WAGNRTP2_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512651_CLARMR-510396_NES-4_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR4 (512813) to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 c. 2. Reclose branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 d. 2. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512651_CLARMR-512679_CLARMR_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR2 (512815) to trip transformer at CLARMR2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301345_2CDRCRST-301344_5CDRCRST_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301345_2CDRCRST-513059_HULBERKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 b. 2. Drop load from bus 2PEGGS (300962) 69.0 kV bus b. 3. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 b. 4. Drop load from bus 2HULBERT (300975) 69.0 kV bus b. 5. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 c. 2. Reclose branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 c. 3. Reclose branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 d. 2. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 d. 3. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_301345_2CDRCRST-513062_TAHLWESTKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 b. 2. Drop load from bus 2LOWERY (300960) 69.0 kV bus b. 3. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 b. 4. Drop load from bus 2SLEEPYH (300968) 69.0 kV bus b. 5. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 c. 2. Reclose branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 c. 3. Reclose branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 d. 2. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 d. 3. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512655_TAHLQH-515956_7CLANS_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512655_TAHLQH-513044_BRIGSKM_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300949_7JASPER-300045_7MORGAN_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300949_7JASPER-300794_5LAMAR_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 b. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 c. 2. Reclose branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 d. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532797_WOLFCRK7-532794_ROSEHIL7_Ckt1 | 3 Phase fault on WOLFCRK7 (532797) 345.0 kV a. Apply fault on WOLFCRK7 (532797) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509755_WEKIWA-7-514803_SOONER_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510406_NES-7-510380_DELWARE7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512694_CLEVLND7-560056_G15-066T_Ckt1 | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512694_CLEVLND7-300138_4CLEVLND_3Winding | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CLEVLND1 (512817) to trip transformer at CLEVLND1 13.8 kV bus b. 2. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509895_TNO2-4-509817_TNO--4_Ckt1 | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509895_TNO2-4-509852_TNO--7_3Winding | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt1 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513591_HERRON-513596_IGLOOV_3Winding | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 b. 2. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt2 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512671_HUNT-512656_GRDA1_3Winding | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 b. 3. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 4. Drop load from bus HUNT (512671) 69.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512671_HUNT-512810_PRYORC12_Ckt1 | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 b. 2. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 3. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 b. 4. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 5. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 c. 2. Reclose branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 c. 3. Reclose branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 d. 2. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 d. 3. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-504201_GENTRY_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509817_TNO--4-509842_CDC-WT_Ckt1 | 3 Phase fault on T.NO.--4 (509817) 138.0 kV a. Apply fault on T.NO.--4 (509817) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512648_MAID | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a. Apply single-phase fault on MAID (512648) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 b. 2. Trip branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 3. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 4. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 5. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 6. Trip branch from NWMAID5 (512757) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 7. Drop load from bus WMAIN (512742) 161.0 kV bus b. 8. Trip branch from WMAIN (512742) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-300740_7SPORTSMAN | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345.0 kV bus a. Apply single-phase fault on 7SPORTSMAN (300740) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 5SPORTSMAN (300741) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-513596_IGLOOV | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a. Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Disconnect IGLOTER1 (513592) 13.2 kV bus to trip transformer at IGLOTER1 1 13.200 (513592) 13.2 kV bus b. 3. Trip branch from IGLOOV1 (513593) 161.0 kV bus to HERRON (513591) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512635_KERR | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 b. 4. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512638_CATSAGR5 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 kV bus to 5ELMCRK (300993) 161.0 kV bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 kV bus to COLINS (512627) 161.0 kV bus CKT 1 b. 5. Trip branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512626_MAID | Single Phase Fault with Stuck Breaker on MAID (512626) 69.0 kV bus a. Apply single-phase fault on MAID (512626) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 kV bus to AMERCAST (512681) 69.0 kV bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 kV bus to CPPTAP (512661) 69.0 kV bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 kV bus to PRYORCHEM2 (512699) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 kV bus to AIRPROD2 (512687) 69.0 kV bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 kV bus to HUNT (512671) 69.0 kV bus CKT 1 b. 9. Disconnect MAITER1 (512836) 13.2 kV bus to trip transformer at MAITER1 1 13.200 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512700_WAGNOR | Single Phase Fault with Stuck Breaker on WAGNOR (512700) 161.0 kV bus a. Apply single-phase fault on WAGNOR (512700) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR1 (512818) 13.8 kV bus to trip transformer at WAGNOR1 13.8 kV bus b. 2. Trip branch from WAGNOR (512700) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-301344_5CDRCRST | Single Phase Fault with Stuck Breaker on 5CDRCRST (301344) 161.0 kV bus a. Apply single-phase fault on 5CDRCRST (301344) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to LOCSTGVKM (513050) 161.0 kV bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 4. Trip branch from 5CDRCRST (301344) 161.0 kV bus to 2CDRCRST (301345) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-300739_7BLACKBERRY | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345.0 kV bus a. Apply single-phase fault on 7BLACKBERRY (300739) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-300741_5SPORTSMAN | Single Phase Fault with Stuck Breaker on 5SPORTSMAN (300741) 161.0 kV bus a. Apply single-phase fault on 5SPORTSMAN (300741) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 b. 2. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 7SPORTSMAN (300740) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512654_PENSA | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a. Apply single-phase fault on PENSA (512654) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 3. Disconnect PENSA (512841) 13.8 kV bus to trip transformer at PENSA 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509790_CATOOSA4 | Single Phase Fault with Stuck Breaker on CATOOSA4 (509790) 138.0 kV bus a. Apply single-phase fault on CATOOSA4 (509790) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 b. 2. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512651_CLARMR | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CLARMR4 (512813) 13.8 kV bus to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 kV bus to OOLOGAHKM (513124) 138.0 kV bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 kV bus to N.E.S.-4 (510396) 138.0 kV bus CKT 1 b. 5. Disconnect CLARMR2 (512815) 13.8 kV bus to trip transformer at CLARMR2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512655_TAHLQH | Single Phase Fault with Stuck Breaker on TAHLQH (512655) 161.0 kV bus a. Apply single-phase fault on TAHLQH (512655) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 kV bus to 7CLANS (515956) 161.0 kV bus CKT 1 b. 3. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-532797_WOLFCRK7 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a. Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 b. 2. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512671_HUNT | Single Phase Fault with Stuck Breaker on HUNT (512671) 69.0 kV bus a. Apply single-phase fault on HUNT (512671) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 kV bus to MAIDTP2 (512625) 69.0 kV bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 kV bus to GRDA1 (512727) 69.0 kV bus CKT 1 b. 3. Disconnect GRDA1 (512816) 13.8 kV bus to trip transformer at GRDA1 1 13.8 kV bus b. 4. Trip branch from HUNT (512671) 69.0 kV bus to PRY0RC22 (512639) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 6. Trip branch from PRY0RC22 (512639) 69.0 kV bus to PRYORC32 (512622) 69.0 kV bus CKT 1 b. 7. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 8. Trip branch from PRYORC32 (512622) 69.0 kV bus to PRYORC12 (512810) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509817_TNO--4 | Single Phase Fault with Stuck Breaker on T.NO.--4 (509817) 138.0 kV bus a. Apply single-phase fault on T.NO.--4 (509817) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-755000_WWDBORDT_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515375_WWRDEHV7-515376_WWRDEHV4_3Winding | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV31 (515795) to trip transformer at WWDEHV31 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt2 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt1 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515852_DGRASSE7-515853_DGRASSE4_3Winding | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt2 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt1 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_755000_WWDBORDT-525832_TUCO_INT_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_755000_WWDBORDT-511553_CHISHOLM7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515376_WWRDEHV4-515533_REDCLFT4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 c. 2. Reclose branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 d. 2. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515376_WWRDEHV4-515375_WWRDEHV7_3Winding | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV21 (515799) to trip transformer at WWDEHV21 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515376_WWRDEHV4-514785_WOODWRD4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 b. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 c. 2. Reclose branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 d. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511553_CHISHOLM7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511553_CHISHOLM7-511557_CHISHOLM6_3Winding | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515853_DGRASSE4-520436_ROSEVLY4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515853_DGRASSE4-514795_KNOBHIL4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515853_DGRASSE4-515852_DGRASSE7_3Winding | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515853_DGRASSE4-520999_MOORLND4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560078_G16-037-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511557_CHISHOLM6-511541_SWEETWT6_Ckt1 | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511557_CHISHOLM6-511458_ELKCTY-4_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 b. 2. Disconnect bus at ELKC2-1 (511482) to trip transformer at ELKC2-1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511557_CHISHOLM6-511553_CHISHOLM7_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515375_WWRDEHV7 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345.0 kV bus a. Apply single-phase fault on WWRDEHV7 (515375) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515407_TATONGA7 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345.0 kV bus a. Apply single-phase fault on TATONGA7 (515407) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515852_DGRASSE7 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345.0 kV bus a. Apply single-phase fault on DGRASSE7 (515852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-560071_G16-003-TAP | Single Phase Fault with Stuck Breaker on G16-003-TAP (560071) 345.0 kV bus a. Apply single-phase fault on G16-003-TAP (560071) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 b. 2. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-755000_WWDBORDT | Single Phase Fault with Stuck Breaker on WWDBORDT (755000) 345.0 kV bus a. Apply single-phase fault on WWDBORDT (755000) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515376_WWRDEHV4 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138.0 kV bus a. Apply single-phase fault on WWRDEHV4 (515376) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 kV bus to IODINE-4 (514796) 138.0 kV bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 kV bus to REDCLFT4 (515533) 138.0 kV bus CKT 1 b. 4. Disconnect WWDEHV31 (515795) 13.8 kV bus to trip transformer at WWDEHV31 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-511553_CHISHOLM7 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345.0 kV bus a. Apply single-phase fault on CHISHOLM7 (511553) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 b. 2. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515497_MATHWSN7 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345.0 kV bus a. Apply single-phase fault on MATHWSN7 (515497) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-539801_THISTLE7 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345.0 kV bus a. Apply single-phase fault on THISTLE7 (539801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515677_BADGER | Single Phase Fault with Stuck Breaker on BADGER (515677) 345.0 kV bus a. Apply single-phase fault on BADGER (515677) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511541_SWEETWT6-511557_CHISHOLM6_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2019-013 (763541) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511541_SWEETWT6-523777_WHEELER_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523777_WHEELER-523771_GRAPEVINE_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523777_WHEELER-511541_SWEETWT6_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523777_WHEELER-523776_WHEELER_3Winding | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WHEELER_TR1113.200 (523774) to trip transformer at WHEELER_TR1113.200 (523774) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_511553_CHISHOLM7-755000_WWDBORDT_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_755000_WWDBORDT-515375_WWRDEHV7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514795_KNOBHIL4-514794_KNOBHIL2_3Winding | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt2 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt1 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520436_ROSEVLY4-520430_NOELSW_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520436_ROSEVLY4-520601_AVARD_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AVARD (520601) 138.0 kV bus b. 2. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-520848_CDRDLTP4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 c. 2. Reclose branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 d. 2. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-514778_CLEOCOR4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 b. 2. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 3. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 4. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 c. 2. Reclose branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 d. 2. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-515785_WINDFRM4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-520553_SEILING4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SEILING4 (520553) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-520462_ASPEN_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus ASPEN (520462) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-521197_CRTSJCT2_3Winding | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MLNDTERT (521180) to trip transformer at MLNDTERT 2.4000 (521180) 2.4000000953674316 kV bus b. 2. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520999_MOORLND4-520957_IODINE_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus IODINE (520957) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_539801_THISTLE7-539638_FLATRDG4_3Winding | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at THISTLE (539802) to trip transformer at THISTLE T1 13.8 kV bus b. 2. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_520430_NOELSW-521200_DRIFTWD4_Ckt1 | 3 Phase fault on NOELSW (520430) 138.0 kV a. Apply fault on NOELSW (520430) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 2. Reclose branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 3. Reclose branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 2. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514794_KNOBHIL2-514795_KNOBHIL4_3Winding | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514794_KNOBHIL2-514792_ALVAOGE2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514794_KNOBHIL2-515371_HELENAT2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 b. 2. Drop load from bus CZYCRVT2 (515560) 69.0 kV bus b. 3. Drop fixed shunt from bus CZYCRVT2 (515560) 69.0 kV bus b. 4. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 b. 5. Drop load from bus SALINE (514716) 69.0 kV bus b. 6. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 c. 2. Reclose branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 c. 3. Reclose branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 d. 2. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 d. 3. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt1 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt2 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_521200_DRIFTWD4-520430_NOELSW_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 2. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 4. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 5. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 6. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 2. Reclose branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 3. Reclose branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 2. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 3. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_521200_DRIFTWD4-520432_BYRONTP4_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_521200_DRIFTWD4-521201_DRIFTWD2_3Winding | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DRFTWDTERT (521185) to trip transformer at DRFTWDTERT 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-515853_DGRASSE4 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138.0 kV bus a. Apply single-phase fault on DGRASSE4 (515853) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-514795_KNOBHIL4 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138.0 kV bus a. Apply single-phase fault on KNOBHIL4 (514795) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Disconnect KNOBHIL1 (515732) 13.2 kV bus to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-520436_ROSEVLY4 | Single Phase Fault with Stuck Breaker on ROSEVLY4 (520436) 138.0 kV bus a. Apply single-phase fault on ROSEVLY4 (520436) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-520999_MOORLND4 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138.0 kV bus a. Apply single-phase fault on MOORLND4 (520999) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 kV bus to CDRDLTP4 (520848) 138.0 kV bus CKT 1 b. 4. Trip branch from MOORLND4 (520999) 138.0 kV bus to GLASMTN4 (514788) 138.0 kV bus CKT 1 b. 5. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 6. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 7. Trip branch from GLASMTN4 (514788) 138.0 kV bus to CLEOCOR4 (514778) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-520430_NOELSW | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a. Apply single-phase fault on NOELSW (520430) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 kV bus to DRIFTWD4 (521200) 138.0 kV bus CKT 1 b. 7. Trip branch from NOELSW (520430) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-532782_BUFFALO7 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345.0 kV bus a. Apply single-phase fault on BUFFALO7 (532782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_763010_G19-065-TAP-509076_NWHENDR4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 2. Drop load from bus LONDON (509072) 138.0 kV bus b. 3. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 6. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 7. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 2. Reclose branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 4. Reclose branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 2. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 4. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_763010_G19-065-TAP-509080_OVERTON4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509080_OVERTON4-508548_KNOXLEE4_Ckt1 | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 2. Reclose branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 4. Reclose branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 2. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 4. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509080_OVERTON4-509079_OVERTON2_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509080_OVERTON4-509241_CROCKET7_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 3. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 4. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 5. Drop load from bus ALTO (509320) 138.0 kV bus b. 6. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 7. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 8. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 9. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 10. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 11. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 b. 12. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 13. Drop switching device from bus OVERTON4 (509080) 138.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 2. Reclose branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 3. Reclose branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 5. Reclose branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 6. Reclose branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 3. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 5. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 6. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509241_CROCKET7-508585_TENRUSK7_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509241_CROCKET7-334028_7GRIMES%_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509241_CROCKET7-509080_OVERTON4_3Winding | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 2. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 3. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 4. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 5. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 6. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 7. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 8. Drop load from bus ALTO (509320) 138.0 kV bus b. 9. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 10. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 11. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 12. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 2. Reclose branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 3. Reclose branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 5. Reclose branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 6. Reclose branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 2. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 3. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 5. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 6. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509079_OVERTON2-508546_KILGORE2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509079_OVERTON2-509080_OVERTON4_3Winding | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509079_OVERTON2-509089_TURNERT2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus TURNERT2 (509089) 69.0 kV bus b. 2. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509076_NWHENDR4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 c. 2. Reclose branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 d. 2. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509080_OVERTON4 | Single Phase Fault with Stuck Breaker on OVERTON4 (509080) 138.0 kV bus a. Apply single-phase fault on OVERTON4 (509080) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 kV bus to LEVERET4 (509069) 138.0 kV bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 kV bus to KILGORR4 (509067) 138.0 kV bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 kV bus to MONROER4 (509073) 138.0 kV bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 kV bus to KNOXLEE4 (508548) 138.0 kV bus CKT 1 b. 8. Trip branch from OVERTON4 (509080) 138.0 kV bus to G19-065-TAP (763010) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509076_NWHENDR4-509075_NWHENDR2_3Winding | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509076_NWHENDR4-763010_G19-065-TAP_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 2. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 3. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 6. Drop load from bus LONDON (509072) 138.0 kV bus b. 7. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 2. Reclose branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 4. Reclose branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 2. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 4. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-508562_PIRKEY_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 c. 2. Reclose branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. 3. Reclose branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 d. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. 3. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-509059_CHEROKE4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CHEROKE4 (509059) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-509080_OVERTON4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 2. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 3. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 6. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 7. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 2. Reclose branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 4. Reclose branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 2. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 4. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-508544_HARRISN4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-508570_SOTXEST4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SOTXEST4 (508570) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508548_KNOXLEE4-508568_SELONGV2_3Winding | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KXLEE-1 (508584) to trip transformer at KXLEE-1 12.470 (508584) 12.470000267028809 kV bus b. 2. Drop load from bus KNOXLEE2 (508547) 69.0 kV bus b. 3. Drop switching device from bus KNOXLEE2 (508547) 69.0 kV bus b. 4. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_334028_7GRIMES%-334026_4GRIMES%_3Winding | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_334028_7GRIMES%-334027_6GRIMES!_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_334028_7GRIMES%-334197_7ROCKYCRK%_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508585_TENRUSK7-508572_LEBROCK7_Ckt1 | 3 Phase fault on TENRUSK7 (508585) 345.0 kV a. Apply fault on TENRUSK7 (508585) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508546_KILGORE2-508573_SPIPETP2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 b. 2. Drop load from bus HOWELL (508545) 69.0 kV bus b. 3. Drop switching device from bus HOWELL (508545) 69.0 kV bus b. 4. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 b. 5. Drop load from bus SABINE (508565) 69.0 kV bus b. 6. Drop switching device from bus SABINE (508565) 69.0 kV bus b. 7. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 c. 2. Reclose branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 c. 3. Reclose branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 d. 2. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 d. 3. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508546_KILGORE2-508574_WHITNEY2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 b. 2. Drop load from bus MONROCR2 (508558) 69.0 kV bus b. 3. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 c. 2. Reclose branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 d. 2. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509075_NWHENDR2-509081_POYNTER2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509075_NWHENDR2-509076_NWHENDR4_3Winding | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509075_NWHENDR2-509061_EVENSID2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_334026_4GRIMES%-334028_7GRIMES%_3Winding | 3 Phase fault on 4GRIMES% (334026) 138.0 kV a. Apply fault on 4GRIMES% (334026) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt2 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt1 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509241_CROCKET7 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509079_OVERTON2 | Single Phase Fault with Stuck Breaker on OVERTON2 (509079) 69.0 kV bus a. Apply single-phase fault on OVERTON2 (509079) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 b. 2. Disconnect OVTON2-1 (509098) 13.2 kV bus to trip transformer at OVTON2-1 13.200 (509098) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509076_NWHENDR4 | Single Phase Fault with Stuck Breaker on NWHENDR4 (509076) 138.0 kV bus a. Apply single-phase fault on NWHENDR4 (509076) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 kV bus to OAK1HIL4 (509077) 138.0 kV bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 kV bus to OAK2HIL4 (509078) 138.0 kV bus CKT 1 b. 5. Disconnect NWHEN1-1 (509095) 13.2 kV bus to trip transformer at NWHEN1-1 13.200 (509095) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508548_KNOXLEE4 | Single Phase Fault with Stuck Breaker on KNOXLEE4 (508548) 138.0 kV bus a. Apply single-phase fault on KNOXLEE4 (508548) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to BRANDYBR (508596) 138.0 kV bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 b. 5. Drop load from bus KNOXL5-1 (509398) 22.0 kV bus b. 6. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to KNOXL5-1 (509398) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-334028_7GRIMES% | Single Phase Fault with Stuck Breaker on 7GRIMES% (334028) 345.0 kV bus a. Apply single-phase fault on 7GRIMES% (334028) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508585_TENRUSK7 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip branch from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-508586_TENGEN | Single Phase Fault with Stuck Breaker on TENGEN (508586) 345.0 kV bus a. Apply single-phase fault on TENGEN (508586) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506745) 18.0 kV bus CKT 1 b. 2. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506746) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-334026_4GRIMES% | Single Phase Fault with Stuck Breaker on 4GRIMES% (334026) 138.0 kV bus a. Apply single-phase fault on 4GRIMES% (334026) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus b. 2. Disconnect 1GRIMES_2 (334018) 13.8 kV bus to trip transformer at 1GRIMES_2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-300997_5KETONVL-ConID-109484 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-300997_5KETONVL-ConID-109485 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN2 (512839) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 1 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-500250_DOLHILL7-ConID-80023 | Single Phase Fault with Stuck Breaker on DOLHILL7 (500250) 345.0 kV bus a. Apply single-phase fault on DOLHILL7 (500250) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DOLHILL7 (500250) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84210 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84211 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84212 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84213 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84214 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84207 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84208 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84209 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-506979_SHIPERD7-ConID-84215 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345.0 kV bus a. Apply single-phase fault on SHIPERD7 (506979) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from SHIPERD7 (506979) 345.0 kV bus to SHIPERD5 (506980) 161.0 kV bus to SHIPERD1 (506981) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507455_TURK-ConID-84200 | Single Phase Fault with Stuck Breaker on TURK (507455) 345.0 kV bus a. Apply single-phase fault on TURK (507455) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from TURK (507454) 138.0 kV bus to TURK (507455) 345.0 kV bus to TURK (507457) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507760_SW-ConID-84164 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507760_SW-ConID-84165 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507760_SW-ConID-84166 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507760_SW-ConID-84167 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-507760_SW-ConID-84168 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84194 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84197 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84198 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84199 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84187 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84189 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84195 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84196 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84206 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 4. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508298_LYDIA-ConID-91933 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508359_WELSH-ConID-84181 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508359_WELSH-ConID-84184 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508359_WELSH-ConID-84190 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84154 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84155 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84156 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84157 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84159 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84160 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84161 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY1-1 (508587) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84162 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY1-1 (508587) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84163 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508572_LEBROCK7-ConID-84153 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508572_LEBROCK7-ConID-84158 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84150 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 b. 3. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84151 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84152 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84169 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84170 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84171 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84172 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84173 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84174 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84175 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84176 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84177 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84178 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508832_DIANA-ConID-84179 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508841_WILKES-ConID-84180 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-508841_WILKES-ConID-84182 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509241_CROCKET7-ConID-84148 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509241_CROCKET7-ConID-84149 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84185 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84186 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84191 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509406_WELSH3-1-ConID-84188 | Single Phase Fault with Stuck Breaker on WELSH3-1 (509406) 18.0 kV bus a. Apply single-phase fault on WELSH3-1 (509406) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509409_WILKE3-1-ConID-84183 | Single Phase Fault with Stuck Breaker on WILKE3-1 (509409) 22.0 kV bus a. Apply single-phase fault on WILKE3-1 (509409) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84239 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84240 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84241 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509782_RSS-7-ConID-84233 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip transformer from RSS (509773) 138.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus to RSST1 (509882) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509782_RSS-7-ConID-84234 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to COGENT (509834) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84248 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84249 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84256 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84257 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84258 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84259 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84260 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84262 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84263 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 b. 2. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84265 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84266 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84242 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84243 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84244 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip line from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509870_SAPLPRD7-ConID-84236 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from SAPLPRD7 (509870) 345.0 kV bus to SAPLPRD4 (509871) 138.0 kV bus to SAPLPRD1 (509872) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509870_SAPLPRD7-ConID-84237 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509874_ONETA5-1-ConID-84264 | Single Phase Fault with Stuck Breaker on ONETA5-1 (509874) 34.5 kV bus a. Apply single-phase fault on ONETA5-1 (509874) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-509881_ONETA1-1-ConID-84261 | Single Phase Fault with Stuck Breaker on ONETA1-1 (509881) 13.8 kV bus a. Apply single-phase fault on ONETA1-1 (509881) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510370_DELAWAR1-ConID-8425301 | Single Phase Fault with Stuck Breaker on DELAWAR1 (510370) 13.8 kV bus a. Apply single-phase fault on DELAWAR1 (510370) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84253 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-842530 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84254 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-842540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84255 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510406_NES-7-ConID-84250 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510406_NES-7-ConID-84251 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510406_NES-7-ConID-84252 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84223 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84224 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84225 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84226 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84227 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84201 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84202 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84203 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-91932 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511411_LES#5-1-ConID-8422101 | Single Phase Fault with Stuck Breaker on LES#5-1 (511411) 13.8 kV bus a. Apply single-phase fault on LES#5-1 (511411) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511456_OKU-7-ConID-84217 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511467_LES-4-ConID-9193401 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-84218 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-842180 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-84221 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-842210 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-84222 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-842720 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-842730 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-91934 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-919340 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-91937 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-919370 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511468_LES-7-ConID-9193701 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84272 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-8427201 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84273 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-8427301 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84274 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-511840_NES3-1-ConID-84247 | Single Phase Fault with Stuck Breaker on NES3-1 (511840) 22.0 kV bus a. Apply single-phase fault on NES3-1 (511840) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512635_KERR-ConID-109452 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512635_KERR-ConID-109453 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512635_KERR-ConID-109454 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512771) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512638_CATSAGR5-ConID-109479 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Trip transformer from CATOOSA4 (509790) 138.0 kV bus to CATSAGR5 (512638) 161.0 kV bus to CATTER2 (512834) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512651_CLARMR-ConID-109481 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512651_CLARMR-ConID-109482 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109486 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR (512700) 161.0 kV bus b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109487 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA2 (512826) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109488 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512686_SALINA-ConID-109461 | Single Phase Fault with Stuck Breaker on SALINA (512686) 161.0 kV bus a. Apply single-phase fault on SALINA (512686) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SALINA (512686) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512707_CLARMR-ConID-109480 | Single Phase Fault with Stuck Breaker on CLARMR (512707) 138.0 kV bus a. Apply single-phase fault on CLARMR (512707) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR2 (512815) 13.8 kV bus CKT 2 b. 2. Disconnect CLARMR (512707) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-512714_KANSATP5-ConID-109462 | Single Phase Fault with Stuck Breaker on KANSATP5 (512714) 161.0 kV bus a. Apply single-phase fault on KANSATP5 (512714) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SILSPWW5 (512642) 161.0 kV bus b. 2. Disconnect KANSATP5 (512714) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118718 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118719 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from JOHNCO (514808) 138.0 kV bus to JOHNCO (514809) 345.0 kV bus to JOHNCO11 (514810) 13.8 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118720 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515136_SUNNYSD7-ConID-118867 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515136_SUNNYSD7-ConID-1188670 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515405_SUNYSD-ConID-11886701 | Single Phase Fault with Stuck Breaker on SUNYSD (515405) 13.8 kV bus a. Apply single-phase fault on SUNYSD (515405) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from G17-075-TAP (560088) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-118540 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BALKOW (515618) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-80821 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to PALDR2W7 (515590) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515802_GRACMNT4-ConID-118667 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 2. Trip line from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-532777_G17-009-TAP-ConID-8425401 | Single Phase Fault with Stuck Breaker on G17-009-TAP (532777) 345.0 kV bus a. Apply single-phase fault on G17-009-TAP (532777) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-587744_G16-091-TAP-ConID-8421801 | Single Phase Fault with Stuck Breaker on G16-091-TAP (587744) 345.0 kV bus a. Apply single-phase fault on G16-091-TAP (587744) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-507760_SW-ConID-AEPW-10 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a.Apply single-phase fault on SW (507760) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 3. Clear fault from SW (507760) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508359_WELSH-ConID-AEPW-3 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508359_WELSH-ConID-AEPW-4 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-4 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) b. 3. Drop generator from LEBROCG1 (506752 ID 1) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-5 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-8 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-9 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508832_DIANA-ConID-AEPW-6 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508832_DIANA-ConID-AEPW-7 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-508841_WILKES-ConID-AEPW-5 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a.Apply single-phase fault on WILKES (508841) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Clear fault from WILKES (508841) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-509807_ONETA--7-ConID-AEPW-82 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a.Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from ONETA--7 (509807) 345.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from ONETA--7 (509807) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 3. Clear fault from ONETA--7 (509807) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512635_KERR-ConID-GRDA-68 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512635_KERR-ConID-GRDA-69 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 b. 4. Disconnect SALNCRK5 (512805) 161.0 kV bus b. 5. Disconnect SALINA (512686) 161.0 kV bus b. 6. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 10. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 11. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 16. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 17. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 22. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 23. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-58 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-59 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-60 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-61 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER2 (512837) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-62 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-63 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-64 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-65 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-66 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-46 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-47 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-48 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-49 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA17-1 (512688) 22.799999237060547 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-71 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-72 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-73 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-74 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Drop generator from PENSA_U4 (512605 ID 4) 13.2 kV bus b. 4. Drop generator from PENSA_U5 (512607 ID 5) 13.2 kV bus b. 5. Drop generator from PENSA_U6 (512606 ID 6) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-53 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Disconnect WAGNOR (512700) 161.0 kV bus b. 4. Disconnect WAGNOR1 (512818) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-54 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Open branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512669_KETCHUM5-ConID-GRDA-70 | Single Phase Fault with Stuck Breaker on KETCHUM5 (512669) 161.0 kV bus a.Apply single-phase fault on KETCHUM5 (512669) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Disconnect AFTON (512632) 161.0 kV bus b. 2. Clear fault from KETCHUM5 (512669) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 4. Drop load from KETCHUM5 (512669 ID 1) 161.0 kV bus b. 5. Disconnect KETCHUM5 (512669) 161.0 kV bus b. 6. Disconnect AFTON1 (512845) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-55 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-56 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-57 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-77 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-78 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Disconnect TONECE1 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512751_TONECE5-ConID-GRDA-76 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512805_SALNCRK5-ConID-GRDA-75 | Single Phase Fault with Stuck Breaker on SALNCRK5 (512805) 161.0 kV bus a.Apply single-phase fault on SALNCRK5 (512805) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from SALNCRK5 (512805) b. 3. Disconnect SALINA (512686) 161.0 kV bus b. 4. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 5. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 6. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 10. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 11. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 16. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 17. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512865_GREC-ConID-GRDA-50 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECSTG_1 (512615) 21.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-512865_GREC-ConID-GRDA-51 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECCTG_1 (512614) 20.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-513596_IGLOOV-ConID-GRDA-52 | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a.Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from IGLOOV (513596) b. 3. Disconnect IGLOTER1 (513592) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-514803_SOONER-ConID-OKGE-29 | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a.Apply single-phase fault on SOONER (514803) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SOONER (515760) 13.8 kV bus b. 2. Open branch from G15-066T (560056) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 b. 3. Clear fault from SOONER (514803) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-514809_JOHNCO-ConID-OKGE-21 | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a.Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Open branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 3. Clear fault from JOHNCO (514809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515045_SEMINOL7-ConID-OKGE-28 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a.Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Disconnect SEMINO21 (515757) 14.399999618530273 kV bus b. 3. Clear fault from SEMINOL7 (515045) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515136_SUNNYSD7-ConID-OKGE-18 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a.Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SUNYSD (515405) 13.8 kV bus b. 2. Open branch from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 b. 3. Clear fault from SUNNYSD7 (515136) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515339_VBI-ConID-OKGE-32 | Single Phase Fault with Stuck Breaker on VBI (515339) 161.0 kV bus a.Apply single-phase fault on VBI (515339) 161.0 kV bus b.Run for 23.52 cycles and trip the following elements: b. 1. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 2. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 3. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 4. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 5. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 11.28 cycles and trip the following elements: b. 6. Close branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 7. Close branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 8. Close branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 9. Close branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 10. Close branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 1.62 cycles and trip the following elements: b. 11. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 9.18 cycles and trip the following elements: b. 12. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 4.02 cycles and trip the following elements: b. 13. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 4.2 cycles and trip the following elements: b. 14. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 2.4 cycles and trip the following elements: b. 15. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 0.18 cycles and trip the following elements: b. 16. Close branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 2.82 cycles and trip the following elements: b. 17. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 6.36 cycles and trip the following elements: b. 18. Close branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 1.44 cycles and trip the following elements: b. 19. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 19.38 cycles and trip the following elements: b. 20. Disconnect VBI (515769) 13.8 kV bus b.Run for 23.82 cycles and trip the following elements: b. 21. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 18.36 cycles and trip the following elements: b. 22. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b. 23. Clear fault from VBI (515339) b. 24. Drop load from HWY59 (504191 ID A1) 161.0 kV bus b. 25. Drop load from GRANDPR5 (504192 ID A1) 161.0 kV bus b. 26. Drop load from SIMMONS5 (515332 ID 1) 161.0 kV bus b. 27. Drop load from SIMMONS5 (515332 ID A1) 161.0 kV bus b. 28. Drop load from DYER (515333 ID A1) 161.0 kV bus b. 29. Drop load from ALMA (515334 ID 1) 161.0 kV bus b. 30. Drop load from RUDY (515337 ID A1) 161.0 kV bus b. 31. Drop load from OAKGROV5 (515340 ID A1) 161.0 kV bus b. 32. Drop load from WHITESD5 (515341 ID 1) 161.0 kV bus b. 33. Drop load from PUDDIN (515346 ID A1) 161.0 kV bus b. 34. Drop load from NITROUS5 (515350 ID 1) 161.0 kV bus b. 35. Drop load from GERBER (515351 ID 1) 161.0 kV bus b. 36. Drop load from TWNBRDG5 (515360 ID 1) 161.0 kV bus b. 37. Drop load from ADABELL5 (515406 ID 1) 161.0 kV bus b. 38. Disconnect HWY59 (504191) 161.0 kV bus b. 39. Disconnect GRANDPR5 (504192) 161.0 kV bus b. 40. Disconnect GERBRTP5 (515326) 161.0 kV bus b. 41. Disconnect NITROTP5 (515329) 161.0 kV bus b. 42. Disconnect SIMMONS5 (515332) 161.0 kV bus b. 43. Disconnect DYER (515333) 161.0 kV bus b. 44. Disconnect ALMA (515334) 161.0 kV bus b. 45. Disconnect RUDY (515337) 161.0 kV bus b. 46. Disconnect OAKGROV5 (515340) 161.0 kV bus b. 47. Disconnect WHITESD5 (515341) 161.0 kV bus b. 48. Disconnect PUDDIN (515346) 161.0 kV bus b. 49. Disconnect NALCOTP5 (515348) 161.0 kV bus b. 50. Disconnect NITROUS5 (515350) 161.0 kV bus b. 51. Disconnect GERBER (515351) 161.0 kV bus b. 52. Disconnect TWNBRDG5 (515360) 161.0 kV bus b. 53. Disconnect ADABELL5 (515406) 161.0 kV bus b. 54. Disconnect GRNDPRT5 (515524) 161.0 kV bus b. 55. Disconnect HWY59TP5 (515527) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515554_BVRCNTY7-ConID-OKGE-16 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a.Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 3. Clear fault from BVRCNTY7 (515554) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515576_RANCHRD7-ConID-OKGE-25 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345.0 kV bus a.Apply single-phase fault on RANCHRD7 (515576) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from SOONER (514803) 345.0 kV bus to RANCHRD7 (515576) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to FRNTWND7 (515688) 345.0 kV bus CKT 1 b. 3. Clear fault from RANCHRD7 (515576) b. 4. Drop generator from FRNTWDG1 (515691 ID 1) 0.65 kV bus b. 5. Drop load from FRNTWD11 (515689 ID S1) 34.5 kV bus b. 6. Disconnect FRNTWND7 (515688) 345.0 kV bus b. 7. Disconnect FRNTWD11 (515689) 34.5 kV bus b. 8. Disconnect FRNTWDC1 (515690) 34.5 kV bus b. 9. Disconnect FRNTWDG1 (515691) 0.65 kV bus b. 10. Disconnect FRNTWDT1 (515692) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515621_OPENSKY7-ConID-OKGE-23 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345.0 kV bus a.Apply single-phase fault on OPENSKY7 (515621) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 b. 3. Clear fault from OPENSKY7 (515621) b. 4. Drop generator from KAYWNDG1 (515651 ID 1) 0.69 kV bus b. 5. Drop generator from KAYWNDG2 (515652 ID 1) 0.69 kV bus b. 6. Drop load from KAYWND11 (515622 ID S1) 34.5 kV bus b. 7. Drop load from KAYWND12 (515623 ID S1) 34.5 kV bus b. 8. Disconnect KAYWIND7 (514825) 345.0 kV bus b. 9. Disconnect KAYWNDT1 (515619) 12.5 kV bus b. 10. Disconnect KAYWNDT2 (515620) 12.5 kV bus b. 11. Disconnect OPENSKY7 (515621) 345.0 kV bus b. 12. Disconnect KAYWND11 (515622) 34.5 kV bus b. 13. Disconnect KAYWND12 (515623) 34.5 kV bus b. 14. Disconnect KAYWNDG1 (515651) 0.69 kV bus b. 15. Disconnect KAYWNDG2 (515652) 0.69 kV bus b. 16. Disconnect KAYWNDC1 (515653) 34.5 kV bus b. 17. Disconnect KAYWNDC2 (515654) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515785_WINDFRM4-ConID-OKGE-17 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138.0 kV bus a.Apply single-phase fault on WINDFRM4 (515785) 138.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WINDFRM4 (515785) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 b. 2. Open branch from WOODWRD4 (514785) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 b. 3. Clear fault from WINDFRM4 (515785) b. 4. Drop generator from FPLWNDG1 (515895 ID 1) 0.69 kV bus b. 5. Drop load from FPLWND11 (515787 ID S1) 34.5 kV bus b. 6. Disconnect WINDFRM4 (515785) 138.0 kV bus b. 7. Disconnect FPLWIND4 (515786) 138.0 kV bus b. 8. Disconnect FPLWND11 (515787) 34.5 kV bus b. 9. Disconnect FLPWND21 (515790) 13.8 kV bus b. 10. Disconnect FPLWNDG1 (515895) 0.69 kV bus b. 11. Disconnect FPLWNDC1 (515896) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515800_GRACMNT7-ConID-OKGE-22 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a.Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from LES (587744) None kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Open branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 3. Clear fault from GRACMNT7 (515800) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-520430_NOELSW-ConID-WFEC-59 | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a.Apply single-phase fault on NOELSW (520430) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DRIFTWD4 (521200) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 b. 3. Open branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 4. Clear fault from NOELSW (520430) b. 5. Drop load from CHRKCTY4 (520431 ID 1) 138.0 kV bus b. 6. Drop load from SALTPLN4 (520437 ID 1) 138.0 kV bus b. 7. Drop load from SALTPLN4 (520437 ID 2) 138.0 kV bus b. 8. Disconnect CHRKCTY4 (520431) 138.0 kV bus b. 9. Disconnect SALTPLN4 (520437) 138.0 kV bus b. 10. Drop load from ROSEVLY4 (520436 ID 1) 138.0 kV bus b. 11. Drop load from AVARD (520601 ID 1) 138.0 kV bus b. 12. Disconnect ROSEVLY4 (520436) 138.0 kV bus b. 13. Disconnect AVARD (520601) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-520814_ANADARK4-ConID-WFEC-51 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138.0 kV bus a.Apply single-phase fault on ANADARK4 (520814) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SUNSHIN4 (521059) 138.0 kV bus to BRIDGCR4 (520501) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 3. Open branch from ANADRK5 (520812) 13.8 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 4. Open branch from ANADARK4 (520814) 138.0 kV bus to POCASET4 (521031) 138.0 kV bus CKT 1 b. 5. Clear fault from ANADARK4 (520814) b. 6. Drop generator from ANADRK5 (520812 ID 1) 13.8 kV bus b. 7. Drop load from ANADRK5 (520812 ID F1) 13.8 kV bus b. 8. Drop load from ANADRK5 (520812 ID V1) 13.8 kV bus b. 9. Disconnect ANADRK5 (520812) 13.8 kV bus b. 10. Drop load from TUTTLE (520496 ID 1) 138.0 kV bus b. 11. Drop load from BRIDGCR4 (520501 ID 1) 138.0 kV bus b. 12. Drop load from POCASET4 (521031 ID 1) 138.0 kV bus b. 13. Disconnect TUTTLE (520496) 138.0 kV bus b. 14. Disconnect BRIDGCR4 (520501) 138.0 kV bus b. 15. Disconnect POCASET4 (521031) 138.0 kV bus b. 16. Disconnect TUTLETP4 (521072) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-520920_FTSUPLY4-ConID-WFEC-55 | Single Phase Fault with Stuck Breaker on FTSUPLY4 (520920) 138.0 kV bus a.Apply single-phase fault on FTSUPLY4 (520920) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SLEEPBR4 (520922) 138.0 kV bus to FTSUPLY4 (520920) 138.0 kV bus CKT 1 b. 2. Drop generator from SLP (521145 ID 1) 0.6000000238418579 kV bus b. 3. Disconnect SLEEPBR4 (520922) 138.0 kV bus b. 4. Disconnect SLP (521141) 34.5 kV bus b. 5. Disconnect SLP (521144) 34.5 kV bus b. 6. Disconnect SLP (521145) 0.6000000238418579 kV bus b. 7. Disconnect SLP (521151) 9.949999809265137 kV bus b.Run for 9.0 cycles and trip the following elements: b. 8. Open branch from MOORLND4 (520999) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 9. Clear fault from FTSUPLY4 (520920) b. 10. Open branch from FTSUPLY4 (520920) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 11. Drop load from IODINE (520957 ID 1) 138.0 kV bus b. 12. Disconnect IODINE (520957) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-521016_OKEENE-ConID-WFEC-60 | Single Phase Fault with Stuck Breaker on OKEENE (521016) 138.0 kV bus a.Apply single-phase fault on OKEENE (521016) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DOVERSW4 (520882) 138.0 kV bus to OKEENE (521016) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 3. Clear fault from OKEENE (521016) b. 4. Drop load from PIC4 (520425 ID 1) 138.0 kV bus b. 5. Drop load from CEDRDAL4 (520507 ID 1) 138.0 kV bus b. 6. Disconnect PIC4 (520425) 138.0 kV bus b. 7. Disconnect CDRDLTP4 (520848) 138.0 kV bus b. 8. Disconnect CEDRDAL4 (520507) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-65 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from CLINTJC4 (511485) 138.0 kV bus to CLINTON4 (520856) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b. 3. Open branch from WASHITA4 (521089) 138.0 kV bus to ONEY (521017) 138.0 kV bus CKT 1 b. 4. Clear fault from WASHITA4 (521089) b. 5. Drop load from HINTON (520468 ID 1) 138.0 kV bus b. 6. Drop load from DEERCR (520503 ID 1) 138.0 kV bus b. 7. Drop load from CLINTON4 (520856 ID 1) 138.0 kV bus b. 8. Drop load from HYDRO (520950 ID 1) 138.0 kV bus b. 9. Drop load from NIJECT (521010 ID 1) 138.0 kV bus b. 10. Drop load from NIJECT (521010 ID 2) 138.0 kV bus b. 11. Drop load from ONEY (521017 ID 1) 138.0 kV bus b. 12. Drop load from SICKLES4 (521050 ID 1) 138.0 kV bus b. 13. Drop load from WEATHFD4 (521092 ID 1) 138.0 kV bus b. 14. Disconnect HINTON (520468) 138.0 kV bus b. 15. Disconnect DEERCR (520503) 138.0 kV bus b. 16. Disconnect BINGERJ4 (520827) 138.0 kV bus b. 17. Disconnect CLINTON4 (520856) 138.0 kV bus b. 18. Disconnect HYDRO (520950) 138.0 kV bus b. 19. Disconnect NIJECT (521010) 138.0 kV bus b. 20. Disconnect ONEY (521017) 138.0 kV bus b. 21. Disconnect SICKLES4 (521050) 138.0 kV bus b. 22. Disconnect WEATHFD4 (521092) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-66 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 3. Clear fault from WASHITA4 (521089) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523777_WHEELER-ConID-SPS-140 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from WHEELER (523777) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT &1 b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523777_WHEELER-ConID-SPS-143 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532791_BENTON-ConID-Evergy-105 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532791_BENTON-ConID-Evergy-106 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Disconnect ROSEH3 (532831) 13.8 kV bus b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-152 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Disconnect ROSEH3 (532831) 13.8 kV bus b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-121 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Disconnect WOLFCRK1 (532962) 17.0 kV bus b. 4. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 5. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542965_WGRDNR7-ConID-Evergy-150 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345.0 kV bus a.Apply single-phase fault on W.GRDNR7 (542965) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from W.GRDNR7 (542965) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 b. 2. Open branch from STILWEL7 (542968) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 3. Clear fault from W.GRDNR7 (542965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542968_STILWEL7-ConID-Evergy-148 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345.0 kV bus a.Apply single-phase fault on STILWEL7 (542968) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from PECULR (541198) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 3. Clear fault from STILWEL7 (542968) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-140 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-141 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-142 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-143 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542956) 24.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-547469_RIV4525-ConID-EMDE-34 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161.0 kV bus a.Apply single-phase fault on RIV4525 (547469) 161.0 kV bus b.Run for 7.0 cycles and trip the following elements: b. 1. Open branch from RIV4525 (547469) 161.0 kV bus to NEOSHO (532937) 161.0 kV bus CKT 1 b.Run for 86.0 cycles and trip the following elements: b. 4. Open branch from BAX488 (547729) 161.0 kV bus to HOC404 (547487) 161.0 kV bus CKT 1 b. 5. Clear fault from RIV4525 (547469) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523097_HITCHLAND-523823_CARPENTER_Ckt1 | 3 Phase fault on HITCHLAND (523097) 345.0 kV a. Apply fault on HITCHLAND (523097) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523323_MCDWL_CREEK623000-523309_MOORE_CNTY_Ckt1 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523323_MCDWL_CREEK623000-523322_MCDWL_CREEK311500_3Winding | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MCDWL_CRKTR113.200 (523321) to trip transformer at MCDWL_CRKTR113.200 (523321) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-523323_MCDWL_CREEK623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-523869_CHAN+TASCOS623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-523979_HARRNG_EST_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-524010_ROLLHILLS_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523959_POTTER_CO-524267_BUSHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523961_POTTER_CO-523097_HITCHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523977_HARRNG_WST-524010_ROLLHILLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523977_HARRNG_WST-524044_NICHOLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523977_HARRNG_WST-524162_EAST_PLANT_3Winding | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 b. 2. Disconnect bus at EPLANT_TR3 (524160) to trip transformer at EPLANT_TR3 113.200 (524160) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523978_HARRNG_MID-523977_HARRNG_WST_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523978_HARRNG_MID-524044_NICHOLS_Ckt2 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523978_HARRNG_MID-524365_RANDALL_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523979_HARRNG_EST-523266_PRINGLE_3Winding | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 b. 2. Disconnect bus at PRINGLE_TR (523265) to trip transformer at PRINGLE_TR 113.200 (523265) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523979_HARRNG_EST-523978_HARRNG_MID_Ckt1 | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524415_AMA_SOUTH-524044_NICHOLS_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524415_AMA_SOUTH-524365_RANDALL_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524415_AMA_SOUTH-524414_AMA_SOUTH_3Winding | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at AMA_SO_TR1 (524410) to trip transformer at AMA_SO_TR1 113.200 (524410) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524746_CASTRO_CNTY311500-524734_DS-#21_Ckt1 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV a. Apply fault on CASTRO_CNTY3115.00 (524746) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 2. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524768_PLSNT_HILL-524770_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524768_PLSNT_HILL-524822_CURRY_Ckt1 | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 b. 2. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 3. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 c. 2. Reclose branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 d. 2. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524770_PLSNT_HILL-524768_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524770_PLSNT_HILL-524875_OASIS_Ckt1 | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524822_CURRY-524669_DS-#20_Ckt1 | 3 Phase fault on CURRY (524822) 115.0 kV a. Apply fault on CURRY (524822) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 2. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524874_OASIS-524764_NORRIS_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 b. 2. Drop load from bus FE-CHZPLT (524863) 115.0 kV bus b. 3. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 c. 2. Reclose branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 d. 2. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524874_OASIS-524790_CANNON_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 b. 2. Drop load from bus PERIMETER (524797) 115.0 kV bus b. 3. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 c. 2. Reclose branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 d. 2. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524874_OASIS-524875_OASIS_3Winding | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524874_OASIS-524924_PORTALES_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524875_OASIS-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524875_OASIS-524874_OASIS_3Winding | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524875_OASIS-524885_SN_JUAN_TAP623000_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524885_SN_JUAN_TAP623000-527483_CHAVES_CNTY623000_Ckt1 | 3 Phase fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV a. Apply fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524908_ROOSEVELT-524822_CURRY_Ckt2 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524908_ROOSEVELT-524909_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524908_ROOSEVELT-524924_PORTALES_Ckt1 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-524875_OASIS_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-524908_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt2 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_524909_ROOSEVELT-599955_PNM-DC6_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop switching device from bus PNM-DC6 (599955) 230.0 kV bus b. 2. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525192_KRESS_INT-525213_SWISHER_3Winding | 3 Phase fault on KRESS_INT (525192) 115.0 kV a. Apply fault on KRESS_INT (525192) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 b. 2. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525213_SWISHER-524415_AMA_SOUTH_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525213_SWISHER-525192_KRESS_INT_3Winding | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 2. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525213_SWISHER-525830_TUCO_INT_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525414_LAMTON-525413_LAMTON_3Winding | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMTON_TR1 (525412) to trip transformer at LAMTON_TR1 113.200 (525412) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525414_LAMTON-525446_RKYFORD_TP_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 b. 2. Drop load from bus LC-S_OLTON+3115.00 (525440) 115.0 kV bus b. 3. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 c. 2. Reclose branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 d. 2. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525414_LAMTON-525454_HALE_CNTY_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525414_LAMTON-525460_NEWHART_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525460_NEWHART-524746_CASTRO_CNTY311500_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525460_NEWHART-525192_KRESS_INT_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525460_NEWHART-525414_LAMTON_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525460_NEWHART-525461_NEWHART_3Winding | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525461_NEWHART-523959_POTTER_CO_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525461_NEWHART-525213_SWISHER_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525461_NEWHART-525460_NEWHART_3Winding | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525461_NEWHART-525481_PLANT_X_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525480_PLANT_X-525019_MULSHVLY_TP311500_Ckt1 | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525480_PLANT_X-525481_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-525461_NEWHART_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-525480_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt2 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-526435_SUNDOWN_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525481_PLANT_X-760498_G17-146-TAP_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525549_TOLK_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525586_NEEDMORE_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525636_LAMB_CNTY_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 b. 2. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525637_LAMB_CNTY_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525531_TOLK-525830_TUCO_INT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525549_TOLK-523961_POTTER_CO_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525549_TOLK-525531_TOLK_3Winding | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525549_TOLK-527656_CROSSROADS_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525586_NEEDMORE-525581_BLUECLDGEN_CktZ1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 b. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 b. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 b. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 b. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 c. 2. Reclose branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 c. 3. Reclose branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 c. 4. Reclose branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 c. 5. Reclose branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 d. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 d. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 d. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 d. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525586_NEEDMORE-526935_YOAKUM_Ckt1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525635_LAMB_CNTY-525636_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525635) 69.0 kV a. Apply fault on LAMB_CNTY (525635) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525636_LAMB_CNTY-525480_PLANT_X_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525636_LAMB_CNTY-525531_TOLK_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525636_LAMB_CNTY-525635_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525636_LAMB_CNTY-526020_HOCKLEY_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525828_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525828) 115.0 kV a. Apply fault on TUCO_INT (525828) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-525213_SWISHER_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-525531_TOLK_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-525828_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-525832_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR1 (525824) to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-526161_CARLISLE_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525830_TUCO_INT-526337_JONES_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-515458_BORDER_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 2. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR2 (525825) to trip transformer at TUCO_TR2 113.200 (525825) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-526936_YOAKUM_345_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526020_HOCKLEY-526019_HOCKLEY_3Winding | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOCKLEY_TR1113.200 (526017) to trip transformer at HOCKLEY_TR1113.200 (526017) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526020_HOCKLEY-526434_SUNDOWN_Ckt1 | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 b. 2. Drop load from bus LC-OPDYKE (526036) 115.0 kV bus b. 3. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 c. 2. Reclose branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 d. 2. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526435_SUNDOWN-526434_SUNDOWN_3Winding | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNDOWN_TR1113.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526435_SUNDOWN-526525_WOLFFORTH_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526435_SUNDOWN-526935_YOAKUM_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 b. 2. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 3. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. 2. Reclose branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. 2. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526934_YOAKUM-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526934) 115.0 kV a. Apply fault on YOAKUM (526934) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-525586_NEEDMORE_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-526460_AMOCO_SS_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 2. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-526934_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-526936_YOAKUM_345_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-527009_BRU_SUB_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-527028_INK_BASIN_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526935_YOAKUM-527149_MUSTANG_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526936_YOAKUM_345-525832_TUCO_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526936_YOAKUM_345-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_526936_YOAKUM_345-527896_HOBBS_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527009_BRU_SUB-527010_OXYBRU_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OXYBRU (527010) 230.0 kV bus b. 2. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527009_BRU_SUB-527011_XTO_MAHONEY623000_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527011_XTO_MAHONEY623000-526784_AMOCOWASSON623000_Ckt1 | 3 Phase fault on XTO_MAHONEY6230.00 (527011) 230.0 kV a. Apply fault on XTO_MAHONEY6230.00 (527011) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 2. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 3. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 4. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-239 GEN1 & GEN2 (761358 & 761361) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527149_MUSTANG-527276_SEMINOLE_Ckt1 | 3 Phase fault on MUSTANG (527149) 230.0 kV a. Apply fault on MUSTANG (527149) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527656_CROSSROADS-527802_EDDY_CNTY_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt2 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527802_EDDY_CNTY-527799_EDDY_NORTH_3Winding | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at EDDY_TR (527796) to trip transformer at EDDY_TR 113.200 (527796) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527802_EDDY_CNTY-527965_KIOWA_Ckt1 | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527894_HOBBS_INT-527896_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527894_HOBBS_INT-528604_ANDREWS_Ckt1 | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-527894_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-527965_KIOWA_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_527965_KIOWA-528185_N_LOVING_Ckt1 | 3 Phase fault on KIOWA (527965) 345.0 kV a. Apply fault on KIOWA (527965) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_762216_G17-151TAP-762467_G18-015-TAP_Ckt1 | 3 Phase fault on G17-151TAP (762216) 345.0 kV a. Apply fault on G17-151TAP (762216) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-523097_HITCHLAND | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Trip branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-523959_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a. Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-523961_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523961) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524746_CASTRO_CNTY311500 | Single Phase Fault with Stuck Breaker on CASTRO_CNTY3115.00 (524746) 115.0 kV bus a. Apply single-phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CASTRO_TR1 (524744) 13.2 kV bus to trip transformer at CASTRO_CNTY2 (524745) 69.0 kV bus b. 2. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 3. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 kV bus to DS-#21 (524734) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524768_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524768) 115.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524768) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus b. 2. Trip branch from PLSNT_HILL (524768) 115.0 kV bus to E_CLOVIS (524773) 115.0 kV bus CKT 1 b. 3. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 4. Trip branch from E_CLOVIS (524773) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524770_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524770) 230.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524770) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524822_CURRY | Single Phase Fault with Stuck Breaker on CURRY (524822) 115.0 kV bus a. Apply single-phase fault on CURRY (524822) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CURRY (524822) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 2 b. 2. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 3. Trip branch from CURRY (524822) 115.0 kV bus to DS-#20 (524669) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524875_OASIS | Single Phase Fault with Stuck Breaker on OASIS (524875) 230.0 kV bus a. Apply single-phase fault on OASIS (524875) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524908_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524908) 115.0 kV bus a. Apply single-phase fault on ROOSEVELT (524908) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus b. 2. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524909_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524909) 230.0 kV bus a. Apply single-phase fault on ROOSEVELT (524909) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 b. 2. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-524924_PORTALES | Single Phase Fault with Stuck Breaker on PORTALES (524924) 115.0 kV bus a. Apply single-phase fault on PORTALES (524924) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PORTALES (524924) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 1 b. 2. Trip branch from PORTALES (524924) 115.0 kV bus to OASIS (524874) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525192_KRESS_INT | Single Phase Fault with Stuck Breaker on KRESS_INT (525192) 115.0 kV bus a. Apply single-phase fault on KRESS_INT (525192) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 kV bus to SWISHER (525212) 115.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from KRESS_INT (525192) 115.0 kV bus to NEWHART (525460) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525213_SWISHER | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a. Apply single-phase fault on SWISHER (525213) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from SWISHER (525212) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525460_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525460) 115.0 kV bus a. Apply single-phase fault on NEWHART (525460) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 b. 2. Disconnect NEWHART_TR2113.200 (525458) 13.2 kV bus to trip transformer at NEWHART_TR2113.200 (525458) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525461_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525461) 230.0 kV bus a. Apply single-phase fault on NEWHART (525461) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 b. 2. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525480_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525480) 115.0 kV bus a. Apply single-phase fault on PLANT_X (525480) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLANTX_TR1 (525479) 13.2 kV bus to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus b. 2. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525481_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525481) 230.0 kV bus a. Apply single-phase fault on PLANT_X (525481) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 b. 2. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525531_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525531) 230.0 kV bus a. Apply single-phase fault on TOLK (525531) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus b. 2. Disconnect TOLK_TR (525538) 13.2 kV bus to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525549_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525549) 345.0 kV bus a. Apply single-phase fault on TOLK (525549) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525635_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525635) 69.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525635) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR2 (525632) 13.2 kV bus to trip transformer at LAMB_TR2 113.200 (525632) 13.2 kV bus b. 2. Disconnect LAMB_TR1 (525631) 13.2 kV bus to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525636_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525636) 115.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525636) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR3 (525633) 13.2 kV bus to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 3. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525828_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525828) 115.0 kV bus a. Apply single-phase fault on TUCO_INT (525828) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TUCO_TR4 (525821) 13.2 kV bus to trip transformer at TUCO_TR4 113.200 (525821) 13.2 kV bus b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525830_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a. Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-526934_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526934) 115.0 kV bus a. Apply single-phase fault on YOAKUM (526934) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus to trip transformer at YOAKUM_TR1 113.200 (526931) 13.2 kV bus b. 2. Disconnect YOAKUM_TR2 (526932) 13.2 kV bus to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-526935_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a. Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-526936_YOAKUM_345 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-527149_MUSTANG | Single Phase Fault with Stuck Breaker on MUSTANG (527149) 230.0 kV bus a. Apply single-phase fault on MUSTANG (527149) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to AMOCOWASSON6 (526784) 230.0 kV bus CKT 1 b. 2. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-527656_CROSSROADS | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-527894_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527894) 230.0 kV bus a. Apply single-phase fault on HOBBS_INT (527894) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect HOBBS_TR3 (527895) 13.2 kV bus to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus b. 2. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-527896_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a. Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-527965_KIOWA | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 2. Trip branch from KIOWA (527965) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-528027_RDRUNNER | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-108426 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1 (523111) 115.0 kV bus b. 5. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-92600 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-523097_HITCHLAND-ConID-108427 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Disconnect HITCHLAND (523097) 345.0 kV bus b. 3. Trip transformer from HITCHLD_TR2113.200 (523094) 13.2 kV bus to HITCHLAND (523095) 230.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-523124_GRPLNS-CB4-134500-ConID-108428 | Single Phase Fault with Stuck Breaker on GRPLNS-CB4-134.500 (523124) 34.5 kV bus a. Apply single-phase fault on GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect NOBLE_TR (523102) 13.8 kV bus b. 3. Disconnect NOBLE_WND (523103) 115.0 kV bus b. 4. Disconnect GRPLNS-HV4-3115.00 (523130) 115.0 kV bus b. 5. Disconnect GRPLNS-HV2-3115.00 (523131) 115.0 kV bus b. 6. Disconnect GRPLNS-LV4-134.500 (523127) 34.5 kV bus b. 7. Disconnect GRPLNS-LV2-134.500 (523129) 34.5 kV bus b. 8. Disconnect GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. 9. Disconnect GRPLNS-CB2-134.500 (523126) 34.5 kV bus b. 10. Disconnect GRPLNS-WT4-10.5750 (523121) 0.574999988079071 kV bus b. 11. Disconnect GRPLNS-WT2-10.5750 (523123) 0.574999988079071 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-523961_POTTER_CO-ConID-108433 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Trip transformer from POTTER_TR (523957) 13.2 kV bus to POTTER_CO (523959) 230.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 3. Disconnect POTTER_CO (523961) 345.0 kV bus b. 4. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 5. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527656_CROSSROADS-ConID-108421 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Trip line from RSVLT_CC_E (527655) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 4. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 5. Disconnect MILO_WIND (527653) 0.7 kV bus b. 6. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 7. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 8. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 9. Disconnect CROSSROADS (527656) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108422 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108423 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108424 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108440 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527965_KIOWA-ConID-108429 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-527965_KIOWA-ConID-108441 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528027_RDRUNNER-ConID-108445 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRUNNER (528027) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528027_RDRUNNER-ConID-108447 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect PHANTOM (528011) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108430 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108431 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108432 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108443 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-118 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to BVRCNTY7 (515554) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus b. 5. Disconnect NOVUS1 (523111) 115.0 kV bus b. 6. Disconnect NOVUS1 (523112) 345.0 kV bus b. 7. Disconnect G06-44 (560577) 115.0 kV bus b. 8. Disconnect NOVUS1_TR2 (560578) 13.8 kV bus b. 9. Disconnect G06-44-2 (560581) 34.5 kV bus b. 10. Disconnect G06-44-3 (560582) 34.5 kV bus b. 11. Disconnect G06-44-4 (560583) 34.5 kV bus b. 12. Disconnect G06-44-2 (560584) 4.16 kV bus b. 13. Disconnect G06-44-3 (560585) 4.16 kV bus b. 14. Disconnect G06-44-4 (560586) 4.16 kV bus b. 15. Drop generator from NOVUS_WND (523107 ID 1) 4.16 kV bus b. 16. Drop generator from G06-44-2 (560584 ID 1) 4.16 kV bus b. 17. Drop generator from G06-44-3 (560585 ID 1) 4.16 kV bus b. 18. Drop generator from G06-44-4 (560586 ID 1) 4.16 kV bus b. 19. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-142 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b. 3. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523853_FINNEY-ConID-SPS-117 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345.0 kV bus a.Apply single-phase fault on FINNEY (523853) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOLCOMB7 (531449) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 2. Open branch from CARPENTER (523823) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 3. Disconnect FINNEY (523853) 345.0 kV bus b. 4. Disconnect LAMAR7 (599950) 345.0 kV bus b. 5. Disconnect LAMAR (599951) 345.0 kV bus b. 6. Disconnect BUFF_DUNES (523118) 345.0 kV bus b. 7. Disconnect BUFF_DN_TR1113.200 (523114) 13.2 kV bus b. 8. Disconnect BUFF_DN_TR2113.200 (523115) 13.2 kV bus b. 9. Disconnect BUFF_DUNES1134.500 (523116) 34.5 kV bus b. 10. Disconnect BUFF_DUNES2134.500 (523117) 34.5 kV bus b. 11. Clear fault from FINNEY (523853) b. 12. Drop generator from BUFF_DUNES230.6900 (523061 ID 1) 0.69 kV bus b. 13. Drop generator from BUFF_DUNES130.6900 (523062 ID 1) 0.69 kV bus b. 14. Disconnect BUFF_DUNES230.6900 (523061) 0.69 kV bus b. 15. Disconnect BUFF_DUNES130.6900 (523062) 0.69 kV bus b. 16. Disconnect BUFF_DUNES2234.500 (523063) 34.5 kV bus b. 17. Disconnect BUFF_DUNES1234.500 (523064) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523959_POTTER_CO-ConID-SPS-136 | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a.Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 2. Open branch from ROLLHILLS (524010) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Clear fault from POTTER_CO (523959) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-125 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Disconnect POTTER_TR (523957) 13.2 kV bus b. 4. Disconnect POTTER_CO (523961) 345.0 kV bus b. 5. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 6. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 7. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 8. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 9. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 10. Clear fault from POTTER_CO (523961) b. 11. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-144 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect POTTER_TR (523957) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Clear fault from POTTER_CO (523961) b.Run for 5.0 cycles and trip the following elements: b. 4. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 5. Disconnect POTTER_TR (523957) 13.2 kV bus b. 6. Disconnect POTTER_CO (523961) 345.0 kV bus b. 7. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 8. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 9. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 10. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 11. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 12. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523977_HARRNG_WST-ConID-SPS-149 | Single Phase Fault with Stuck Breaker on HARRNG_WST (523977) 230.0 kV bus a.Apply single-phase fault on HARRNG_WST (523977) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_WST (523977) 230.0 kV bus to EAST_PLANT (524163) 230.0 kV bus CKT 1 b. 3. Open branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 4. Disconnect HARRNG_WST (523977) 230.0 kV bus b. 5. Disconnect HARRNGTON1 (523971) 24.0 kV bus b. 6. Clear fault from HARRNG_WST (523977) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-150 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 3. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 4. Disconnect HARRNGTON2 (523972) 24.0 kV bus b. 5. Clear fault from HARRNG_MID (523978) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-153 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 2. Clear fault from HARRNG_MID (523978) b. 3. Drop generator from HARRNGTON2 (523972 ID 1) 24.0 kV bus b. 4. Drop load from HARRNGTON2 (523972 ID S1) 24.0 kV bus b. 5. Disconnect HARRNGTON2 (523972) 24.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523979_HARRNG_EST-ConID-SPS-151 | Single Phase Fault with Stuck Breaker on HARRNG_EST (523979) 230.0 kV bus a.Apply single-phase fault on HARRNG_EST (523979) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_EST (523979) 230.0 kV bus to PRINGLE (523267) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_EST (523979) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Disconnect HARRNG_EST (523979) 230.0 kV bus b. 4. Disconnect HARRNGTON3 (523973) 24.0 kV bus b. 5. Clear fault from HARRNG_EST (523979) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-524044_NICHOLS-ConID-SPS-134 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230.0 kV bus a.Apply single-phase fault on NICHOLS (524044) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 2. Open branch from HUTCHISON (523551) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 3. Clear fault from NICHOLS (524044) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-524267_BUSHLAND-ConID-SPS-148 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230.0 kV bus a.Apply single-phase fault on BUSHLAND (524267) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to WILDOR2_JUS6230.00 (524290) 230.0 kV bus CKT 1 b. 2. Trip switching device at bus 524267 (BUSHLAND) 230.0 kV bus b. 3. Disconnect BSHLND_TR1 (524263) 13.2 kV bus b. 4. Disconnect WILDORA_GEN10.6900 (524285) 0.69 kV bus b. 5. Disconnect GS-PHWD_GEN10.6900 (524287) 0.69 kV bus b. 6. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b.Run for 16.0 cycles and trip the following elements: b. 7. Open branch from BUSHLAND (524267) 230.0 kV bus to DEAFSMITH (524623) 230.0 kV bus CKT 1 b. 8. Clear fault from BUSHLAND (524267) b. 9. Disconnect WILDOR_WND (524275) 34.5 kV bus b. 10. Disconnect WILDOR_WND (524276) 230.0 kV bus b. 11. Disconnect GS-PHWDRNCH134.500 (524289) 34.5 kV bus b. 12. Disconnect WILDOR2_JUS6230.00 (524290) 230.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525213_SWISHER-ConID-SPS-146 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a.Apply single-phase fault on SWISHER (525213) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525213 (SWISHER) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 b. 3. Clear fault from SWISHER (525213) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525830_TUCO_INT-ConID-SPS-147 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a.Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525830 (TUCO_INT) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525830) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526935_YOAKUM-ConID-SPS-137 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a.Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 b. 3. Clear fault from YOAKUM (526935) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-109 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 2. Open branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 4. Disconnect MILO_WIND (527653) 0.7 kV bus b. 5. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 6. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 7. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 8. Clear fault from CROSSROADS (527656) b. 9. Drop generator from SAGSFT3_2.210.7000 (527605 ID 1) 0.7 kV bus b. 10. Drop generator from SAGSFT4_2.210.7000 (527607 ID 1) 0.7 kV bus b. 11. Drop generator from SAGSFT1_2.210.7000 (527614 ID 1) 0.7 kV bus b. 12. Drop generator from SAGSFT1_2.010.7000 (527615 ID 1) 0.7 kV bus b. 13. Drop generator from SAGSFT2_2.210.7000 (527617 ID 1) 0.7 kV bus b. 14. Drop generator from SAGSFT2_2.010.7000 (527618 ID 1) 0.7 kV bus b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 25. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 26. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 27. Disconnect SUB (527608) 34.5 kV bus b. 28. Disconnect SUB (527609) 34.5 kV bus b. 29. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 30. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 31. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 32. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 33. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 34. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 35. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 36. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 37. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 38. Disconnect SAGA_NCLTR3113.8 kV bus b. 39. Disconnect SAGA_NCLTR4113.8 kV bus b. 40. Disconnect SAGA_SCLTR1113.8 kV bus b. 41. Disconnect SAGA_SCLTR2113.8 kV bus b. 42. Disconnect SUB (527628) 34.5 kV bus b. 43. Disconnect SUB (527629) 34.5 kV bus b. 44. Disconnect CROSSROADS (527656) 345.0 kV bus b. 45. Disconnect RSVLT_WIND1134.500 (527658) 34.5 kV bus b. 46. Disconnect RSVLT_WIND2134.500 (527659) 34.5 kV bus b. 47. Disconnect RSVLT_COL1 (527660) 34.5 kV bus b. 48. Disconnect RSVLT_COL2 (527661) 34.5 kV bus b. 49. Disconnect RSVLT_TR1 (527662) 13.2 kV bus b. 50. Disconnect RSVLT_TR2 (527663) 13.2 kV bus b. 51. Disconnect RSVLT_COL1 (527666) 345.0 kV bus b. 52. Disconnect RSVLT_COL2 (527667) 345.0 kV bus b. 53. Disconnect MILO_CB (577120) 34.5 kV bus b. 54. Disconnect MILO_WND (577121) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-110 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Open branch from CROSSROADS (527656) 345.0 kV bus to SAGA_SCOL (527610) 345.0 kV bus CKT 1 b. 3. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 4. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 5. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 6. Disconnect SUB (527608) 34.5 kV bus b. 7. Disconnect SUB (527609) 34.5 kV bus b. 8. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 9. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 10. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 11. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 12. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 13. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 14. Clear fault from CROSSROADS (527656) b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 25. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 26. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 27. Disconnect SAGA_NCLTR3113.8 kV bus b. 28. Disconnect SAGA_NCLTR4113.8 kV bus b. 29. Disconnect SAGA_SCLTR1113.8 kV bus b. 30. Disconnect SAGA_SCLTR2113.8 kV bus b. 31. Disconnect SUB (527628) 34.5 kV bus b. 32. Disconnect SUB (527629) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-114 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-115 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-116 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 7. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527896_HOBBS_INT-ConID-SPS-119 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a.Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Open branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Disconnect HOBBS_TR3 (527895) 13.2 kV bus b. 4. Disconnect HOBBS_INT (527896) 345.0 kV bus b. 5. Clear fault from HOBBS_INT (527896) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527965_KIOWA-ConID-SPS-120 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b.Run for 16.0 cycles and trip the following elements: b. 2. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 5. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-527965_KIOWA-ConID-SPS-121 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 20.0 cycles and trip the following elements: b. 1. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-126 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-127 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 6. Disconnect RDRUNNER (528027) 345.0 kV bus b. 7. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-128 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-122 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-123 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus b. 7. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-124 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523097_HITCHLAND-523823_CARPENTER_Ckt1 | 3 Phase fault on HITCHLAND (523097) 345.0 kV a. Apply fault on HITCHLAND (523097) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523323_MCDWL_CREEK623000-523309_MOORE_CNTY_Ckt1 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523323_MCDWL_CREEK623000-523322_MCDWL_CREEK311500_3Winding | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MCDWL_CRKTR113.200 (523321) to trip transformer at MCDWL_CRKTR113.200 (523321) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-523323_MCDWL_CREEK623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-523869_CHAN+TASCOS623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-523979_HARRNG_EST_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-524010_ROLLHILLS_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523959_POTTER_CO-524267_BUSHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523961_POTTER_CO-523097_HITCHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523977_HARRNG_WST-524010_ROLLHILLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523977_HARRNG_WST-524044_NICHOLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523977_HARRNG_WST-524162_EAST_PLANT_3Winding | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 b. 2. Disconnect bus at EPLANT_TR3 (524160) to trip transformer at EPLANT_TR3 113.200 (524160) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523978_HARRNG_MID-523977_HARRNG_WST_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523978_HARRNG_MID-524044_NICHOLS_Ckt2 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523978_HARRNG_MID-524365_RANDALL_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523979_HARRNG_EST-523266_PRINGLE_3Winding | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 b. 2. Disconnect bus at PRINGLE_TR (523265) to trip transformer at PRINGLE_TR 113.200 (523265) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_523979_HARRNG_EST-523978_HARRNG_MID_Ckt1 | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Fault simulation crashes. | Disabled fault reclosing. No additional stability issues.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524415_AMA_SOUTH-524044_NICHOLS_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524415_AMA_SOUTH-524365_RANDALL_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524415_AMA_SOUTH-524414_AMA_SOUTH_3Winding | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at AMA_SO_TR1 (524410) to trip transformer at AMA_SO_TR1 113.200 (524410) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524746_CASTRO_CNTY311500-524734_DS-#21_Ckt1 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV a. Apply fault on CASTRO_CNTY3115.00 (524746) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 2. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524768_PLSNT_HILL-524770_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524768_PLSNT_HILL-524822_CURRY_Ckt1 | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 b. 2. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 3. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 c. 2. Reclose branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 d. 2. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524770_PLSNT_HILL-524768_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524770_PLSNT_HILL-524875_OASIS_Ckt1 | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524822_CURRY-524669_DS-#20_Ckt1 | 3 Phase fault on CURRY (524822) 115.0 kV a. Apply fault on CURRY (524822) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 2. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524874_OASIS-524764_NORRIS_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 b. 2. Drop load from bus FE-CHZPLT (524863) 115.0 kV bus b. 3. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 c. 2. Reclose branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 d. 2. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524874_OASIS-524790_CANNON_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 b. 2. Drop load from bus PERIMETER (524797) 115.0 kV bus b. 3. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 c. 2. Reclose branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 d. 2. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524874_OASIS-524875_OASIS_3Winding | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524874_OASIS-524924_PORTALES_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524875_OASIS-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524875_OASIS-524874_OASIS_3Winding | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524875_OASIS-524885_SN_JUAN_TAP623000_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524885_SN_JUAN_TAP623000-527483_CHAVES_CNTY623000_Ckt1 | 3 Phase fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV a. Apply fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524908_ROOSEVELT-524822_CURRY_Ckt2 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524908_ROOSEVELT-524909_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524908_ROOSEVELT-524924_PORTALES_Ckt1 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-524875_OASIS_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-524908_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt2 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_524909_ROOSEVELT-599955_PNM-DC6_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop switching device from bus PNM-DC6 (599955) 230.0 kV bus b. 2. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525192_KRESS_INT-525213_SWISHER_3Winding | 3 Phase fault on KRESS_INT (525192) 115.0 kV a. Apply fault on KRESS_INT (525192) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 b. 2. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525213_SWISHER-524415_AMA_SOUTH_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525213_SWISHER-525192_KRESS_INT_3Winding | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 2. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525213_SWISHER-525830_TUCO_INT_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525414_LAMTON-525413_LAMTON_3Winding | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMTON_TR1 (525412) to trip transformer at LAMTON_TR1 113.200 (525412) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525414_LAMTON-525446_RKYFORD_TP_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 b. 2. Drop load from bus LC-S_OLTON+3115.00 (525440) 115.0 kV bus b. 3. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 c. 2. Reclose branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 d. 2. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525414_LAMTON-525454_HALE_CNTY_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525414_LAMTON-525460_NEWHART_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525460_NEWHART-524746_CASTRO_CNTY311500_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525460_NEWHART-525192_KRESS_INT_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525460_NEWHART-525414_LAMTON_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525460_NEWHART-525461_NEWHART_3Winding | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525461_NEWHART-523959_POTTER_CO_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525461_NEWHART-525213_SWISHER_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525461_NEWHART-525460_NEWHART_3Winding | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525461_NEWHART-525481_PLANT_X_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525480_PLANT_X-525019_MULSHVLY_TP311500_Ckt1 | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525480_PLANT_X-525481_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-525461_NEWHART_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-525480_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt2 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-526435_SUNDOWN_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525481_PLANT_X-760498_G17-146-TAP_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525549_TOLK_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525586_NEEDMORE_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525636_LAMB_CNTY_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 b. 2. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525637_LAMB_CNTY_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525531_TOLK-525830_TUCO_INT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525549_TOLK-523961_POTTER_CO_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525549_TOLK-525531_TOLK_3Winding | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525549_TOLK-527656_CROSSROADS_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525586_NEEDMORE-525581_BLUECLDGEN_CktZ1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 b. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 b. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 b. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 b. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 c. 2. Reclose branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 c. 3. Reclose branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 c. 4. Reclose branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 c. 5. Reclose branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 d. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 d. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 d. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 d. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525586_NEEDMORE-526935_YOAKUM_Ckt1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525635_LAMB_CNTY-525636_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525635) 69.0 kV a. Apply fault on LAMB_CNTY (525635) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525636_LAMB_CNTY-525480_PLANT_X_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525636_LAMB_CNTY-525531_TOLK_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525636_LAMB_CNTY-525635_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525636_LAMB_CNTY-526020_HOCKLEY_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525828_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525828) 115.0 kV a. Apply fault on TUCO_INT (525828) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-525213_SWISHER_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-525531_TOLK_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-525828_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-525832_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR1 (525824) to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-526161_CARLISLE_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525830_TUCO_INT-526337_JONES_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-515458_BORDER_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 2. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR2 (525825) to trip transformer at TUCO_TR2 113.200 (525825) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-526936_YOAKUM_345_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526020_HOCKLEY-526019_HOCKLEY_3Winding | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOCKLEY_TR1113.200 (526017) to trip transformer at HOCKLEY_TR1113.200 (526017) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526020_HOCKLEY-526434_SUNDOWN_Ckt1 | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 b. 2. Drop load from bus LC-OPDYKE (526036) 115.0 kV bus b. 3. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 c. 2. Reclose branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 d. 2. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526435_SUNDOWN-526434_SUNDOWN_3Winding | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNDOWN_TR1113.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526435_SUNDOWN-526525_WOLFFORTH_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526435_SUNDOWN-526935_YOAKUM_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 b. 2. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 3. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. 2. Reclose branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. 2. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526934_YOAKUM-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526934) 115.0 kV a. Apply fault on YOAKUM (526934) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-525586_NEEDMORE_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-526460_AMOCO_SS_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 2. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-526934_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-526936_YOAKUM_345_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-527009_BRU_SUB_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-527028_INK_BASIN_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526935_YOAKUM-527149_MUSTANG_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526936_YOAKUM_345-525832_TUCO_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526936_YOAKUM_345-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_526936_YOAKUM_345-527896_HOBBS_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527009_BRU_SUB-527010_OXYBRU_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OXYBRU (527010) 230.0 kV bus b. 2. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527009_BRU_SUB-527011_XTO_MAHONEY623000_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527011_XTO_MAHONEY623000-526784_AMOCOWASSON623000_Ckt1 | 3 Phase fault on XTO_MAHONEY6230.00 (527011) 230.0 kV a. Apply fault on XTO_MAHONEY6230.00 (527011) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 2. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 3. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 4. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-239 GEN1 & GEN2 (761358 & 761361) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527149_MUSTANG-527276_SEMINOLE_Ckt1 | 3 Phase fault on MUSTANG (527149) 230.0 kV a. Apply fault on MUSTANG (527149) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527656_CROSSROADS-527802_EDDY_CNTY_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt2 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527802_EDDY_CNTY-527799_EDDY_NORTH_3Winding | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at EDDY_TR (527796) to trip transformer at EDDY_TR 113.200 (527796) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527802_EDDY_CNTY-527965_KIOWA_Ckt1 | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527894_HOBBS_INT-527896_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527894_HOBBS_INT-528604_ANDREWS_Ckt1 | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-527894_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-527965_KIOWA_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_527965_KIOWA-528185_N_LOVING_Ckt1 | 3 Phase fault on KIOWA (527965) 345.0 kV a. Apply fault on KIOWA (527965) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_762216_G17-151TAP-762467_G18-015-TAP_Ckt1 | 3 Phase fault on G17-151TAP (762216) 345.0 kV a. Apply fault on G17-151TAP (762216) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-523097_HITCHLAND | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Trip branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-523959_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a. Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-523961_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523961) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524746_CASTRO_CNTY311500 | Single Phase Fault with Stuck Breaker on CASTRO_CNTY3115.00 (524746) 115.0 kV bus a. Apply single-phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CASTRO_TR1 (524744) 13.2 kV bus to trip transformer at CASTRO_CNTY2 (524745) 69.0 kV bus b. 2. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 3. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 kV bus to DS-#21 (524734) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524768_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524768) 115.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524768) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus b. 2. Trip branch from PLSNT_HILL (524768) 115.0 kV bus to E_CLOVIS (524773) 115.0 kV bus CKT 1 b. 3. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 4. Trip branch from E_CLOVIS (524773) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524770_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524770) 230.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524770) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524822_CURRY | Single Phase Fault with Stuck Breaker on CURRY (524822) 115.0 kV bus a. Apply single-phase fault on CURRY (524822) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CURRY (524822) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 2 b. 2. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 3. Trip branch from CURRY (524822) 115.0 kV bus to DS-#20 (524669) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524875_OASIS | Single Phase Fault with Stuck Breaker on OASIS (524875) 230.0 kV bus a. Apply single-phase fault on OASIS (524875) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524908_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524908) 115.0 kV bus a. Apply single-phase fault on ROOSEVELT (524908) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus b. 2. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524909_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524909) 230.0 kV bus a. Apply single-phase fault on ROOSEVELT (524909) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 b. 2. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-524924_PORTALES | Single Phase Fault with Stuck Breaker on PORTALES (524924) 115.0 kV bus a. Apply single-phase fault on PORTALES (524924) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PORTALES (524924) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 1 b. 2. Trip branch from PORTALES (524924) 115.0 kV bus to OASIS (524874) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525192_KRESS_INT | Single Phase Fault with Stuck Breaker on KRESS_INT (525192) 115.0 kV bus a. Apply single-phase fault on KRESS_INT (525192) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 kV bus to SWISHER (525212) 115.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from KRESS_INT (525192) 115.0 kV bus to NEWHART (525460) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525213_SWISHER | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a. Apply single-phase fault on SWISHER (525213) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from SWISHER (525212) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525460_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525460) 115.0 kV bus a. Apply single-phase fault on NEWHART (525460) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 b. 2. Disconnect NEWHART_TR2113.200 (525458) 13.2 kV bus to trip transformer at NEWHART_TR2113.200 (525458) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525461_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525461) 230.0 kV bus a. Apply single-phase fault on NEWHART (525461) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 b. 2. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525480_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525480) 115.0 kV bus a. Apply single-phase fault on PLANT_X (525480) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLANTX_TR1 (525479) 13.2 kV bus to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus b. 2. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525481_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525481) 230.0 kV bus a. Apply single-phase fault on PLANT_X (525481) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 b. 2. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525531_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525531) 230.0 kV bus a. Apply single-phase fault on TOLK (525531) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus b. 2. Disconnect TOLK_TR (525538) 13.2 kV bus to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525549_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525549) 345.0 kV bus a. Apply single-phase fault on TOLK (525549) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525635_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525635) 69.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525635) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR2 (525632) 13.2 kV bus to trip transformer at LAMB_TR2 113.200 (525632) 13.2 kV bus b. 2. Disconnect LAMB_TR1 (525631) 13.2 kV bus to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525636_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525636) 115.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525636) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR3 (525633) 13.2 kV bus to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 3. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525828_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525828) 115.0 kV bus a. Apply single-phase fault on TUCO_INT (525828) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TUCO_TR4 (525821) 13.2 kV bus to trip transformer at TUCO_TR4 113.200 (525821) 13.2 kV bus b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525830_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a. Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-526934_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526934) 115.0 kV bus a. Apply single-phase fault on YOAKUM (526934) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus to trip transformer at YOAKUM_TR1 113.200 (526931) 13.2 kV bus b. 2. Disconnect YOAKUM_TR2 (526932) 13.2 kV bus to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-526935_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a. Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-526936_YOAKUM_345 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-527149_MUSTANG | Single Phase Fault with Stuck Breaker on MUSTANG (527149) 230.0 kV bus a. Apply single-phase fault on MUSTANG (527149) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to AMOCOWASSON6 (526784) 230.0 kV bus CKT 1 b. 2. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-527656_CROSSROADS | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-527894_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527894) 230.0 kV bus a. Apply single-phase fault on HOBBS_INT (527894) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect HOBBS_TR3 (527895) 13.2 kV bus to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus b. 2. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-527896_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a. Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-527965_KIOWA | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 2. Trip branch from KIOWA (527965) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-528027_RDRUNNER | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-108426 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1 (523111) 115.0 kV bus b. 5. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-92600 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-523097_HITCHLAND-ConID-108427 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Disconnect HITCHLAND (523097) 345.0 kV bus b. 3. Trip transformer from HITCHLD_TR2113.200 (523094) 13.2 kV bus to HITCHLAND (523095) 230.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-523124_GRPLNS-CB4-134500-ConID-108428 | Single Phase Fault with Stuck Breaker on GRPLNS-CB4-134.500 (523124) 34.5 kV bus a. Apply single-phase fault on GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect NOBLE_TR (523102) 13.8 kV bus b. 3. Disconnect NOBLE_WND (523103) 115.0 kV bus b. 4. Disconnect GRPLNS-HV4-3115.00 (523130) 115.0 kV bus b. 5. Disconnect GRPLNS-HV2-3115.00 (523131) 115.0 kV bus b. 6. Disconnect GRPLNS-LV4-134.500 (523127) 34.5 kV bus b. 7. Disconnect GRPLNS-LV2-134.500 (523129) 34.5 kV bus b. 8. Disconnect GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. 9. Disconnect GRPLNS-CB2-134.500 (523126) 34.5 kV bus b. 10. Disconnect GRPLNS-WT4-10.5750 (523121) 0.574999988079071 kV bus b. 11. Disconnect GRPLNS-WT2-10.5750 (523123) 0.574999988079071 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-523961_POTTER_CO-ConID-108433 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Trip transformer from POTTER_TR (523957) 13.2 kV bus to POTTER_CO (523959) 230.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 3. Disconnect POTTER_CO (523961) 345.0 kV bus b. 4. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 5. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527656_CROSSROADS-ConID-108421 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Trip line from RSVLT_CC_E (527655) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 4. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 5. Disconnect MILO_WIND (527653) 0.7 kV bus b. 6. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 7. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 8. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 9. Disconnect CROSSROADS (527656) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108422 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108423 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108424 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108440 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527965_KIOWA-ConID-108429 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-527965_KIOWA-ConID-108441 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528027_RDRUNNER-ConID-108445 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRUNNER (528027) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528027_RDRUNNER-ConID-108447 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect PHANTOM (528011) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108430 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108431 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108432 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108443 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-118 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to BVRCNTY7 (515554) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus b. 5. Disconnect NOVUS1 (523111) 115.0 kV bus b. 6. Disconnect NOVUS1 (523112) 345.0 kV bus b. 7. Disconnect G06-44 (560577) 115.0 kV bus b. 8. Disconnect NOVUS1_TR2 (560578) 13.8 kV bus b. 9. Disconnect G06-44-2 (560581) 34.5 kV bus b. 10. Disconnect G06-44-3 (560582) 34.5 kV bus b. 11. Disconnect G06-44-4 (560583) 34.5 kV bus b. 12. Disconnect G06-44-2 (560584) 4.16 kV bus b. 13. Disconnect G06-44-3 (560585) 4.16 kV bus b. 14. Disconnect G06-44-4 (560586) 4.16 kV bus b. 15. Drop generator from NOVUS_WND (523107 ID 1) 4.16 kV bus b. 16. Drop generator from G06-44-2 (560584 ID 1) 4.16 kV bus b. 17. Drop generator from G06-44-3 (560585 ID 1) 4.16 kV bus b. 18. Drop generator from G06-44-4 (560586 ID 1) 4.16 kV bus b. 19. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-142 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b. 3. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523853_FINNEY-ConID-SPS-117 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345.0 kV bus a.Apply single-phase fault on FINNEY (523853) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOLCOMB7 (531449) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 2. Open branch from CARPENTER (523823) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 3. Disconnect FINNEY (523853) 345.0 kV bus b. 4. Disconnect LAMAR7 (599950) 345.0 kV bus b. 5. Disconnect LAMAR (599951) 345.0 kV bus b. 6. Disconnect BUFF_DUNES (523118) 345.0 kV bus b. 7. Disconnect BUFF_DN_TR1113.200 (523114) 13.2 kV bus b. 8. Disconnect BUFF_DN_TR2113.200 (523115) 13.2 kV bus b. 9. Disconnect BUFF_DUNES1134.500 (523116) 34.5 kV bus b. 10. Disconnect BUFF_DUNES2134.500 (523117) 34.5 kV bus b. 11. Clear fault from FINNEY (523853) b. 12. Drop generator from BUFF_DUNES230.6900 (523061 ID 1) 0.69 kV bus b. 13. Drop generator from BUFF_DUNES130.6900 (523062 ID 1) 0.69 kV bus b. 14. Disconnect BUFF_DUNES230.6900 (523061) 0.69 kV bus b. 15. Disconnect BUFF_DUNES130.6900 (523062) 0.69 kV bus b. 16. Disconnect BUFF_DUNES2234.500 (523063) 34.5 kV bus b. 17. Disconnect BUFF_DUNES1234.500 (523064) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523959_POTTER_CO-ConID-SPS-136 | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a.Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 2. Open branch from ROLLHILLS (524010) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Clear fault from POTTER_CO (523959) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-125 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Disconnect POTTER_TR (523957) 13.2 kV bus b. 4. Disconnect POTTER_CO (523961) 345.0 kV bus b. 5. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 6. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 7. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 8. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 9. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 10. Clear fault from POTTER_CO (523961) b. 11. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-144 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect POTTER_TR (523957) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Clear fault from POTTER_CO (523961) b.Run for 5.0 cycles and trip the following elements: b. 4. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 5. Disconnect POTTER_TR (523957) 13.2 kV bus b. 6. Disconnect POTTER_CO (523961) 345.0 kV bus b. 7. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 8. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 9. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 10. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 11. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 12. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523977_HARRNG_WST-ConID-SPS-149 | Single Phase Fault with Stuck Breaker on HARRNG_WST (523977) 230.0 kV bus a.Apply single-phase fault on HARRNG_WST (523977) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_WST (523977) 230.0 kV bus to EAST_PLANT (524163) 230.0 kV bus CKT 1 b. 3. Open branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 4. Disconnect HARRNG_WST (523977) 230.0 kV bus b. 5. Disconnect HARRNGTON1 (523971) 24.0 kV bus b. 6. Clear fault from HARRNG_WST (523977) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-150 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 3. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 4. Disconnect HARRNGTON2 (523972) 24.0 kV bus b. 5. Clear fault from HARRNG_MID (523978) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-153 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 2. Clear fault from HARRNG_MID (523978) b. 3. Drop generator from HARRNGTON2 (523972 ID 1) 24.0 kV bus b. 4. Drop load from HARRNGTON2 (523972 ID S1) 24.0 kV bus b. 5. Disconnect HARRNGTON2 (523972) 24.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-523979_HARRNG_EST-ConID-SPS-151 | Single Phase Fault with Stuck Breaker on HARRNG_EST (523979) 230.0 kV bus a.Apply single-phase fault on HARRNG_EST (523979) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_EST (523979) 230.0 kV bus to PRINGLE (523267) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_EST (523979) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Disconnect HARRNG_EST (523979) 230.0 kV bus b. 4. Disconnect HARRNGTON3 (523973) 24.0 kV bus b. 5. Clear fault from HARRNG_EST (523979) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-524044_NICHOLS-ConID-SPS-134 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230.0 kV bus a.Apply single-phase fault on NICHOLS (524044) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 2. Open branch from HUTCHISON (523551) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 3. Clear fault from NICHOLS (524044) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-524267_BUSHLAND-ConID-SPS-148 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230.0 kV bus a.Apply single-phase fault on BUSHLAND (524267) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to WILDOR2_JUS6230.00 (524290) 230.0 kV bus CKT 1 b. 2. Trip switching device at bus 524267 (BUSHLAND) 230.0 kV bus b. 3. Disconnect BSHLND_TR1 (524263) 13.2 kV bus b. 4. Disconnect WILDORA_GEN10.6900 (524285) 0.69 kV bus b. 5. Disconnect GS-PHWD_GEN10.6900 (524287) 0.69 kV bus b. 6. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b.Run for 16.0 cycles and trip the following elements: b. 7. Open branch from BUSHLAND (524267) 230.0 kV bus to DEAFSMITH (524623) 230.0 kV bus CKT 1 b. 8. Clear fault from BUSHLAND (524267) b. 9. Disconnect WILDOR_WND (524275) 34.5 kV bus b. 10. Disconnect WILDOR_WND (524276) 230.0 kV bus b. 11. Disconnect GS-PHWDRNCH134.500 (524289) 34.5 kV bus b. 12. Disconnect WILDOR2_JUS6230.00 (524290) 230.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525213_SWISHER-ConID-SPS-146 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a.Apply single-phase fault on SWISHER (525213) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525213 (SWISHER) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 b. 3. Clear fault from SWISHER (525213) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525830_TUCO_INT-ConID-SPS-147 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a.Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525830 (TUCO_INT) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525830) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526935_YOAKUM-ConID-SPS-137 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a.Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 b. 3. Clear fault from YOAKUM (526935) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-109 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 2. Open branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 4. Disconnect MILO_WIND (527653) 0.7 kV bus b. 5. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 6. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 7. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 8. Clear fault from CROSSROADS (527656) b. 9. Drop generator from SAGSFT3_2.210.7000 (527605 ID 1) 0.7 kV bus b. 10. Drop generator from SAGSFT4_2.210.7000 (527607 ID 1) 0.7 kV bus b. 11. Drop generator from SAGSFT1_2.210.7000 (527614 ID 1) 0.7 kV bus b. 12. Drop generator from SAGSFT1_2.010.7000 (527615 ID 1) 0.7 kV bus b. 13. Drop generator from SAGSFT2_2.210.7000 (527617 ID 1) 0.7 kV bus b. 14. Drop generator from SAGSFT2_2.010.7000 (527618 ID 1) 0.7 kV bus b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 25. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 26. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 27. Disconnect SUB (527608) 34.5 kV bus b. 28. Disconnect SUB (527609) 34.5 kV bus b. 29. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 30. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 31. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 32. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 33. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 34. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 35. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 36. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 37. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 38. Disconnect SAGA_NCLTR3113.8 kV bus b. 39. Disconnect SAGA_NCLTR4113.8 kV bus b. 40. Disconnect SAGA_SCLTR1113.8 kV bus b. 41. Disconnect SAGA_SCLTR2113.8 kV bus b. 42. Disconnect SUB (527628) 34.5 kV bus b. 43. Disconnect SUB (527629) 34.5 kV bus b. 44. Disconnect CROSSROADS (527656) 345.0 kV bus b. 45. Disconnect RSVLT_WIND1134.500 (527658) 34.5 kV bus b. 46. Disconnect RSVLT_WIND2134.500 (527659) 34.5 kV bus b. 47. Disconnect RSVLT_COL1 (527660) 34.5 kV bus b. 48. Disconnect RSVLT_COL2 (527661) 34.5 kV bus b. 49. Disconnect RSVLT_TR1 (527662) 13.2 kV bus b. 50. Disconnect RSVLT_TR2 (527663) 13.2 kV bus b. 51. Disconnect RSVLT_COL1 (527666) 345.0 kV bus b. 52. Disconnect RSVLT_COL2 (527667) 345.0 kV bus b. 53. Disconnect MILO_CB (577120) 34.5 kV bus b. 54. Disconnect MILO_WND (577121) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-110 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Open branch from CROSSROADS (527656) 345.0 kV bus to SAGA_SCOL (527610) 345.0 kV bus CKT 1 b. 3. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 4. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 5. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 6. Disconnect SUB (527608) 34.5 kV bus b. 7. Disconnect SUB (527609) 34.5 kV bus b. 8. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 9. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 10. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 11. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 12. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 13. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 14. Clear fault from CROSSROADS (527656) b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 25. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 26. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 27. Disconnect SAGA_NCLTR3113.8 kV bus b. 28. Disconnect SAGA_NCLTR4113.8 kV bus b. 29. Disconnect SAGA_SCLTR1113.8 kV bus b. 30. Disconnect SAGA_SCLTR2113.8 kV bus b. 31. Disconnect SUB (527628) 34.5 kV bus b. 32. Disconnect SUB (527629) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-114 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-115 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-116 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 7. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527896_HOBBS_INT-ConID-SPS-119 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a.Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Open branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Disconnect HOBBS_TR3 (527895) 13.2 kV bus b. 4. Disconnect HOBBS_INT (527896) 345.0 kV bus b. 5. Clear fault from HOBBS_INT (527896) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527965_KIOWA-ConID-SPS-120 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b.Run for 16.0 cycles and trip the following elements: b. 2. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 5. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-527965_KIOWA-ConID-SPS-121 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 20.0 cycles and trip the following elements: b. 1. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-126 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-127 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 6. Disconnect RDRUNNER (528027) 345.0 kV bus b. 7. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-128 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-122 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-123 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus b. 7. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-124 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512753_TONNEC2-512745_SSLINC2_Ckt1 | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 b. 5. Drop load from bus SSNORT2 (512746) 69.0 kV bus b. 6. Drop load from bus SSLINC2 (512745) 69.0 kV bus b. 7. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 c. 2. Reclose branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 c. 3. Reclose branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 c. 4. Reclose branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 c. 5. Reclose branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 d. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 d. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 d. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 d. 5. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512753_TONNEC2-512751_TONECE5_3Winding | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512751_TONECE5-512643_SILMCTY5_Ckt1 | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512751_TONECE5-512750_TONECE7_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512751_TONECE5-512753_TONNEC2_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512750_TONECE7-512650_GRDA1_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512750_TONECE7-506935_FLINTCR7_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512750_TONECE7-512751_TONECE5_3Winding | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506935_FLINTCR7-506929_ECNTRTN5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 b. 2. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 3. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 4. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 5. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 c. 2. Reclose branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 3. Reclose branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 d. 2. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506935_FLINTCR7-549984_BROOKLINE_Ckt1 | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506935_FLINTCR7-506934_FLINTCR5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512643_SILMCTY5-506948_SILOAM_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512643_SILMCTY5-512714_KANSATP5_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512643_SILMCTY5-512820_SILMCTY2_3Winding | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512650_GRDA1-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512650_GRDA1-512865_GREC_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512650_GRDA1-512656_GRDA1_3Winding | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_549984_BROOKLINE-300045_7MORGAN_Ckt1 | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_549984_BROOKLINE-549969_BROOKLINE_3Winding | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at BRKLNE (549989) to trip transformer at BRKLNE XF2 113.200 (549989) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-506990_GREENHOUSE_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 b. 2. Drop load from bus GENTRY (504201) 161.0 kV bus b. 3. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 b. 4. Drop load from bus BEN279_5 (506960) 161.0 kV bus b. 5. Drop load from bus GREENHOUSE (506990) 161.0 kV bus b. 6. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. 2. Reclose branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 c. 3. Reclose branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. 2. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 d. 3. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-506957_TONTITN5_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-547484_DEC392_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-504202_SILOAMSP_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SILOAMSP (504202) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-506935_FLINTCR7_3Winding | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-506948_SILOAM_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506948_SILOAM-506944_CHAMSPR5_Ckt1 | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506948_SILOAM-506936_GREENLD2_3Winding | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SILOAM-1 (506917) to trip transformer at SILOAM-1 13.200 (506917) 13.2 kV bus b. 2. Drop switching device from bus SILOAM (506973) 69.0 kV bus b. 3. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 b. 4. Drop load from bus LINCOLN2 (506972) 69.0 kV bus b. 5. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 b. 6. Drop load from bus PRGROVE2 (506941) 69.0 kV bus b. 7. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 c. 2. Reclose branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 c. 3. Reclose branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 d. 2. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 d. 3. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512820_SILMCTY2-512730_SSSWES2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SSSWES2 (512730) 69.0 kV bus b. 2. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512820_SILMCTY2-512643_SILMCTY5_3Winding | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512820_SILMCTY2-512744_SSMOSS2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 b. 2. Drop load from bus SSMOSS2 (512744) 69.0 kV bus b. 3. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 c. 2. Reclose branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 d. 2. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt2 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300740_7SPORTSMAN-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512865_GREC-513596_IGLOOV_Ckt1 | 3 Phase fault on GREC (512865) 345.0 kV a. Apply fault on GREC (512865) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-512742_WMAIN_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus WMAIN (512742) 161.0 kV bus b. 2. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-512650_GRDA1_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300045_7MORGAN-300949_7JASPER_Ckt1 | 3 Phase fault on 7MORGAN (300045) 345.0 kV a. Apply fault on 7MORGAN (300045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_549969_BROOKLINE-505492_SPRGFLD5_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_549969_BROOKLINE-549955_JUNCTION_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506957_TONTITN5-504010_ELMSPRGS_Ckt1 | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506957_TONTITN5-506945_CHAMSPR7_3Winding | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus b. 2. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506944_CHAMSPR5-506992_WEDINGTON_Ckt1 | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506944_CHAMSPR5-506945_CHAMSPR7_3Winding | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512714_KANSATP5-512635_KERR_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512714_KANSATP5-512643_SILMCTY5_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512714_KANSATP5-512715_KANSAS_3Winding | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 b. 2. Disconnect bus at KANSAS1 (512736) to trip transformer at KANSAS1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506929_ECNTRTN5-506935_FLINTCR7_3Winding | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 b. 4. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 5. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 6. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 7. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 2. Reclose branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 c. 3. Reclose branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 2. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 d. 3. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506929_ECNTRTN5-506963_BENT_SL5_Ckt1 | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 2. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513596_IGLOOV-513591_HERRON_3Winding | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus b. 2. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513596_IGLOOV-509852_TNO--7_Ckt1 | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506945_CHAMSPR7-509745_CLARKSV7_Ckt1 | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506945_CHAMSPR7-506957_TONTITN5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 b. 2. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506945_CHAMSPR7-506944_CHAMSPR5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512751_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a. Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 b. 2. Disconnect TONECE1 (512752) 13.2 kV bus to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512750_TONECE7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a. Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506935_FLINTCR7 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 3. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 4. Trip branch from SHIPERD5 (506980) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 5. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 6. Trip branch from CENTRTN5 (506952) 161.0 kV bus to ECNTRTN5 (506929) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512643_SILMCTY5 | Single Phase Fault with Stuck Breaker on SILMCTY5 (512643) 161.0 kV bus a. Apply single-phase fault on SILMCTY5 (512643) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILSPWW5 (512642) 161.0 kV bus CKT 1 b. 3. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 4. Trip branch from SILSPWW5 (512642) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512650_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a. Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-549984_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549984) 345.0 kV bus a. Apply single-phase fault on BROOKLINE (549984) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 b. 2. Disconnect BRKLNE (549988) 13.2 kV bus to trip transformer at BRKLNE XF1 113.200 (549988) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506934_FLINTCR5 | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161.0 kV bus a. Apply single-phase fault on FLINTCR5 (506934) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 kV bus to GENTRY (504201) 161.0 kV bus CKT 1 b. 3. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506948_SILOAM | Single Phase Fault with Stuck Breaker on SILOAM (506948) 161.0 kV bus a. Apply single-phase fault on SILOAM (506948) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 b. 2. Trip branch from SILOAM (506948) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512656_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 8. Disconnect GRDA2 (512826) 13.8 kV bus to trip transformer at GRDA2 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-300045_7MORGAN | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345.0 kV bus a. Apply single-phase fault on 7MORGAN (300045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7MORGAN (300045) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-549969_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549969) 161.0 kV bus a. Apply single-phase fault on BROOKLINE (549969) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 b. 2. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506957_TONTITN5 | Single Phase Fault with Stuck Breaker on TONTITN5 (506957) 161.0 kV bus a. Apply single-phase fault on TONTITN5 (506957) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 b. 2. Disconnect TONTITN1 (506958) 13.8 kV bus to trip transformer at TONTITN1 13.8 kV bus b. 3. Trip branch from TONTITN7 (506959) 345.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506944_CHAMSPR5 | Single Phase Fault with Stuck Breaker on CHAMSPR5 (506944) 161.0 kV bus a. Apply single-phase fault on CHAMSPR5 (506944) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 b. 2. Disconnect CHAMSPR1 (506919) 13.8 kV bus to trip transformer at CHAMSPR1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514803_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a. Apply single-phase fault on SOONER (514803) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-506929_ECNTRTN5 | Single Phase Fault with Stuck Breaker on ECNTRTN5 (506929) 161.0 kV bus a. Apply single-phase fault on ECNTRTN5 (506929) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 kV bus to SHIPERD5 (506980) 161.0 kV bus CKT 1 b. 4. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 5. Trip branch from SHIPERD7 (506979) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 b. 6. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 7. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to BENT_SL5 (506963) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515576_RANCHRD7-515621_OPENSKY7_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515576_RANCHRD7-514803_SOONER_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514803_SOONER-560056_G15-066T_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514803_SOONER-509755_WEKIWA-7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514803_SOONER-516010_PINTAIL7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514803_SOONER-514802_SOONER_3Winding | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SOONER (515760) to trip transformer at SOONER 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514803_SOONER-587804_G16-119-TAP_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515621_OPENSKY7-560053_G15-052T_Ckt1 | 3 Phase fault on OPENSKY7 (515621) 345.0 kV a. Apply fault on OPENSKY7 (515621) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509755_WEKIWA-7-509757_WEKIWA-4_3Winding | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WEKIW1-1 (509879) to trip transformer at WEKIW1-1 34.500 (509879) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509755_WEKIWA-7-509870_SAPLPRD7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509755_WEKIWA-7-509852_TNO--7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560056_G15-066T-512694_CLEVLND7_Ckt1 | 3 Phase fault on G15-066T (560056) 345.0 kV a. Apply fault on G15-066T (560056) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514802_SOONER-514798_SNRPMPT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514802_SOONER-514704_MILLERT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560053_G15-052T-532794_ROSEHIL7_Ckt1 | 3 Phase fault on G15-052T (560053) 345.0 kV a. Apply fault on G15-052T (560053) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514802_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514802) 138.0 kV bus a. Apply single-phase fault on SOONER (514802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_763113_G18-079-TAP-512734_FARML_Ckt1 | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_763113_G18-079-TAP-510380_DELWARE7_3Winding | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 b. 2. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512734_FARML-510378_SCOFCTY4_Ckt1 | 3 Phase fault on FARML (512734) 138.0 kV a. Apply fault on FARML (512734) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510380_DELWARE7-510406_NES-7_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510380_DELWARE7-532793_NEOSHO_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510380_DELWARE7-763113_G18-079-TAP_3Winding | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus b. 2. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510378_SCOFCTY4-510422_COFFEYT4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510378_SCOFCTY4-510420_SCOFFEYV4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SCOFFEYV4 (510420) 138.0 kV bus b. 2. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510406_NES-7-509852_TNO--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510406_NES-7-509807_ONETA--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532793_NEOSHO-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532793_NEOSHO-542981_LACYGNE7_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532793_NEOSHO-533021_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532793_NEOSHO-532777_G17-009-TAP_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532793_NEOSHO-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510422_COFFEYT4-533002_DEARING4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510422_COFFEYT4-510391_BV-SE--4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 b. 2. Drop load from bus NBVILLE4 (510386) 138.0 kV bus b. 3. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 c. 2. Reclose branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 d. 2. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt2 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt1 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509852_TNO--7-509895_TNO2-4_3Winding | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_542981_LACYGNE7-542968_STILWEL7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_542981_LACYGNE7-542965_WGRDNR7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533021_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533021_NEOSHO-533022_NEOSHON4_CktZ1 | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532937_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532937_NEOSHO-547469_RIV4525_Ckt1 | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533020_NEOSHOS4-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEOSH5 (532959) to trip transformer at NEOSH5 1 13.200 (532959) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533020_NEOSHOS4-533003_LIBERTY4_Ckt1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 b. 2. Drop load from bus TV1MNDV4 (533008) 138.0 kV bus b. 3. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 c. 2. Reclose branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 d. 2. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533020_NEOSHOS4-533021_NEOSHO_CktZ1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533022_NEOSHON4-588664_G17-022-TAP_Ckt1 | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 b. 2. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 3. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 4. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 5. Drop switching device from bus NEPARSN4 (533005) 138.0 kV bus b. 6. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 c. 2. Reclose branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 d. 2. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_533022_NEOSHON4-533768_NEOSHON2_3Winding | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEC (532711) to trip transformer at NEC U3 12.000 (532711) 12.0 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510380_DELWARE7 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510378_SCOFCTY4 | Single Phase Fault with Stuck Breaker on SCOFCTY4 (510378) 138.0 kV bus a. Apply single-phase fault on SCOFCTY4 (510378) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510406_NES-7 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 b. 2. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-532793_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532793) 345.0 kV bus a. Apply single-phase fault on NEOSHO (532793) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509807_ONETA--7 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509852_TNO--7 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TNO2-1 (509894) 34.5 kV bus to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus b. 2. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-542981_LACYGNE7 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a. Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-533021_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (533021) 138.0 kV bus a. Apply single-phase fault on NEOSHO (533021) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532824) 13.8 kV bus to trip transformer at N345 1 1 13.8 kV bus b. 2. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-532937_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532937) 161.0 kV bus a. Apply single-phase fault on NEOSHO (532937) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510907_PITTSB-7-514809_JOHNCO_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510907_PITTSB-7-515045_SEMINOL7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510907_PITTSB-7-515422_C-RIVER7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510907_PITTSB-7-510911_VALIANT7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510911_VALIANT7-508298_LYDIA_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510911_VALIANT7-510918_VALIANT4_3Winding | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at VALN3-1 (510939) to trip transformer at VALN3-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510911_VALIANT7-521157_HUGO_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510911_VALIANT7-508072_NWTXARK7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514809_JOHNCO-514808_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510907_PITTSB-7 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514809_JOHNCO-515136_SUNNYSD7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514809_JOHNCO-516006_DMNDSPG7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt2 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_3Winding | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SEMINO11 (515756) to trip transformer at SEMINO11 14.400 (515756) 14.399999618530273 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515045_SEMINOL7-514908_ARCADIA7_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515422_C-RIVER7-510951_TALAWANDA_3Winding | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at C-RIVER1 (510947) to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515422_C-RIVER7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508298_LYDIA-508359_WELSH_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508298_LYDIA-508072_NWTXARK7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510918_VALIANT4-510866_V-WEYCO4_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510918_VALIANT4-520948_HUGO_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515136_SUNNYSD7-511568_TERRYRD7_Ckt1 | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515136_SUNNYSD7-515135_SUNNYSD4_3Winding | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNYSD (515405) to trip transformer at SUNYSD 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514808_JOHNCO-514809_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514808_JOHNCO-515120_RUSSET-4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514808_JOHNCO-515150_CANEYCK4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514808_JOHNCO-515122_SXMLCKT4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514934_DRAPER-514933_DRAPER_3Winding | 3 Phase fault on DRAPER (514934) 345.0 kV a. Apply fault on DRAPER (514934) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DRAPER41 (515721) to trip transformer at DRAPER41 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510911_VALIANT7 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 2. Disconnect VALN2-1 (510938) 13.8 kV bus to trip transformer at VALN2-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514809_JOHNCO | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a. Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect JOHNCO11 (514810) 13.8 kV bus to trip transformer at JOHNCO11 13.8 kV bus b. 2. Trip branch from JOHNCO (514809) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515045_SEMINOL7 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a. Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 b. 2. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515422_C-RIVER7 | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345.0 kV bus a. Apply single-phase fault on C-RIVER7 (515422) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect C-RIVER1 (510947) 13.8 kV bus to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 kV bus to TALAWANDA (510951) 138.0 kV bus CKT 1 b. 3. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-510918_VALIANT4 | Single Phase Fault with Stuck Breaker on VALIANT4 (510918) 138.0 kV bus a. Apply single-phase fault on VALIANT4 (510918) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 kV bus to V-WEYCO4 (510866) 138.0 kV bus CKT 1 b. 4. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515136_SUNNYSD7 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Disconnect SUNYSD (515405) 13.8 kV bus to trip transformer at SUNYSD 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514934_DRAPER | Single Phase Fault with Stuck Breaker on DRAPER (514934) 345.0 kV bus a. Apply single-phase fault on DRAPER (514934) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DRAPER31 (515720) 13.8 kV bus to trip transformer at DRAPER31 13.8 kV bus b. 2. Disconnect DRAPER41 (515721) 13.8 kV bus to trip transformer at DRAPER41 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508298_LYDIA-510911_VALIANT7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508072_NWTXARK7-507454_TURK_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 b. 2. Disconnect bus at TURK (507457) to trip transformer at TURK 1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508072_NWTXARK7-508071_NWTXARK4_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX2-1 (508101) to trip transformer at NWTEX2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508072_NWTXARK7-508359_WELSH_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508072_NWTXARK7-510911_VALIANT7_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508359_WELSH-508832_DIANA_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508359_WELSH-508832_DIANA_Ckt2 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508359_WELSH-508841_WILKES_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508359_WELSH-5917_SPPMAINBUS_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510911_VALIANT7-510907_PITTSB-7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508071_NWTXARK4-508070_NWT-BNT4_Ckt1 | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508071_NWTXARK4-508072_NWTXARK7_3Winding | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX1-1 (508100) to trip transformer at NWTEX1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508298_LYDIA | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508072_NWTXARK7 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to TURK (507455) 345.0 kV bus CKT 1 b. 2. Disconnect TURK (507457) 13.8 kV bus to trip transformer at TURK 1 13.8 kV bus b. 3. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508359_WELSH | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508071_NWTXARK4 | Single Phase Fault with Stuck Breaker on NWTXARK4 (508071) 138.0 kV bus a. Apply single-phase fault on NWTXARK4 (508071) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 b. 2. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508832_DIANA | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508809_LONGWD-508808_LONGWD_3Winding | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508809_LONGWD-508841_WILKES_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508809_LONGWD-507760_SW_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508809_LONGWD-337376_7SAREPTA%_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337376_7SAREPTA%-337561_8EL_3Winding | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 b. 2. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337376_7SAREPTA%-337363_3SAREPTA!_Ckt1 | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507760_SW-507759_SW_3Winding | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507760_SW-500250_DOLHILL7_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507760_SW-508832_DIANA_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508841_WILKES-508840_WILKES_3Winding | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt2 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508841_WILKES-508359_WELSH_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508808_LONGWD-508809_LONGWD_3Winding | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508808_LONGWD-508806_LIEBERM4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508808_LONGWD-507711_ARSHILL4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 b. 2. Drop load from bus NORAM (507774) 138.0 kV bus b. 3. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 b. 4. Drop load from bus RAINES (507749) 138.0 kV bus b. 5. Drop switching device from bus RAINES (507749) 138.0 kV bus b. 6. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 c. 2. Reclose branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 c. 3. Reclose branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 d. 2. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 d. 3. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508808_LONGWD-507727_FLOURNY4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508808_LONGWD-508566_SABMINT4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 2. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 4. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 5. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 2. Reclose branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 3. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 2. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337368_8MT_OLIVE%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337420_8STERLING%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt2 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337643_8SHERIDAN%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337376_7SAREPTA%_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus b. 2. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337539_3EL_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337561_8EL-337515_8MCNEIL%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337363_3SAREPTA!-337376_7SAREPTA%_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337363_3SAREPTA!-337361_3MINDEN_LA!_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_500250_DOLHILL7-500260_DOLHILL6_Ckt1 | 3 Phase fault on DOLHILL7 (500250) 345.0 kV a. Apply fault on DOLHILL7 (500250) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508832_DIANA-508359_WELSH_Ckt1 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508832_DIANA-508359_WELSH_Ckt2 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507759_SW-507760_SW_3Winding | 3 Phase fault on SW (507759) 138.0 kV a. Apply fault on SW (507759) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508840_WILKES-508841_WILKES_3Winding | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508840_WILKES-508297_LSSOUTH4_Ckt1 | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508806_LIEBERM4-588404_G16-167-TAP_Ckt1 | 3 Phase fault on LIEBERM4 (508806) 138.0 kV a. Apply fault on LIEBERM4 (508806) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507727_FLOURNY4-507726_FLOURNY2_3Winding | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLOURNY1 (507740) to trip transformer at FLOURNY1 12.470 (507740) 12.470000267028809 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507727_FLOURNY4-508808_LONGWD_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507727_FLOURNY4-507732_GENMOTR4_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENMOTR4 (507732) 138.0 kV bus b. 2. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337368_8MT_OLIVE%-509366_LAYFLD8_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337368_8MT_OLIVE%-337369_6MT_OLIVE%_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_337539_3EL-337561_8EL_3Winding | 3 Phase fault on 3EL (337539) 115.0 kV a. Apply fault on 3EL (337539) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507711_ARSHILL4-507789_STLGENS4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_507711_ARSHILL4-507731_FTHUMBG4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508566_SABMINT4-508562_PIRKEY_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508566_SABMINT4-508808_LONGWD_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 2. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 4. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 5. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 2. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 3. Reclose branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 2. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508566_SABMINT4-508577_SABINEM4_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 2. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 3. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508562_PIRKEY-508595_HALLSVLS4_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508562_PIRKEY-509092_EASTON_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus EASTON (509092) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508809_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-337376_7SAREPTA% | Single Phase Fault with Stuck Breaker on 7SAREPTA% (337376) 345.0 kV bus a. Apply single-phase fault on 7SAREPTA% (337376) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to 7EL (337562) 345.0 kV bus CKT 1 b. 2. Disconnect 1EL (337565) 13.8 kV bus to trip transformer at 1EL DORADO2 13.8 kV bus b. 3. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-507760_SW | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508841_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508808_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508808) 138.0 kV bus a. Apply single-phase fault on LONGWD (508808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-337561_8EL | Single Phase Fault with Stuck Breaker on 8EL (337561) 500.0 kV bus a. Apply single-phase fault on 8EL (337561) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 b. 2. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-337363_3SAREPTA! | Single Phase Fault with Stuck Breaker on 3SAREPTA! (337363) 115.0 kV bus a. Apply single-phase fault on 3SAREPTA! (337363) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-507759_SW | Single Phase Fault with Stuck Breaker on SW (507759) 138.0 kV bus a. Apply single-phase fault on SW (507759) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508840_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508840) 138.0 kV bus a. Apply single-phase fault on WILKES (508840) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus b. 2. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508806_LIEBERM4 | Single Phase Fault with Stuck Breaker on LIEBERM4 (508806) 138.0 kV bus a. Apply single-phase fault on LIEBERM4 (508806) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to LONGWD (508808) 138.0 kV bus CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-338440_8PANDA% | Single Phase Fault with Stuck Breaker on 8PANDA% (338440) 500.0 kV bus a. Apply single-phase fault on 8PANDA% (338440) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 1 b. 2. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-337539_3EL | Single Phase Fault with Stuck Breaker on 3EL (337539) 115.0 kV bus a. Apply single-phase fault on 3EL (337539) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1EL (337564) 13.8 kV bus to trip transformer at 1EL DORADO1 13.8 kV bus b. 2. Disconnect 1EL (337566) 13.8 kV bus to trip transformer at 1EL DORADO3 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-507711_ARSHILL4 | Single Phase Fault with Stuck Breaker on ARSHILL4 (507711) 138.0 kV bus a. Apply single-phase fault on ARSHILL4 (507711) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 b. 2. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508562_PIRKEY | Single Phase Fault with Stuck Breaker on PIRKEY (508562) 138.0 kV bus a. Apply single-phase fault on PIRKEY (508562) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 kV bus to HALLSVLS4 (508595) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from PIRKEY (508562) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511468_LES-7-511456_OKU-7_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511468_LES-7-760938_G17-171-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511468_LES-7-511467_LES-4_3Winding | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511468_LES-7-587744_G16-091-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511456_OKU-7-762467_G18-015-TAP_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511456_OKU-7-511565_OKLAUN_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus OKLAUN (511565) 345.0 kV bus b. 2. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_587744_G16-091-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-091-TAP (587744) 345.0 kV a. Apply fault on G16-091-TAP (587744) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_760938_G17-171-TAP-511568_TERRYRD7_Ckt1 | 3 Phase fault on G17-171-TAP (760938) 345.0 kV a. Apply fault on G17-171-TAP (760938) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511468_LES-7_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511537_ARTVLTP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 b. 2. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 3. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 c. 2. Reclose branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 d. 2. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511439_LWSTAP_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511494_COMMTAP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511437_COMANC-4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511466_LES-2_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#1-1 (511416) to trip transformer at LES#1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511423_FLE_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511467_LES-4-511486_ELGINJT4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515800_GRACMNT7-514801_MINCO_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515800_GRACMNT7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515800_GRACMNT7-515802_GRACMNT4_3Winding | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRCMNT11 (515801) to trip transformer at GRCMNT11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_762467_G18-015-TAP-762216_G17-151TAP_Ckt1 | 3 Phase fault on G18-015-TAP (762467) 345.0 kV a. Apply fault on G18-015-TAP (762467) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511568_TERRYRD7-515136_SUNNYSD7_Ckt1 | 3 Phase fault on TERRYRD7 (511568) 345.0 kV a. Apply fault on TERRYRD7 (511568) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511439_LWSTAP-511488_112GORE4_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 b. 2. Drop load from bus RPPAPER4 (511512) 138.0 kV bus b. 3. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 c. 2. Reclose branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 d. 2. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511439_LWSTAP-511431_LWS_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus LWS (511431) 138.0 kV bus b. 2. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511466_LES-2-511503_LAW_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511466_LES-2-511487_ELGINJT2_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 3. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 b. 4. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 5. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 6. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 b. 7. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 8. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 c. 3. Reclose branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 c. 4. Reclose branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 d. 3. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 d. 4. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514801_MINCO-516096_NORMHLL7_Ckt1 | 3 Phase fault on MINCO (514801) 345.0 kV a. Apply fault on MINCO (514801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560078_G16-037-TAP-511553_CHISHOLM7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt1 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt2 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-511468_LES-7 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-511456_OKU-7 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-511467_LES-4 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LES#5-1 (511411) 13.8 kV bus to trip transformer at LES#5-1 13.8 kV bus b. 2. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to SHERID4 (511474) 138.0 kV bus CKT 1 b. 3. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 4. Trip branch from SHERID4 (511474) 138.0 kV bus to ARTVLTP4 (511537) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515800_GRACMNT7 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a. Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-511466_LES-2 | Single Phase Fault with Stuck Breaker on L.E.S.-2 (511466) 69.0 kV bus a. Apply single-phase fault on L.E.S.-2 (511466) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-S2 (511470) 69.0 kV bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 kV bus to LAW (511503) 69.0 kV bus CKT 1 b. 5. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-N2 (511469) 69.0 kV bus CKT 1 b. 6. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 7. Trip branch from LGORE-N2 (511469) 69.0 kV bus to FT.SILL2 (511461) 69.0 kV bus CKT 1 b. 8. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 9. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 10. Trip branch from FT.SILL2 (511461) 69.0 kV bus to PO.HILL2 (511473) 69.0 kV bus CKT 1 b. 11. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 12. Trip branch from PO.HILL2 (511473) 69.0 kV bus to ELGINJT2 (511487) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514801_MINCO | Single Phase Fault with Stuck Breaker on MINCO (514801) 345.0 kV bus a. Apply single-phase fault on MINCO (514801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515802_GRACMNT4 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-300069_5CHOTEAU1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512656_GRDA1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-301344_5CDRCRST_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512629_DRYGULCH5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512626_MAID_3Winding | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512635_KERR_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512635_KERR_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512648_MAID-512656_GRDA1_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-512648_MAID_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. 2. Reclose branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 c. 3. Reclose branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 c. 4. Reclose branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. 2. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 d. 3. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 d. 4. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-513570_CHOUTEAUCRK516100_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-512671_HUNT_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 2. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 3. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512656_GRDA1-512700_WAGNOR_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512650_GRDA1-512750_TONECE7_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300069_5CHOTEAU1-301348_5CHOTEAU2_CktZ1 | 3 Phase fault on 5CHOTEAU1 (300069) 161.0 kV a. Apply fault on 5CHOTEAU1 (300069) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512629_DRYGULCH5-512654_PENSA_Ckt1 | 3 Phase fault on DRYGULCH5 (512629) 161.0 kV a. Apply fault on DRYGULCH5 (512629) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512714_KANSATP5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt2 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512654_PENSA_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512771_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512635_KERR-512770_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512638_CATSAGR5-512627_COLINS_Ckt1 | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 c. 2. Reclose branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 d. 2. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512638_CATSAGR5-509790_CATOOSA4_3Winding | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CATTER1 (512833) to trip transformer at CATTER1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512626_MAID-512671_HUNT_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 c. 2. Reclose branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 c. 3. Reclose branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 c. 4. Reclose branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 c. 5. Reclose branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 d. 2. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 d. 3. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 d. 4. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 d. 5. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512626_MAID-512648_MAID_3Winding | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512626_MAID-512683_AMERCAST_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 b. 2. Drop load from bus REDDEN (512698) 69.0 kV bus b. 3. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 b. 4. Drop load from bus AMERCAST (512683) 69.0 kV bus b. 5. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 c. 2. Reclose branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 c. 3. Reclose branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 d. 2. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 d. 3. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512700_WAGNOR-512697_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512700_WAGNOR-512640_OKAYGR_Ckt1 | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513570_CHOUTEAUCRK516100-512651_CLARMR_Ckt1 | 3 Phase fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV a. Apply fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301344_5CDRCRST-512648_MAID_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301344_5CDRCRST-301345_2CDRCRST_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301344_5CDRCRST-512655_TAHLQH_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300739_7BLACKBERRY-300949_7JASPER_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300739_7BLACKBERRY-532797_WOLFCRK7_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300739_7BLACKBERRY-532793_NEOSHO_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300741_5SPORTSMAN-301348_5CHOTEAU2_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt2 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509852_TNO--7-510406_NES-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509852_TNO--7-512694_CLEVLND7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509852_TNO--7-509755_WEKIWA-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512654_PENSA-512669_KETCHUM5_Ckt1 | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512654_PENSA-512628_PENSA_3Winding | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PENSA (512841) to trip transformer at PENSA 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509790_CATOOSA4-509752_INOLATP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509790_CATOOSA4-509835_TERNITP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512640_OKAYGR-505560_FT_Ckt1 | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512640_OKAYGR-512646_OKAYGR_3Winding | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OKAY1 (512848) to trip transformer at OKAY1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512697_WAGNOR-512700_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512697_WAGNOR-512801_WAGCTY12_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 b. 2. Drop load from bus WAGCTY22 (512759) 69.0 kV bus b. 3. Drop load from bus WAGCTY12 (512801) 69.0 kV bus b. 4. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 c. 2. Reclose branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 d. 2. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512697_WAGNOR-300958_2HIGHLND_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 b. 2. Drop load from bus 2WAGNERW (300972) 69.0 kV bus b. 3. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 b. 4. Drop load from bus 2COWETA (300955) 69.0 kV bus b. 5. Drop load from bus 2HIGHLND (300958) 69.0 kV bus b. 6. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 c. 2. Reclose branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 c. 3. Reclose branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 d. 2. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 d. 3. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512697_WAGNOR-512690_WAGNRTP2_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512651_CLARMR-510396_NES-4_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR4 (512813) to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 c. 2. Reclose branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 d. 2. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512651_CLARMR-512679_CLARMR_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR2 (512815) to trip transformer at CLARMR2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301345_2CDRCRST-301344_5CDRCRST_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301345_2CDRCRST-513059_HULBERKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 b. 2. Drop load from bus 2PEGGS (300962) 69.0 kV bus b. 3. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 b. 4. Drop load from bus 2HULBERT (300975) 69.0 kV bus b. 5. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 c. 2. Reclose branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 c. 3. Reclose branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 d. 2. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 d. 3. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_301345_2CDRCRST-513062_TAHLWESTKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 b. 2. Drop load from bus 2LOWERY (300960) 69.0 kV bus b. 3. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 b. 4. Drop load from bus 2SLEEPYH (300968) 69.0 kV bus b. 5. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 c. 2. Reclose branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 c. 3. Reclose branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 d. 2. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 d. 3. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512655_TAHLQH-515956_7CLANS_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512655_TAHLQH-513044_BRIGSKM_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300949_7JASPER-300045_7MORGAN_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_300949_7JASPER-300794_5LAMAR_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 b. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 c. 2. Reclose branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 d. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532797_WOLFCRK7-532794_ROSEHIL7_Ckt1 | 3 Phase fault on WOLFCRK7 (532797) 345.0 kV a. Apply fault on WOLFCRK7 (532797) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509755_WEKIWA-7-514803_SOONER_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_510406_NES-7-510380_DELWARE7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512694_CLEVLND7-560056_G15-066T_Ckt1 | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512694_CLEVLND7-300138_4CLEVLND_3Winding | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CLEVLND1 (512817) to trip transformer at CLEVLND1 13.8 kV bus b. 2. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509895_TNO2-4-509817_TNO--4_Ckt1 | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509895_TNO2-4-509852_TNO--7_3Winding | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt1 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513591_HERRON-513596_IGLOOV_3Winding | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 b. 2. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt2 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512671_HUNT-512656_GRDA1_3Winding | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 b. 3. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 4. Drop load from bus HUNT (512671) 69.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_512671_HUNT-512810_PRYORC12_Ckt1 | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 b. 2. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 3. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 b. 4. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 5. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 c. 2. Reclose branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 c. 3. Reclose branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 d. 2. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 d. 3. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_506934_FLINTCR5-504201_GENTRY_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509817_TNO--4-509842_CDC-WT_Ckt1 | 3 Phase fault on T.NO.--4 (509817) 138.0 kV a. Apply fault on T.NO.--4 (509817) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512648_MAID | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a. Apply single-phase fault on MAID (512648) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 b. 2. Trip branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 3. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 4. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 5. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 6. Trip branch from NWMAID5 (512757) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 7. Drop load from bus WMAIN (512742) 161.0 kV bus b. 8. Trip branch from WMAIN (512742) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-300740_7SPORTSMAN | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345.0 kV bus a. Apply single-phase fault on 7SPORTSMAN (300740) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 5SPORTSMAN (300741) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-513596_IGLOOV | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a. Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Disconnect IGLOTER1 (513592) 13.2 kV bus to trip transformer at IGLOTER1 1 13.200 (513592) 13.2 kV bus b. 3. Trip branch from IGLOOV1 (513593) 161.0 kV bus to HERRON (513591) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512635_KERR | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 b. 4. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512638_CATSAGR5 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 kV bus to 5ELMCRK (300993) 161.0 kV bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 kV bus to COLINS (512627) 161.0 kV bus CKT 1 b. 5. Trip branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512626_MAID | Single Phase Fault with Stuck Breaker on MAID (512626) 69.0 kV bus a. Apply single-phase fault on MAID (512626) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 kV bus to AMERCAST (512681) 69.0 kV bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 kV bus to CPPTAP (512661) 69.0 kV bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 kV bus to PRYORCHEM2 (512699) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 kV bus to AIRPROD2 (512687) 69.0 kV bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 kV bus to HUNT (512671) 69.0 kV bus CKT 1 b. 9. Disconnect MAITER1 (512836) 13.2 kV bus to trip transformer at MAITER1 1 13.200 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512700_WAGNOR | Single Phase Fault with Stuck Breaker on WAGNOR (512700) 161.0 kV bus a. Apply single-phase fault on WAGNOR (512700) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR1 (512818) 13.8 kV bus to trip transformer at WAGNOR1 13.8 kV bus b. 2. Trip branch from WAGNOR (512700) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-301344_5CDRCRST | Single Phase Fault with Stuck Breaker on 5CDRCRST (301344) 161.0 kV bus a. Apply single-phase fault on 5CDRCRST (301344) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to LOCSTGVKM (513050) 161.0 kV bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 4. Trip branch from 5CDRCRST (301344) 161.0 kV bus to 2CDRCRST (301345) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-300739_7BLACKBERRY | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345.0 kV bus a. Apply single-phase fault on 7BLACKBERRY (300739) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-300741_5SPORTSMAN | Single Phase Fault with Stuck Breaker on 5SPORTSMAN (300741) 161.0 kV bus a. Apply single-phase fault on 5SPORTSMAN (300741) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 b. 2. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 7SPORTSMAN (300740) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512654_PENSA | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a. Apply single-phase fault on PENSA (512654) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 3. Disconnect PENSA (512841) 13.8 kV bus to trip transformer at PENSA 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509790_CATOOSA4 | Single Phase Fault with Stuck Breaker on CATOOSA4 (509790) 138.0 kV bus a. Apply single-phase fault on CATOOSA4 (509790) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 b. 2. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512651_CLARMR | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CLARMR4 (512813) 13.8 kV bus to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 kV bus to OOLOGAHKM (513124) 138.0 kV bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 kV bus to N.E.S.-4 (510396) 138.0 kV bus CKT 1 b. 5. Disconnect CLARMR2 (512815) 13.8 kV bus to trip transformer at CLARMR2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512655_TAHLQH | Single Phase Fault with Stuck Breaker on TAHLQH (512655) 161.0 kV bus a. Apply single-phase fault on TAHLQH (512655) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 kV bus to 7CLANS (515956) 161.0 kV bus CKT 1 b. 3. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-532797_WOLFCRK7 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a. Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 b. 2. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-512671_HUNT | Single Phase Fault with Stuck Breaker on HUNT (512671) 69.0 kV bus a. Apply single-phase fault on HUNT (512671) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 kV bus to MAIDTP2 (512625) 69.0 kV bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 kV bus to GRDA1 (512727) 69.0 kV bus CKT 1 b. 3. Disconnect GRDA1 (512816) 13.8 kV bus to trip transformer at GRDA1 1 13.8 kV bus b. 4. Trip branch from HUNT (512671) 69.0 kV bus to PRY0RC22 (512639) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 6. Trip branch from PRY0RC22 (512639) 69.0 kV bus to PRYORC32 (512622) 69.0 kV bus CKT 1 b. 7. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 8. Trip branch from PRYORC32 (512622) 69.0 kV bus to PRYORC12 (512810) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509817_TNO--4 | Single Phase Fault with Stuck Breaker on T.NO.--4 (509817) 138.0 kV bus a. Apply single-phase fault on T.NO.--4 (509817) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-755000_WWDBORDT_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515375_WWRDEHV7-515376_WWRDEHV4_3Winding | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV31 (515795) to trip transformer at WWDEHV31 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt2 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt1 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515852_DGRASSE7-515853_DGRASSE4_3Winding | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt2 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt1 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_755000_WWDBORDT-525832_TUCO_INT_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_755000_WWDBORDT-511553_CHISHOLM7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515376_WWRDEHV4-515533_REDCLFT4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 c. 2. Reclose branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 d. 2. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515376_WWRDEHV4-515375_WWRDEHV7_3Winding | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV21 (515799) to trip transformer at WWDEHV21 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515376_WWRDEHV4-514785_WOODWRD4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 b. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 c. 2. Reclose branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 d. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511553_CHISHOLM7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511553_CHISHOLM7-511557_CHISHOLM6_3Winding | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515853_DGRASSE4-520436_ROSEVLY4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515853_DGRASSE4-514795_KNOBHIL4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515853_DGRASSE4-515852_DGRASSE7_3Winding | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515853_DGRASSE4-520999_MOORLND4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_560078_G16-037-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511557_CHISHOLM6-511541_SWEETWT6_Ckt1 | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511557_CHISHOLM6-511458_ELKCTY-4_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 b. 2. Disconnect bus at ELKC2-1 (511482) to trip transformer at ELKC2-1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511557_CHISHOLM6-511553_CHISHOLM7_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515375_WWRDEHV7 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345.0 kV bus a. Apply single-phase fault on WWRDEHV7 (515375) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515407_TATONGA7 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345.0 kV bus a. Apply single-phase fault on TATONGA7 (515407) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515852_DGRASSE7 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345.0 kV bus a. Apply single-phase fault on DGRASSE7 (515852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-560071_G16-003-TAP | Single Phase Fault with Stuck Breaker on G16-003-TAP (560071) 345.0 kV bus a. Apply single-phase fault on G16-003-TAP (560071) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 b. 2. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-755000_WWDBORDT | Single Phase Fault with Stuck Breaker on WWDBORDT (755000) 345.0 kV bus a. Apply single-phase fault on WWDBORDT (755000) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515376_WWRDEHV4 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138.0 kV bus a. Apply single-phase fault on WWRDEHV4 (515376) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 kV bus to IODINE-4 (514796) 138.0 kV bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 kV bus to REDCLFT4 (515533) 138.0 kV bus CKT 1 b. 4. Disconnect WWDEHV31 (515795) 13.8 kV bus to trip transformer at WWDEHV31 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-511553_CHISHOLM7 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345.0 kV bus a. Apply single-phase fault on CHISHOLM7 (511553) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 b. 2. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515497_MATHWSN7 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345.0 kV bus a. Apply single-phase fault on MATHWSN7 (515497) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-539801_THISTLE7 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345.0 kV bus a. Apply single-phase fault on THISTLE7 (539801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515677_BADGER | Single Phase Fault with Stuck Breaker on BADGER (515677) 345.0 kV bus a. Apply single-phase fault on BADGER (515677) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511541_SWEETWT6-511557_CHISHOLM6_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2019-013 (763541) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511541_SWEETWT6-523777_WHEELER_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523777_WHEELER-523771_GRAPEVINE_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523777_WHEELER-511541_SWEETWT6_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523777_WHEELER-523776_WHEELER_3Winding | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WHEELER_TR1113.200 (523774) to trip transformer at WHEELER_TR1113.200 (523774) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_511553_CHISHOLM7-755000_WWDBORDT_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_755000_WWDBORDT-515375_WWRDEHV7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514795_KNOBHIL4-514794_KNOBHIL2_3Winding | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt2 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt1 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520436_ROSEVLY4-520430_NOELSW_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520436_ROSEVLY4-520601_AVARD_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AVARD (520601) 138.0 kV bus b. 2. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-520848_CDRDLTP4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 c. 2. Reclose branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 d. 2. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-514778_CLEOCOR4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 b. 2. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 3. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 4. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 c. 2. Reclose branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 d. 2. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-515785_WINDFRM4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-520553_SEILING4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SEILING4 (520553) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-520462_ASPEN_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus ASPEN (520462) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-521197_CRTSJCT2_3Winding | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MLNDTERT (521180) to trip transformer at MLNDTERT 2.4000 (521180) 2.4000000953674316 kV bus b. 2. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520999_MOORLND4-520957_IODINE_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus IODINE (520957) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_539801_THISTLE7-539638_FLATRDG4_3Winding | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at THISTLE (539802) to trip transformer at THISTLE T1 13.8 kV bus b. 2. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_520430_NOELSW-521200_DRIFTWD4_Ckt1 | 3 Phase fault on NOELSW (520430) 138.0 kV a. Apply fault on NOELSW (520430) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 2. Reclose branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 3. Reclose branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 2. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514794_KNOBHIL2-514795_KNOBHIL4_3Winding | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514794_KNOBHIL2-514792_ALVAOGE2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_514794_KNOBHIL2-515371_HELENAT2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 b. 2. Drop load from bus CZYCRVT2 (515560) 69.0 kV bus b. 3. Drop fixed shunt from bus CZYCRVT2 (515560) 69.0 kV bus b. 4. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 b. 5. Drop load from bus SALINE (514716) 69.0 kV bus b. 6. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 c. 2. Reclose branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 c. 3. Reclose branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 d. 2. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 d. 3. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt1 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt2 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_521200_DRIFTWD4-520430_NOELSW_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 2. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 4. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 5. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 6. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 2. Reclose branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 3. Reclose branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 2. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 3. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_521200_DRIFTWD4-520432_BYRONTP4_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_521200_DRIFTWD4-521201_DRIFTWD2_3Winding | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DRFTWDTERT (521185) to trip transformer at DRFTWDTERT 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-515853_DGRASSE4 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138.0 kV bus a. Apply single-phase fault on DGRASSE4 (515853) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-514795_KNOBHIL4 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138.0 kV bus a. Apply single-phase fault on KNOBHIL4 (514795) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Disconnect KNOBHIL1 (515732) 13.2 kV bus to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-520436_ROSEVLY4 | Single Phase Fault with Stuck Breaker on ROSEVLY4 (520436) 138.0 kV bus a. Apply single-phase fault on ROSEVLY4 (520436) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-520999_MOORLND4 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138.0 kV bus a. Apply single-phase fault on MOORLND4 (520999) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 kV bus to CDRDLTP4 (520848) 138.0 kV bus CKT 1 b. 4. Trip branch from MOORLND4 (520999) 138.0 kV bus to GLASMTN4 (514788) 138.0 kV bus CKT 1 b. 5. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 6. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 7. Trip branch from GLASMTN4 (514788) 138.0 kV bus to CLEOCOR4 (514778) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-520430_NOELSW | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a. Apply single-phase fault on NOELSW (520430) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 kV bus to DRIFTWD4 (521200) 138.0 kV bus CKT 1 b. 7. Trip branch from NOELSW (520430) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-532782_BUFFALO7 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345.0 kV bus a. Apply single-phase fault on BUFFALO7 (532782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_763010_G19-065-TAP-509076_NWHENDR4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 2. Drop load from bus LONDON (509072) 138.0 kV bus b. 3. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 6. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 7. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 2. Reclose branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 4. Reclose branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 2. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 4. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_763010_G19-065-TAP-509080_OVERTON4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509080_OVERTON4-508548_KNOXLEE4_Ckt1 | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 2. Reclose branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 4. Reclose branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 2. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 4. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509080_OVERTON4-509079_OVERTON2_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509080_OVERTON4-509241_CROCKET7_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 3. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 4. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 5. Drop load from bus ALTO (509320) 138.0 kV bus b. 6. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 7. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 8. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 9. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 10. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 11. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 b. 12. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 13. Drop switching device from bus OVERTON4 (509080) 138.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 2. Reclose branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 3. Reclose branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 5. Reclose branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 6. Reclose branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 3. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 5. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 6. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509241_CROCKET7-508585_TENRUSK7_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509241_CROCKET7-334028_7GRIMES%_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509241_CROCKET7-509080_OVERTON4_3Winding | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 2. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 3. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 4. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 5. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 6. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 7. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 8. Drop load from bus ALTO (509320) 138.0 kV bus b. 9. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 10. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 11. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 12. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 2. Reclose branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 3. Reclose branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 5. Reclose branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 6. Reclose branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 2. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 3. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 5. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 6. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509079_OVERTON2-508546_KILGORE2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509079_OVERTON2-509080_OVERTON4_3Winding | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509079_OVERTON2-509089_TURNERT2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus TURNERT2 (509089) 69.0 kV bus b. 2. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509076_NWHENDR4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 c. 2. Reclose branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 d. 2. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509080_OVERTON4 | Single Phase Fault with Stuck Breaker on OVERTON4 (509080) 138.0 kV bus a. Apply single-phase fault on OVERTON4 (509080) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 kV bus to LEVERET4 (509069) 138.0 kV bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 kV bus to KILGORR4 (509067) 138.0 kV bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 kV bus to MONROER4 (509073) 138.0 kV bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 kV bus to KNOXLEE4 (508548) 138.0 kV bus CKT 1 b. 8. Trip branch from OVERTON4 (509080) 138.0 kV bus to G19-065-TAP (763010) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509076_NWHENDR4-509075_NWHENDR2_3Winding | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509076_NWHENDR4-763010_G19-065-TAP_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 2. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 3. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 6. Drop load from bus LONDON (509072) 138.0 kV bus b. 7. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 2. Reclose branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 4. Reclose branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 2. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 4. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-508562_PIRKEY_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 c. 2. Reclose branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. 3. Reclose branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 d. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. 3. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-509059_CHEROKE4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CHEROKE4 (509059) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-509080_OVERTON4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 2. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 3. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 6. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 7. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 2. Reclose branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 4. Reclose branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 2. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 4. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-508544_HARRISN4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-508570_SOTXEST4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SOTXEST4 (508570) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508548_KNOXLEE4-508568_SELONGV2_3Winding | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KXLEE-1 (508584) to trip transformer at KXLEE-1 12.470 (508584) 12.470000267028809 kV bus b. 2. Drop load from bus KNOXLEE2 (508547) 69.0 kV bus b. 3. Drop switching device from bus KNOXLEE2 (508547) 69.0 kV bus b. 4. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_334028_7GRIMES%-334026_4GRIMES%_3Winding | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_334028_7GRIMES%-334027_6GRIMES!_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_334028_7GRIMES%-334197_7ROCKYCRK%_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508585_TENRUSK7-508572_LEBROCK7_Ckt1 | 3 Phase fault on TENRUSK7 (508585) 345.0 kV a. Apply fault on TENRUSK7 (508585) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508546_KILGORE2-508573_SPIPETP2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 b. 2. Drop load from bus HOWELL (508545) 69.0 kV bus b. 3. Drop switching device from bus HOWELL (508545) 69.0 kV bus b. 4. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 b. 5. Drop load from bus SABINE (508565) 69.0 kV bus b. 6. Drop switching device from bus SABINE (508565) 69.0 kV bus b. 7. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 c. 2. Reclose branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 c. 3. Reclose branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 d. 2. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 d. 3. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508546_KILGORE2-508574_WHITNEY2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 b. 2. Drop load from bus MONROCR2 (508558) 69.0 kV bus b. 3. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 c. 2. Reclose branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 d. 2. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509075_NWHENDR2-509081_POYNTER2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509075_NWHENDR2-509076_NWHENDR4_3Winding | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_509075_NWHENDR2-509061_EVENSID2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_334026_4GRIMES%-334028_7GRIMES%_3Winding | 3 Phase fault on 4GRIMES% (334026) 138.0 kV a. Apply fault on 4GRIMES% (334026) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt2 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt1 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509241_CROCKET7 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509079_OVERTON2 | Single Phase Fault with Stuck Breaker on OVERTON2 (509079) 69.0 kV bus a. Apply single-phase fault on OVERTON2 (509079) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 b. 2. Disconnect OVTON2-1 (509098) 13.2 kV bus to trip transformer at OVTON2-1 13.200 (509098) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-509076_NWHENDR4 | Single Phase Fault with Stuck Breaker on NWHENDR4 (509076) 138.0 kV bus a. Apply single-phase fault on NWHENDR4 (509076) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 kV bus to OAK1HIL4 (509077) 138.0 kV bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 kV bus to OAK2HIL4 (509078) 138.0 kV bus CKT 1 b. 5. Disconnect NWHEN1-1 (509095) 13.2 kV bus to trip transformer at NWHEN1-1 13.200 (509095) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508548_KNOXLEE4 | Single Phase Fault with Stuck Breaker on KNOXLEE4 (508548) 138.0 kV bus a. Apply single-phase fault on KNOXLEE4 (508548) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to BRANDYBR (508596) 138.0 kV bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 b. 5. Drop load from bus KNOXL5-1 (509398) 22.0 kV bus b. 6. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to KNOXL5-1 (509398) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-334028_7GRIMES% | Single Phase Fault with Stuck Breaker on 7GRIMES% (334028) 345.0 kV bus a. Apply single-phase fault on 7GRIMES% (334028) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508585_TENRUSK7 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip branch from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-508586_TENGEN | Single Phase Fault with Stuck Breaker on TENGEN (508586) 345.0 kV bus a. Apply single-phase fault on TENGEN (508586) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506745) 18.0 kV bus CKT 1 b. 2. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506746) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-334026_4GRIMES% | Single Phase Fault with Stuck Breaker on 4GRIMES% (334026) 138.0 kV bus a. Apply single-phase fault on 4GRIMES% (334026) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus b. 2. Disconnect 1GRIMES_2 (334018) 13.8 kV bus to trip transformer at 1GRIMES_2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-300997_5KETONVL-ConID-109484 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-300997_5KETONVL-ConID-109485 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-500250_DOLHILL7-ConID-80023 | Single Phase Fault with Stuck Breaker on DOLHILL7 (500250) 345.0 kV bus a. Apply single-phase fault on DOLHILL7 (500250) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DOLHILL7 (500250) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84210 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84211 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84212 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84213 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84214 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84207 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84208 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84209 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-506979_SHIPERD7-ConID-84215 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345.0 kV bus a. Apply single-phase fault on SHIPERD7 (506979) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from SHIPERD7 (506979) 345.0 kV bus to SHIPERD5 (506980) 161.0 kV bus to SHIPERD1 (506981) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507455_TURK-ConID-84200 | Single Phase Fault with Stuck Breaker on TURK (507455) 345.0 kV bus a. Apply single-phase fault on TURK (507455) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from TURK (507454) 138.0 kV bus to TURK (507455) 345.0 kV bus to TURK (507457) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507760_SW-ConID-84164 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507760_SW-ConID-84165 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507760_SW-ConID-84166 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507760_SW-ConID-84167 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-507760_SW-ConID-84168 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84194 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84197 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84198 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84199 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84187 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84189 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84195 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84196 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84206 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 4. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508298_LYDIA-ConID-91933 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508359_WELSH-ConID-84181 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508359_WELSH-ConID-84184 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508359_WELSH-ConID-84190 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84154 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84155 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84156 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84157 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84159 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84160 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84161 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84162 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84163 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508572_LEBROCK7-ConID-84153 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508572_LEBROCK7-ConID-84158 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84150 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 b. 3. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84151 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84152 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84169 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84170 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84171 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84172 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84173 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84174 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84175 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84176 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84177 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84178 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508832_DIANA-ConID-84179 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508841_WILKES-ConID-84180 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-508841_WILKES-ConID-84182 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509241_CROCKET7-ConID-84148 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509241_CROCKET7-ConID-84149 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84185 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84186 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84191 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509406_WELSH3-1-ConID-84188 | Single Phase Fault with Stuck Breaker on WELSH3-1 (509406) 18.0 kV bus a. Apply single-phase fault on WELSH3-1 (509406) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509409_WILKE3-1-ConID-84183 | Single Phase Fault with Stuck Breaker on WILKE3-1 (509409) 22.0 kV bus a. Apply single-phase fault on WILKE3-1 (509409) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84239 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84240 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84241 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509782_RSS-7-ConID-84233 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip transformer from RSS (509773) 138.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus to RSST1 (509882) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509782_RSS-7-ConID-84234 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to COGENT (509834) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84248 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84249 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84256 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84257 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84258 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84259 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84260 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84262 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84263 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 b. 2. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84265 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84266 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84242 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84243 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84244 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip line from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509870_SAPLPRD7-ConID-84236 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from SAPLPRD7 (509870) 345.0 kV bus to SAPLPRD4 (509871) 138.0 kV bus to SAPLPRD1 (509872) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509870_SAPLPRD7-ConID-84237 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509874_ONETA5-1-ConID-84264 | Single Phase Fault with Stuck Breaker on ONETA5-1 (509874) 34.5 kV bus a. Apply single-phase fault on ONETA5-1 (509874) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-509881_ONETA1-1-ConID-84261 | Single Phase Fault with Stuck Breaker on ONETA1-1 (509881) 13.8 kV bus a. Apply single-phase fault on ONETA1-1 (509881) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510370_DELAWAR1-ConID-8425301 | Single Phase Fault with Stuck Breaker on DELAWAR1 (510370) 13.8 kV bus a. Apply single-phase fault on DELAWAR1 (510370) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84253 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-842530 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84254 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-842540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84255 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510406_NES-7-ConID-84250 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510406_NES-7-ConID-84251 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510406_NES-7-ConID-84252 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84223 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84224 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84225 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84226 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84227 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84201 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84202 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84203 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-91932 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511411_LES#5-1-ConID-8422101 | Single Phase Fault with Stuck Breaker on LES#5-1 (511411) 13.8 kV bus a. Apply single-phase fault on LES#5-1 (511411) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511456_OKU-7-ConID-84217 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511467_LES-4-ConID-9193401 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-84218 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-842180 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-84221 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-842210 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-84222 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-842720 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-842730 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-91934 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-919340 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-91937 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-919370 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511468_LES-7-ConID-9193701 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84272 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-8427201 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84273 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-8427301 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84274 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-511840_NES3-1-ConID-84247 | Single Phase Fault with Stuck Breaker on NES3-1 (511840) 22.0 kV bus a. Apply single-phase fault on NES3-1 (511840) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512635_KERR-ConID-109452 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512635_KERR-ConID-109453 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512635_KERR-ConID-109454 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512771) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512638_CATSAGR5-ConID-109479 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Trip transformer from CATOOSA4 (509790) 138.0 kV bus to CATSAGR5 (512638) 161.0 kV bus to CATTER2 (512834) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512651_CLARMR-ConID-109481 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512651_CLARMR-ConID-109482 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109486 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR (512700) 161.0 kV bus b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109487 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA2 (512826) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109488 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512686_SALINA-ConID-109461 | Single Phase Fault with Stuck Breaker on SALINA (512686) 161.0 kV bus a. Apply single-phase fault on SALINA (512686) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SALINA (512686) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512707_CLARMR-ConID-109480 | Single Phase Fault with Stuck Breaker on CLARMR (512707) 138.0 kV bus a. Apply single-phase fault on CLARMR (512707) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR2 (512815) 13.8 kV bus CKT 2 b. 2. Disconnect CLARMR (512707) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-512714_KANSATP5-ConID-109462 | Single Phase Fault with Stuck Breaker on KANSATP5 (512714) 161.0 kV bus a. Apply single-phase fault on KANSATP5 (512714) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SILSPWW5 (512642) 161.0 kV bus b. 2. Disconnect KANSATP5 (512714) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118718 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118719 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from JOHNCO (514808) 138.0 kV bus to JOHNCO (514809) 345.0 kV bus to JOHNCO11 (514810) 13.8 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118720 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515136_SUNNYSD7-ConID-118867 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515136_SUNNYSD7-ConID-1188670 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515405_SUNYSD-ConID-11886701 | Single Phase Fault with Stuck Breaker on SUNYSD (515405) 13.8 kV bus a. Apply single-phase fault on SUNYSD (515405) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from G17-075-TAP (560088) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-118540 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BALKOW (515618) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-80821 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to PALDR2W7 (515590) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515802_GRACMNT4-ConID-118667 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 2. Trip line from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-532777_G17-009-TAP-ConID-8425401 | Single Phase Fault with Stuck Breaker on G17-009-TAP (532777) 345.0 kV bus a. Apply single-phase fault on G17-009-TAP (532777) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-587744_G16-091-TAP-ConID-8421801 | Single Phase Fault with Stuck Breaker on G16-091-TAP (587744) 345.0 kV bus a. Apply single-phase fault on G16-091-TAP (587744) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-507760_SW-ConID-AEPW-10 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a.Apply single-phase fault on SW (507760) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 3. Clear fault from SW (507760) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508359_WELSH-ConID-AEPW-3 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508359_WELSH-ConID-AEPW-4 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-4 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) b. 3. Drop generator from LEBROCG1 (506752 ID 1) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-5 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-8 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-9 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508832_DIANA-ConID-AEPW-6 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508832_DIANA-ConID-AEPW-7 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-508841_WILKES-ConID-AEPW-5 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a.Apply single-phase fault on WILKES (508841) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Clear fault from WILKES (508841) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-509807_ONETA--7-ConID-AEPW-82 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a.Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from ONETA--7 (509807) 345.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from ONETA--7 (509807) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 3. Clear fault from ONETA--7 (509807) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512635_KERR-ConID-GRDA-68 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512635_KERR-ConID-GRDA-69 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 b. 4. Disconnect SALNCRK5 (512805) 161.0 kV bus b. 5. Disconnect SALINA (512686) 161.0 kV bus b. 6. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 10. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 11. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 16. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 17. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 22. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 23. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-58 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-59 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-60 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-61 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER2 (512837) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-62 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-63 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-64 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-65 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-66 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-46 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-47 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-48 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-49 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA17-1 (512688) 22.799999237060547 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-71 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-72 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-73 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-74 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Drop generator from PENSA_U4 (512605 ID 4) 13.2 kV bus b. 4. Drop generator from PENSA_U5 (512607 ID 5) 13.2 kV bus b. 5. Drop generator from PENSA_U6 (512606 ID 6) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-53 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Disconnect WAGNOR (512700) 161.0 kV bus b. 4. Disconnect WAGNOR1 (512818) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-54 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Open branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512669_KETCHUM5-ConID-GRDA-70 | Single Phase Fault with Stuck Breaker on KETCHUM5 (512669) 161.0 kV bus a.Apply single-phase fault on KETCHUM5 (512669) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Disconnect AFTON (512632) 161.0 kV bus b. 2. Clear fault from KETCHUM5 (512669) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 4. Drop load from KETCHUM5 (512669 ID 1) 161.0 kV bus b. 5. Disconnect KETCHUM5 (512669) 161.0 kV bus b. 6. Disconnect AFTON1 (512845) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-55 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-56 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-57 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-77 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-78 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Disconnect TONECE1 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512751_TONECE5-ConID-GRDA-76 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512805_SALNCRK5-ConID-GRDA-75 | Single Phase Fault with Stuck Breaker on SALNCRK5 (512805) 161.0 kV bus a.Apply single-phase fault on SALNCRK5 (512805) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from SALNCRK5 (512805) b. 3. Disconnect SALINA (512686) 161.0 kV bus b. 4. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 5. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 6. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 10. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 11. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 16. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 17. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512865_GREC-ConID-GRDA-50 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECSTG_1 (512615) 21.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-512865_GREC-ConID-GRDA-51 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECCTG_1 (512614) 20.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-513596_IGLOOV-ConID-GRDA-52 | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a.Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from IGLOOV (513596) b. 3. Disconnect IGLOTER1 (513592) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-514803_SOONER-ConID-OKGE-29 | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a.Apply single-phase fault on SOONER (514803) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SOONER (515760) 13.8 kV bus b. 2. Open branch from G15-066T (560056) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 b. 3. Clear fault from SOONER (514803) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-514809_JOHNCO-ConID-OKGE-21 | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a.Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Open branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 3. Clear fault from JOHNCO (514809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515045_SEMINOL7-ConID-OKGE-28 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a.Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Disconnect SEMINO21 (515757) 14.399999618530273 kV bus b. 3. Clear fault from SEMINOL7 (515045) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515136_SUNNYSD7-ConID-OKGE-18 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a.Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SUNYSD (515405) 13.8 kV bus b. 2. Open branch from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 b. 3. Clear fault from SUNNYSD7 (515136) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515339_VBI-ConID-OKGE-32 | Single Phase Fault with Stuck Breaker on VBI (515339) 161.0 kV bus a.Apply single-phase fault on VBI (515339) 161.0 kV bus b.Run for 23.52 cycles and trip the following elements: b. 1. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 2. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 3. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 4. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 5. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 11.28 cycles and trip the following elements: b. 6. Close branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 7. Close branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 8. Close branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 9. Close branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 10. Close branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 1.62 cycles and trip the following elements: b. 11. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 9.18 cycles and trip the following elements: b. 12. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 4.02 cycles and trip the following elements: b. 13. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 4.2 cycles and trip the following elements: b. 14. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 2.4 cycles and trip the following elements: b. 15. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 0.18 cycles and trip the following elements: b. 16. Close branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 2.82 cycles and trip the following elements: b. 17. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 6.36 cycles and trip the following elements: b. 18. Close branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 1.44 cycles and trip the following elements: b. 19. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 19.38 cycles and trip the following elements: b. 20. Disconnect VBI (515769) 13.8 kV bus b.Run for 23.82 cycles and trip the following elements: b. 21. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 18.36 cycles and trip the following elements: b. 22. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b. 23. Clear fault from VBI (515339) b. 24. Drop load from HWY59 (504191 ID A1) 161.0 kV bus b. 25. Drop load from GRANDPR5 (504192 ID A1) 161.0 kV bus b. 26. Drop load from SIMMONS5 (515332 ID 1) 161.0 kV bus b. 27. Drop load from SIMMONS5 (515332 ID A1) 161.0 kV bus b. 28. Drop load from DYER (515333 ID A1) 161.0 kV bus b. 29. Drop load from ALMA (515334 ID 1) 161.0 kV bus b. 30. Drop load from RUDY (515337 ID A1) 161.0 kV bus b. 31. Drop load from OAKGROV5 (515340 ID A1) 161.0 kV bus b. 32. Drop load from WHITESD5 (515341 ID 1) 161.0 kV bus b. 33. Drop load from PUDDIN (515346 ID A1) 161.0 kV bus b. 34. Drop load from NITROUS5 (515350 ID 1) 161.0 kV bus b. 35. Drop load from GERBER (515351 ID 1) 161.0 kV bus b. 36. Drop load from TWNBRDG5 (515360 ID 1) 161.0 kV bus b. 37. Drop load from ADABELL5 (515406 ID 1) 161.0 kV bus b. 38. Disconnect HWY59 (504191) 161.0 kV bus b. 39. Disconnect GRANDPR5 (504192) 161.0 kV bus b. 40. Disconnect GERBRTP5 (515326) 161.0 kV bus b. 41. Disconnect NITROTP5 (515329) 161.0 kV bus b. 42. Disconnect SIMMONS5 (515332) 161.0 kV bus b. 43. Disconnect DYER (515333) 161.0 kV bus b. 44. Disconnect ALMA (515334) 161.0 kV bus b. 45. Disconnect RUDY (515337) 161.0 kV bus b. 46. Disconnect OAKGROV5 (515340) 161.0 kV bus b. 47. Disconnect WHITESD5 (515341) 161.0 kV bus b. 48. Disconnect PUDDIN (515346) 161.0 kV bus b. 49. Disconnect NALCOTP5 (515348) 161.0 kV bus b. 50. Disconnect NITROUS5 (515350) 161.0 kV bus b. 51. Disconnect GERBER (515351) 161.0 kV bus b. 52. Disconnect TWNBRDG5 (515360) 161.0 kV bus b. 53. Disconnect ADABELL5 (515406) 161.0 kV bus b. 54. Disconnect GRNDPRT5 (515524) 161.0 kV bus b. 55. Disconnect HWY59TP5 (515527) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515554_BVRCNTY7-ConID-OKGE-16 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a.Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 3. Clear fault from BVRCNTY7 (515554) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515576_RANCHRD7-ConID-OKGE-25 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345.0 kV bus a.Apply single-phase fault on RANCHRD7 (515576) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from SOONER (514803) 345.0 kV bus to RANCHRD7 (515576) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to FRNTWND7 (515688) 345.0 kV bus CKT 1 b. 3. Clear fault from RANCHRD7 (515576) b. 4. Drop generator from FRNTWDG1 (515691 ID 1) 0.65 kV bus b. 5. Drop load from FRNTWD11 (515689 ID S1) 34.5 kV bus b. 6. Disconnect FRNTWND7 (515688) 345.0 kV bus b. 7. Disconnect FRNTWD11 (515689) 34.5 kV bus b. 8. Disconnect FRNTWDC1 (515690) 34.5 kV bus b. 9. Disconnect FRNTWDG1 (515691) 0.65 kV bus b. 10. Disconnect FRNTWDT1 (515692) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515621_OPENSKY7-ConID-OKGE-23 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345.0 kV bus a.Apply single-phase fault on OPENSKY7 (515621) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 b. 3. Clear fault from OPENSKY7 (515621) b. 4. Drop generator from KAYWNDG1 (515651 ID 1) 0.69 kV bus b. 5. Drop generator from KAYWNDG2 (515652 ID 1) 0.69 kV bus b. 6. Drop load from KAYWND11 (515622 ID S1) 34.5 kV bus b. 7. Drop load from KAYWND12 (515623 ID S1) 34.5 kV bus b. 8. Disconnect KAYWIND7 (514825) 345.0 kV bus b. 9. Disconnect KAYWNDT1 (515619) 12.5 kV bus b. 10. Disconnect KAYWNDT2 (515620) 12.5 kV bus b. 11. Disconnect OPENSKY7 (515621) 345.0 kV bus b. 12. Disconnect KAYWND11 (515622) 34.5 kV bus b. 13. Disconnect KAYWND12 (515623) 34.5 kV bus b. 14. Disconnect KAYWNDG1 (515651) 0.69 kV bus b. 15. Disconnect KAYWNDG2 (515652) 0.69 kV bus b. 16. Disconnect KAYWNDC1 (515653) 34.5 kV bus b. 17. Disconnect KAYWNDC2 (515654) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515785_WINDFRM4-ConID-OKGE-17 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138.0 kV bus a.Apply single-phase fault on WINDFRM4 (515785) 138.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WINDFRM4 (515785) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 b. 2. Open branch from WOODWRD4 (514785) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 b. 3. Clear fault from WINDFRM4 (515785) b. 4. Drop generator from FPLWNDG1 (515895 ID 1) 0.69 kV bus b. 5. Drop load from FPLWND11 (515787 ID S1) 34.5 kV bus b. 6. Disconnect WINDFRM4 (515785) 138.0 kV bus b. 7. Disconnect FPLWIND4 (515786) 138.0 kV bus b. 8. Disconnect FPLWND11 (515787) 34.5 kV bus b. 9. Disconnect FLPWND21 (515790) 13.8 kV bus b. 10. Disconnect FPLWNDG1 (515895) 0.69 kV bus b. 11. Disconnect FPLWNDC1 (515896) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515800_GRACMNT7-ConID-OKGE-22 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a.Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from LES (587744) None kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Open branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 3. Clear fault from GRACMNT7 (515800) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-520430_NOELSW-ConID-WFEC-59 | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a.Apply single-phase fault on NOELSW (520430) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DRIFTWD4 (521200) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 b. 3. Open branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 4. Clear fault from NOELSW (520430) b. 5. Drop load from CHRKCTY4 (520431 ID 1) 138.0 kV bus b. 6. Drop load from SALTPLN4 (520437 ID 1) 138.0 kV bus b. 7. Drop load from SALTPLN4 (520437 ID 2) 138.0 kV bus b. 8. Disconnect CHRKCTY4 (520431) 138.0 kV bus b. 9. Disconnect SALTPLN4 (520437) 138.0 kV bus b. 10. Drop load from ROSEVLY4 (520436 ID 1) 138.0 kV bus b. 11. Drop load from AVARD (520601 ID 1) 138.0 kV bus b. 12. Disconnect ROSEVLY4 (520436) 138.0 kV bus b. 13. Disconnect AVARD (520601) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-520814_ANADARK4-ConID-WFEC-51 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138.0 kV bus a.Apply single-phase fault on ANADARK4 (520814) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SUNSHIN4 (521059) 138.0 kV bus to BRIDGCR4 (520501) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 3. Open branch from ANADRK5 (520812) 13.8 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 4. Open branch from ANADARK4 (520814) 138.0 kV bus to POCASET4 (521031) 138.0 kV bus CKT 1 b. 5. Clear fault from ANADARK4 (520814) b. 6. Drop generator from ANADRK5 (520812 ID 1) 13.8 kV bus b. 7. Drop load from ANADRK5 (520812 ID F1) 13.8 kV bus b. 8. Drop load from ANADRK5 (520812 ID V1) 13.8 kV bus b. 9. Disconnect ANADRK5 (520812) 13.8 kV bus b. 10. Drop load from TUTTLE (520496 ID 1) 138.0 kV bus b. 11. Drop load from BRIDGCR4 (520501 ID 1) 138.0 kV bus b. 12. Drop load from POCASET4 (521031 ID 1) 138.0 kV bus b. 13. Disconnect TUTTLE (520496) 138.0 kV bus b. 14. Disconnect BRIDGCR4 (520501) 138.0 kV bus b. 15. Disconnect POCASET4 (521031) 138.0 kV bus b. 16. Disconnect TUTLETP4 (521072) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-520920_FTSUPLY4-ConID-WFEC-55 | Single Phase Fault with Stuck Breaker on FTSUPLY4 (520920) 138.0 kV bus a.Apply single-phase fault on FTSUPLY4 (520920) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SLEEPBR4 (520922) 138.0 kV bus to FTSUPLY4 (520920) 138.0 kV bus CKT 1 b. 2. Drop generator from SLP (521145 ID 1) 0.6000000238418579 kV bus b. 3. Disconnect SLEEPBR4 (520922) 138.0 kV bus b. 4. Disconnect SLP (521141) 34.5 kV bus b. 5. Disconnect SLP (521144) 34.5 kV bus b. 6. Disconnect SLP (521145) 0.6000000238418579 kV bus b. 7. Disconnect SLP (521151) 9.949999809265137 kV bus b.Run for 9.0 cycles and trip the following elements: b. 8. Open branch from MOORLND4 (520999) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 9. Clear fault from FTSUPLY4 (520920) b. 10. Open branch from FTSUPLY4 (520920) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 11. Drop load from IODINE (520957 ID 1) 138.0 kV bus b. 12. Disconnect IODINE (520957) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-521016_OKEENE-ConID-WFEC-60 | Single Phase Fault with Stuck Breaker on OKEENE (521016) 138.0 kV bus a.Apply single-phase fault on OKEENE (521016) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DOVERSW4 (520882) 138.0 kV bus to OKEENE (521016) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 3. Clear fault from OKEENE (521016) b. 4. Drop load from PIC4 (520425 ID 1) 138.0 kV bus b. 5. Drop load from CEDRDAL4 (520507 ID 1) 138.0 kV bus b. 6. Disconnect PIC4 (520425) 138.0 kV bus b. 7. Disconnect CDRDLTP4 (520848) 138.0 kV bus b. 8. Disconnect CEDRDAL4 (520507) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-65 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from CLINTJC4 (511485) 138.0 kV bus to CLINTON4 (520856) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b. 3. Open branch from WASHITA4 (521089) 138.0 kV bus to ONEY (521017) 138.0 kV bus CKT 1 b. 4. Clear fault from WASHITA4 (521089) b. 5. Drop load from HINTON (520468 ID 1) 138.0 kV bus b. 6. Drop load from DEERCR (520503 ID 1) 138.0 kV bus b. 7. Drop load from CLINTON4 (520856 ID 1) 138.0 kV bus b. 8. Drop load from HYDRO (520950 ID 1) 138.0 kV bus b. 9. Drop load from NIJECT (521010 ID 1) 138.0 kV bus b. 10. Drop load from NIJECT (521010 ID 2) 138.0 kV bus b. 11. Drop load from ONEY (521017 ID 1) 138.0 kV bus b. 12. Drop load from SICKLES4 (521050 ID 1) 138.0 kV bus b. 13. Drop load from WEATHFD4 (521092 ID 1) 138.0 kV bus b. 14. Disconnect HINTON (520468) 138.0 kV bus b. 15. Disconnect DEERCR (520503) 138.0 kV bus b. 16. Disconnect BINGERJ4 (520827) 138.0 kV bus b. 17. Disconnect CLINTON4 (520856) 138.0 kV bus b. 18. Disconnect HYDRO (520950) 138.0 kV bus b. 19. Disconnect NIJECT (521010) 138.0 kV bus b. 20. Disconnect ONEY (521017) 138.0 kV bus b. 21. Disconnect SICKLES4 (521050) 138.0 kV bus b. 22. Disconnect WEATHFD4 (521092) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-66 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 3. Clear fault from WASHITA4 (521089) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523777_WHEELER-ConID-SPS-140 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from WHEELER (523777) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT &1 b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523777_WHEELER-ConID-SPS-143 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532791_BENTON-ConID-Evergy-105 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532791_BENTON-ConID-Evergy-106 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Disconnect ROSEH3 (532831) 13.8 kV bus b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-152 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Disconnect ROSEH3 (532831) 13.8 kV bus b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-121 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Disconnect WOLFCRK1 (532962) 17.0 kV bus b. 4. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 5. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542965_WGRDNR7-ConID-Evergy-150 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345.0 kV bus a.Apply single-phase fault on W.GRDNR7 (542965) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from W.GRDNR7 (542965) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 b. 2. Open branch from STILWEL7 (542968) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 3. Clear fault from W.GRDNR7 (542965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542968_STILWEL7-ConID-Evergy-148 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345.0 kV bus a.Apply single-phase fault on STILWEL7 (542968) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from PECULR (541198) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 3. Clear fault from STILWEL7 (542968) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-140 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-141 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-142 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-143 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542956) 24.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-547469_RIV4525-ConID-EMDE-34 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161.0 kV bus a.Apply single-phase fault on RIV4525 (547469) 161.0 kV bus b.Run for 7.0 cycles and trip the following elements: b. 1. Open branch from RIV4525 (547469) 161.0 kV bus to NEOSHO (532937) 161.0 kV bus CKT 1 b.Run for 86.0 cycles and trip the following elements: b. 4. Open branch from BAX488 (547729) 161.0 kV bus to HOC404 (547487) 161.0 kV bus CKT 1 b. 5. Clear fault from RIV4525 (547469) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512753_TONNEC2-512745_SSLINC2_Ckt1 | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 b. 5. Drop load from bus SSNORT2 (512746) 69.0 kV bus b. 6. Drop load from bus SSLINC2 (512745) 69.0 kV bus b. 7. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 c. 2. Reclose branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 c. 3. Reclose branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 c. 4. Reclose branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 c. 5. Reclose branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 d. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 d. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 d. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 d. 5. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512753_TONNEC2-512751_TONECE5_3Winding | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512751_TONECE5-512643_SILMCTY5_Ckt1 | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512751_TONECE5-512750_TONECE7_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512751_TONECE5-512753_TONNEC2_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512750_TONECE7-512650_GRDA1_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512750_TONECE7-506935_FLINTCR7_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512750_TONECE7-512751_TONECE5_3Winding | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506935_FLINTCR7-506929_ECNTRTN5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 b. 2. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 3. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 4. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 5. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 c. 2. Reclose branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 3. Reclose branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 d. 2. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506935_FLINTCR7-549984_BROOKLINE_Ckt1 | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506935_FLINTCR7-506934_FLINTCR5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512643_SILMCTY5-506948_SILOAM_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512643_SILMCTY5-512714_KANSATP5_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512643_SILMCTY5-512820_SILMCTY2_3Winding | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512650_GRDA1-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512650_GRDA1-512865_GREC_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512650_GRDA1-512656_GRDA1_3Winding | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_549984_BROOKLINE-300045_7MORGAN_Ckt1 | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_549984_BROOKLINE-549969_BROOKLINE_3Winding | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at BRKLNE (549989) to trip transformer at BRKLNE XF2 113.200 (549989) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-506990_GREENHOUSE_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 b. 2. Drop load from bus GENTRY (504201) 161.0 kV bus b. 3. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 b. 4. Drop load from bus BEN279_5 (506960) 161.0 kV bus b. 5. Drop load from bus GREENHOUSE (506990) 161.0 kV bus b. 6. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. 2. Reclose branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 c. 3. Reclose branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. 2. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 d. 3. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-506957_TONTITN5_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-547484_DEC392_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-504202_SILOAMSP_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SILOAMSP (504202) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-506935_FLINTCR7_3Winding | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-506948_SILOAM_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506948_SILOAM-506944_CHAMSPR5_Ckt1 | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506948_SILOAM-506936_GREENLD2_3Winding | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SILOAM-1 (506917) to trip transformer at SILOAM-1 13.200 (506917) 13.2 kV bus b. 2. Drop switching device from bus SILOAM (506973) 69.0 kV bus b. 3. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 b. 4. Drop load from bus LINCOLN2 (506972) 69.0 kV bus b. 5. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 b. 6. Drop load from bus PRGROVE2 (506941) 69.0 kV bus b. 7. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 c. 2. Reclose branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 c. 3. Reclose branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 d. 2. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 d. 3. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512820_SILMCTY2-512730_SSSWES2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SSSWES2 (512730) 69.0 kV bus b. 2. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512820_SILMCTY2-512643_SILMCTY5_3Winding | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512820_SILMCTY2-512744_SSMOSS2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 b. 2. Drop load from bus SSMOSS2 (512744) 69.0 kV bus b. 3. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 c. 2. Reclose branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 d. 2. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt2 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300740_7SPORTSMAN-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512865_GREC-513596_IGLOOV_Ckt1 | 3 Phase fault on GREC (512865) 345.0 kV a. Apply fault on GREC (512865) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-512742_WMAIN_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus WMAIN (512742) 161.0 kV bus b. 2. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-512650_GRDA1_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300045_7MORGAN-300949_7JASPER_Ckt1 | 3 Phase fault on 7MORGAN (300045) 345.0 kV a. Apply fault on 7MORGAN (300045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_549969_BROOKLINE-505492_SPRGFLD5_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_549969_BROOKLINE-549955_JUNCTION_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506957_TONTITN5-504010_ELMSPRGS_Ckt1 | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506957_TONTITN5-506945_CHAMSPR7_3Winding | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus b. 2. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506944_CHAMSPR5-506992_WEDINGTON_Ckt1 | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506944_CHAMSPR5-506945_CHAMSPR7_3Winding | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512714_KANSATP5-512635_KERR_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512714_KANSATP5-512643_SILMCTY5_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512714_KANSATP5-512715_KANSAS_3Winding | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 b. 2. Disconnect bus at KANSAS1 (512736) to trip transformer at KANSAS1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506929_ECNTRTN5-506935_FLINTCR7_3Winding | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 b. 4. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 5. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 6. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 7. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 2. Reclose branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 c. 3. Reclose branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 2. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 d. 3. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506929_ECNTRTN5-506963_BENT_SL5_Ckt1 | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 2. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513596_IGLOOV-513591_HERRON_3Winding | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus b. 2. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513596_IGLOOV-509852_TNO--7_Ckt1 | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506945_CHAMSPR7-509745_CLARKSV7_Ckt1 | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506945_CHAMSPR7-506957_TONTITN5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 b. 2. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506945_CHAMSPR7-506944_CHAMSPR5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512751_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a. Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 b. 2. Disconnect TONECE1 (512752) 13.2 kV bus to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512750_TONECE7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a. Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506935_FLINTCR7 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 3. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 4. Trip branch from SHIPERD5 (506980) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 5. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 6. Trip branch from CENTRTN5 (506952) 161.0 kV bus to ECNTRTN5 (506929) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512643_SILMCTY5 | Single Phase Fault with Stuck Breaker on SILMCTY5 (512643) 161.0 kV bus a. Apply single-phase fault on SILMCTY5 (512643) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILSPWW5 (512642) 161.0 kV bus CKT 1 b. 3. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 4. Trip branch from SILSPWW5 (512642) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512650_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a. Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-549984_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549984) 345.0 kV bus a. Apply single-phase fault on BROOKLINE (549984) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 b. 2. Disconnect BRKLNE (549988) 13.2 kV bus to trip transformer at BRKLNE XF1 113.200 (549988) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506934_FLINTCR5 | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161.0 kV bus a. Apply single-phase fault on FLINTCR5 (506934) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 kV bus to GENTRY (504201) 161.0 kV bus CKT 1 b. 3. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506948_SILOAM | Single Phase Fault with Stuck Breaker on SILOAM (506948) 161.0 kV bus a. Apply single-phase fault on SILOAM (506948) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 b. 2. Trip branch from SILOAM (506948) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512656_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 8. Disconnect GRDA2 (512826) 13.8 kV bus to trip transformer at GRDA2 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-300045_7MORGAN | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345.0 kV bus a. Apply single-phase fault on 7MORGAN (300045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7MORGAN (300045) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-549969_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549969) 161.0 kV bus a. Apply single-phase fault on BROOKLINE (549969) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 b. 2. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506957_TONTITN5 | Single Phase Fault with Stuck Breaker on TONTITN5 (506957) 161.0 kV bus a. Apply single-phase fault on TONTITN5 (506957) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 b. 2. Disconnect TONTITN1 (506958) 13.8 kV bus to trip transformer at TONTITN1 13.8 kV bus b. 3. Trip branch from TONTITN7 (506959) 345.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506944_CHAMSPR5 | Single Phase Fault with Stuck Breaker on CHAMSPR5 (506944) 161.0 kV bus a. Apply single-phase fault on CHAMSPR5 (506944) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 b. 2. Disconnect CHAMSPR1 (506919) 13.8 kV bus to trip transformer at CHAMSPR1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514803_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a. Apply single-phase fault on SOONER (514803) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-506929_ECNTRTN5 | Single Phase Fault with Stuck Breaker on ECNTRTN5 (506929) 161.0 kV bus a. Apply single-phase fault on ECNTRTN5 (506929) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 kV bus to SHIPERD5 (506980) 161.0 kV bus CKT 1 b. 4. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 5. Trip branch from SHIPERD7 (506979) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 b. 6. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 7. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to BENT_SL5 (506963) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515576_RANCHRD7-515621_OPENSKY7_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515576_RANCHRD7-514803_SOONER_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514803_SOONER-560056_G15-066T_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514803_SOONER-509755_WEKIWA-7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514803_SOONER-516010_PINTAIL7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514803_SOONER-514802_SOONER_3Winding | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SOONER (515760) to trip transformer at SOONER 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514803_SOONER-587804_G16-119-TAP_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515621_OPENSKY7-560053_G15-052T_Ckt1 | 3 Phase fault on OPENSKY7 (515621) 345.0 kV a. Apply fault on OPENSKY7 (515621) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509755_WEKIWA-7-509757_WEKIWA-4_3Winding | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WEKIW1-1 (509879) to trip transformer at WEKIW1-1 34.500 (509879) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509755_WEKIWA-7-509870_SAPLPRD7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509755_WEKIWA-7-509852_TNO--7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560056_G15-066T-512694_CLEVLND7_Ckt1 | 3 Phase fault on G15-066T (560056) 345.0 kV a. Apply fault on G15-066T (560056) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514802_SOONER-514798_SNRPMPT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514802_SOONER-514704_MILLERT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560053_G15-052T-532794_ROSEHIL7_Ckt1 | 3 Phase fault on G15-052T (560053) 345.0 kV a. Apply fault on G15-052T (560053) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514802_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514802) 138.0 kV bus a. Apply single-phase fault on SOONER (514802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_763113_G18-079-TAP-512734_FARML_Ckt1 | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_763113_G18-079-TAP-510380_DELWARE7_3Winding | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 b. 2. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512734_FARML-510378_SCOFCTY4_Ckt1 | 3 Phase fault on FARML (512734) 138.0 kV a. Apply fault on FARML (512734) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510380_DELWARE7-510406_NES-7_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510380_DELWARE7-532793_NEOSHO_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510380_DELWARE7-763113_G18-079-TAP_3Winding | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus b. 2. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510378_SCOFCTY4-510422_COFFEYT4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510378_SCOFCTY4-510420_SCOFFEYV4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SCOFFEYV4 (510420) 138.0 kV bus b. 2. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510406_NES-7-509852_TNO--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510406_NES-7-509807_ONETA--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532793_NEOSHO-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532793_NEOSHO-542981_LACYGNE7_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532793_NEOSHO-533021_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532793_NEOSHO-532777_G17-009-TAP_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532793_NEOSHO-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510422_COFFEYT4-533002_DEARING4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510422_COFFEYT4-510391_BV-SE--4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 b. 2. Drop load from bus NBVILLE4 (510386) 138.0 kV bus b. 3. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 c. 2. Reclose branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 d. 2. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt2 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt1 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509852_TNO--7-509895_TNO2-4_3Winding | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_542981_LACYGNE7-542968_STILWEL7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_542981_LACYGNE7-542965_WGRDNR7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533021_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533021_NEOSHO-533022_NEOSHON4_CktZ1 | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532937_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532937_NEOSHO-547469_RIV4525_Ckt1 | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533020_NEOSHOS4-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEOSH5 (532959) to trip transformer at NEOSH5 1 13.200 (532959) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533020_NEOSHOS4-533003_LIBERTY4_Ckt1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 b. 2. Drop load from bus TV1MNDV4 (533008) 138.0 kV bus b. 3. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 c. 2. Reclose branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 d. 2. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533020_NEOSHOS4-533021_NEOSHO_CktZ1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533022_NEOSHON4-588664_G17-022-TAP_Ckt1 | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 b. 2. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 3. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 4. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 5. Drop switching device from bus NEPARSN4 (533005) 138.0 kV bus b. 6. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 c. 2. Reclose branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 d. 2. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_533022_NEOSHON4-533768_NEOSHON2_3Winding | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEC (532711) to trip transformer at NEC U3 12.000 (532711) 12.0 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510380_DELWARE7 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510378_SCOFCTY4 | Single Phase Fault with Stuck Breaker on SCOFCTY4 (510378) 138.0 kV bus a. Apply single-phase fault on SCOFCTY4 (510378) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510406_NES-7 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 b. 2. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-532793_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532793) 345.0 kV bus a. Apply single-phase fault on NEOSHO (532793) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509807_ONETA--7 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509852_TNO--7 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TNO2-1 (509894) 34.5 kV bus to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus b. 2. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-542981_LACYGNE7 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a. Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-533021_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (533021) 138.0 kV bus a. Apply single-phase fault on NEOSHO (533021) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532824) 13.8 kV bus to trip transformer at N345 1 1 13.8 kV bus b. 2. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-532937_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532937) 161.0 kV bus a. Apply single-phase fault on NEOSHO (532937) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510907_PITTSB-7-514809_JOHNCO_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510907_PITTSB-7-515045_SEMINOL7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510907_PITTSB-7-515422_C-RIVER7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510907_PITTSB-7-510911_VALIANT7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510911_VALIANT7-508298_LYDIA_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510911_VALIANT7-510918_VALIANT4_3Winding | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at VALN3-1 (510939) to trip transformer at VALN3-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510911_VALIANT7-521157_HUGO_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510911_VALIANT7-508072_NWTXARK7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514809_JOHNCO-514808_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510907_PITTSB-7 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514809_JOHNCO-515136_SUNNYSD7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514809_JOHNCO-516006_DMNDSPG7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt2 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_3Winding | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SEMINO11 (515756) to trip transformer at SEMINO11 14.400 (515756) 14.399999618530273 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515045_SEMINOL7-514908_ARCADIA7_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515422_C-RIVER7-510951_TALAWANDA_3Winding | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at C-RIVER1 (510947) to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515422_C-RIVER7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508298_LYDIA-508359_WELSH_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508298_LYDIA-508072_NWTXARK7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510918_VALIANT4-510866_V-WEYCO4_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510918_VALIANT4-520948_HUGO_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515136_SUNNYSD7-511568_TERRYRD7_Ckt1 | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515136_SUNNYSD7-515135_SUNNYSD4_3Winding | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNYSD (515405) to trip transformer at SUNYSD 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514808_JOHNCO-514809_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514808_JOHNCO-515120_RUSSET-4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514808_JOHNCO-515150_CANEYCK4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514808_JOHNCO-515122_SXMLCKT4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514934_DRAPER-514933_DRAPER_3Winding | 3 Phase fault on DRAPER (514934) 345.0 kV a. Apply fault on DRAPER (514934) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DRAPER41 (515721) to trip transformer at DRAPER41 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510911_VALIANT7 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 2. Disconnect VALN2-1 (510938) 13.8 kV bus to trip transformer at VALN2-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514809_JOHNCO | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a. Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect JOHNCO11 (514810) 13.8 kV bus to trip transformer at JOHNCO11 13.8 kV bus b. 2. Trip branch from JOHNCO (514809) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515045_SEMINOL7 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a. Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 b. 2. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515422_C-RIVER7 | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345.0 kV bus a. Apply single-phase fault on C-RIVER7 (515422) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect C-RIVER1 (510947) 13.8 kV bus to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 kV bus to TALAWANDA (510951) 138.0 kV bus CKT 1 b. 3. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-510918_VALIANT4 | Single Phase Fault with Stuck Breaker on VALIANT4 (510918) 138.0 kV bus a. Apply single-phase fault on VALIANT4 (510918) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 kV bus to V-WEYCO4 (510866) 138.0 kV bus CKT 1 b. 4. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515136_SUNNYSD7 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Disconnect SUNYSD (515405) 13.8 kV bus to trip transformer at SUNYSD 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514934_DRAPER | Single Phase Fault with Stuck Breaker on DRAPER (514934) 345.0 kV bus a. Apply single-phase fault on DRAPER (514934) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DRAPER31 (515720) 13.8 kV bus to trip transformer at DRAPER31 13.8 kV bus b. 2. Disconnect DRAPER41 (515721) 13.8 kV bus to trip transformer at DRAPER41 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508298_LYDIA-510911_VALIANT7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508072_NWTXARK7-507454_TURK_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 b. 2. Disconnect bus at TURK (507457) to trip transformer at TURK 1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508072_NWTXARK7-508071_NWTXARK4_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX2-1 (508101) to trip transformer at NWTEX2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508072_NWTXARK7-508359_WELSH_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508072_NWTXARK7-510911_VALIANT7_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508359_WELSH-508832_DIANA_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508359_WELSH-508832_DIANA_Ckt2 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508359_WELSH-508841_WILKES_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508359_WELSH-5917_SPPMAINBUS_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510911_VALIANT7-510907_PITTSB-7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508071_NWTXARK4-508070_NWT-BNT4_Ckt1 | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508071_NWTXARK4-508072_NWTXARK7_3Winding | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX1-1 (508100) to trip transformer at NWTEX1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508298_LYDIA | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508072_NWTXARK7 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to TURK (507455) 345.0 kV bus CKT 1 b. 2. Disconnect TURK (507457) 13.8 kV bus to trip transformer at TURK 1 13.8 kV bus b. 3. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508359_WELSH | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508071_NWTXARK4 | Single Phase Fault with Stuck Breaker on NWTXARK4 (508071) 138.0 kV bus a. Apply single-phase fault on NWTXARK4 (508071) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 b. 2. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508832_DIANA | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508809_LONGWD-508808_LONGWD_3Winding | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508809_LONGWD-508841_WILKES_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508809_LONGWD-507760_SW_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508809_LONGWD-337376_7SAREPTA%_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337376_7SAREPTA%-337561_8EL_3Winding | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 b. 2. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337376_7SAREPTA%-337363_3SAREPTA!_Ckt1 | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507760_SW-507759_SW_3Winding | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507760_SW-500250_DOLHILL7_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507760_SW-508832_DIANA_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508841_WILKES-508840_WILKES_3Winding | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt2 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508841_WILKES-508359_WELSH_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508808_LONGWD-508809_LONGWD_3Winding | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508808_LONGWD-508806_LIEBERM4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508808_LONGWD-507711_ARSHILL4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 b. 2. Drop load from bus NORAM (507774) 138.0 kV bus b. 3. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 b. 4. Drop load from bus RAINES (507749) 138.0 kV bus b. 5. Drop switching device from bus RAINES (507749) 138.0 kV bus b. 6. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 c. 2. Reclose branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 c. 3. Reclose branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 d. 2. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 d. 3. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508808_LONGWD-507727_FLOURNY4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508808_LONGWD-508566_SABMINT4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 2. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 4. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 5. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 2. Reclose branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 3. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 2. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337368_8MT_OLIVE%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337420_8STERLING%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt2 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337643_8SHERIDAN%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337376_7SAREPTA%_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus b. 2. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337539_3EL_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337561_8EL-337515_8MCNEIL%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337363_3SAREPTA!-337376_7SAREPTA%_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337363_3SAREPTA!-337361_3MINDEN_LA!_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_500250_DOLHILL7-500260_DOLHILL6_Ckt1 | 3 Phase fault on DOLHILL7 (500250) 345.0 kV a. Apply fault on DOLHILL7 (500250) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508832_DIANA-508359_WELSH_Ckt1 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508832_DIANA-508359_WELSH_Ckt2 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507759_SW-507760_SW_3Winding | 3 Phase fault on SW (507759) 138.0 kV a. Apply fault on SW (507759) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508840_WILKES-508841_WILKES_3Winding | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508840_WILKES-508297_LSSOUTH4_Ckt1 | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508806_LIEBERM4-588404_G16-167-TAP_Ckt1 | 3 Phase fault on LIEBERM4 (508806) 138.0 kV a. Apply fault on LIEBERM4 (508806) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507727_FLOURNY4-507726_FLOURNY2_3Winding | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLOURNY1 (507740) to trip transformer at FLOURNY1 12.470 (507740) 12.470000267028809 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507727_FLOURNY4-508808_LONGWD_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507727_FLOURNY4-507732_GENMOTR4_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENMOTR4 (507732) 138.0 kV bus b. 2. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337368_8MT_OLIVE%-509366_LAYFLD8_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337368_8MT_OLIVE%-337369_6MT_OLIVE%_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_337539_3EL-337561_8EL_3Winding | 3 Phase fault on 3EL (337539) 115.0 kV a. Apply fault on 3EL (337539) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507711_ARSHILL4-507789_STLGENS4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_507711_ARSHILL4-507731_FTHUMBG4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508566_SABMINT4-508562_PIRKEY_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508566_SABMINT4-508808_LONGWD_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 2. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 4. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 5. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 2. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 3. Reclose branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 2. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508566_SABMINT4-508577_SABINEM4_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 2. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 3. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508562_PIRKEY-508595_HALLSVLS4_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508562_PIRKEY-509092_EASTON_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus EASTON (509092) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508809_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-337376_7SAREPTA% | Single Phase Fault with Stuck Breaker on 7SAREPTA% (337376) 345.0 kV bus a. Apply single-phase fault on 7SAREPTA% (337376) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to 7EL (337562) 345.0 kV bus CKT 1 b. 2. Disconnect 1EL (337565) 13.8 kV bus to trip transformer at 1EL DORADO2 13.8 kV bus b. 3. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-507760_SW | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508841_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508808_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508808) 138.0 kV bus a. Apply single-phase fault on LONGWD (508808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-337561_8EL | Single Phase Fault with Stuck Breaker on 8EL (337561) 500.0 kV bus a. Apply single-phase fault on 8EL (337561) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 b. 2. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-337363_3SAREPTA! | Single Phase Fault with Stuck Breaker on 3SAREPTA! (337363) 115.0 kV bus a. Apply single-phase fault on 3SAREPTA! (337363) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-507759_SW | Single Phase Fault with Stuck Breaker on SW (507759) 138.0 kV bus a. Apply single-phase fault on SW (507759) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508840_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508840) 138.0 kV bus a. Apply single-phase fault on WILKES (508840) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus b. 2. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508806_LIEBERM4 | Single Phase Fault with Stuck Breaker on LIEBERM4 (508806) 138.0 kV bus a. Apply single-phase fault on LIEBERM4 (508806) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to LONGWD (508808) 138.0 kV bus CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-338440_8PANDA% | Single Phase Fault with Stuck Breaker on 8PANDA% (338440) 500.0 kV bus a. Apply single-phase fault on 8PANDA% (338440) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 1 b. 2. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-337539_3EL | Single Phase Fault with Stuck Breaker on 3EL (337539) 115.0 kV bus a. Apply single-phase fault on 3EL (337539) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1EL (337564) 13.8 kV bus to trip transformer at 1EL DORADO1 13.8 kV bus b. 2. Disconnect 1EL (337566) 13.8 kV bus to trip transformer at 1EL DORADO3 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-507711_ARSHILL4 | Single Phase Fault with Stuck Breaker on ARSHILL4 (507711) 138.0 kV bus a. Apply single-phase fault on ARSHILL4 (507711) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 b. 2. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508562_PIRKEY | Single Phase Fault with Stuck Breaker on PIRKEY (508562) 138.0 kV bus a. Apply single-phase fault on PIRKEY (508562) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 kV bus to HALLSVLS4 (508595) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from PIRKEY (508562) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511468_LES-7-511456_OKU-7_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511468_LES-7-760938_G17-171-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511468_LES-7-511467_LES-4_3Winding | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511468_LES-7-587744_G16-091-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511456_OKU-7-762467_G18-015-TAP_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511456_OKU-7-511565_OKLAUN_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus OKLAUN (511565) 345.0 kV bus b. 2. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_587744_G16-091-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-091-TAP (587744) 345.0 kV a. Apply fault on G16-091-TAP (587744) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_760938_G17-171-TAP-511568_TERRYRD7_Ckt1 | 3 Phase fault on G17-171-TAP (760938) 345.0 kV a. Apply fault on G17-171-TAP (760938) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511468_LES-7_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511537_ARTVLTP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 b. 2. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 3. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 c. 2. Reclose branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 d. 2. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511439_LWSTAP_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511494_COMMTAP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511437_COMANC-4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511466_LES-2_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#1-1 (511416) to trip transformer at LES#1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511423_FLE_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511467_LES-4-511486_ELGINJT4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515800_GRACMNT7-514801_MINCO_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515800_GRACMNT7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515800_GRACMNT7-515802_GRACMNT4_3Winding | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRCMNT11 (515801) to trip transformer at GRCMNT11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_762467_G18-015-TAP-762216_G17-151TAP_Ckt1 | 3 Phase fault on G18-015-TAP (762467) 345.0 kV a. Apply fault on G18-015-TAP (762467) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511568_TERRYRD7-515136_SUNNYSD7_Ckt1 | 3 Phase fault on TERRYRD7 (511568) 345.0 kV a. Apply fault on TERRYRD7 (511568) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511439_LWSTAP-511488_112GORE4_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 b. 2. Drop load from bus RPPAPER4 (511512) 138.0 kV bus b. 3. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 c. 2. Reclose branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 d. 2. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511439_LWSTAP-511431_LWS_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus LWS (511431) 138.0 kV bus b. 2. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511466_LES-2-511503_LAW_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511466_LES-2-511487_ELGINJT2_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 3. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 b. 4. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 5. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 6. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 b. 7. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 8. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 c. 3. Reclose branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 c. 4. Reclose branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 d. 3. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 d. 4. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514801_MINCO-516096_NORMHLL7_Ckt1 | 3 Phase fault on MINCO (514801) 345.0 kV a. Apply fault on MINCO (514801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560078_G16-037-TAP-511553_CHISHOLM7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt1 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt2 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-511468_LES-7 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-511456_OKU-7 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-511467_LES-4 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LES#5-1 (511411) 13.8 kV bus to trip transformer at LES#5-1 13.8 kV bus b. 2. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to SHERID4 (511474) 138.0 kV bus CKT 1 b. 3. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 4. Trip branch from SHERID4 (511474) 138.0 kV bus to ARTVLTP4 (511537) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515800_GRACMNT7 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a. Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-511466_LES-2 | Single Phase Fault with Stuck Breaker on L.E.S.-2 (511466) 69.0 kV bus a. Apply single-phase fault on L.E.S.-2 (511466) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-S2 (511470) 69.0 kV bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 kV bus to LAW (511503) 69.0 kV bus CKT 1 b. 5. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-N2 (511469) 69.0 kV bus CKT 1 b. 6. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 7. Trip branch from LGORE-N2 (511469) 69.0 kV bus to FT.SILL2 (511461) 69.0 kV bus CKT 1 b. 8. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 9. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 10. Trip branch from FT.SILL2 (511461) 69.0 kV bus to PO.HILL2 (511473) 69.0 kV bus CKT 1 b. 11. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 12. Trip branch from PO.HILL2 (511473) 69.0 kV bus to ELGINJT2 (511487) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514801_MINCO | Single Phase Fault with Stuck Breaker on MINCO (514801) 345.0 kV bus a. Apply single-phase fault on MINCO (514801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515802_GRACMNT4 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-300069_5CHOTEAU1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512656_GRDA1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-301344_5CDRCRST_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512629_DRYGULCH5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512626_MAID_3Winding | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512635_KERR_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512635_KERR_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512648_MAID-512656_GRDA1_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-512648_MAID_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. 2. Reclose branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 c. 3. Reclose branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 c. 4. Reclose branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. 2. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 d. 3. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 d. 4. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-513570_CHOUTEAUCRK516100_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-512671_HUNT_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 2. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 3. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512656_GRDA1-512700_WAGNOR_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512650_GRDA1-512750_TONECE7_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300069_5CHOTEAU1-301348_5CHOTEAU2_CktZ1 | 3 Phase fault on 5CHOTEAU1 (300069) 161.0 kV a. Apply fault on 5CHOTEAU1 (300069) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512629_DRYGULCH5-512654_PENSA_Ckt1 | 3 Phase fault on DRYGULCH5 (512629) 161.0 kV a. Apply fault on DRYGULCH5 (512629) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512714_KANSATP5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt2 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512654_PENSA_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512771_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512635_KERR-512770_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512638_CATSAGR5-512627_COLINS_Ckt1 | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 c. 2. Reclose branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 d. 2. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512638_CATSAGR5-509790_CATOOSA4_3Winding | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CATTER1 (512833) to trip transformer at CATTER1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512626_MAID-512671_HUNT_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 c. 2. Reclose branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 c. 3. Reclose branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 c. 4. Reclose branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 c. 5. Reclose branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 d. 2. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 d. 3. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 d. 4. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 d. 5. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512626_MAID-512648_MAID_3Winding | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512626_MAID-512683_AMERCAST_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 b. 2. Drop load from bus REDDEN (512698) 69.0 kV bus b. 3. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 b. 4. Drop load from bus AMERCAST (512683) 69.0 kV bus b. 5. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 c. 2. Reclose branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 c. 3. Reclose branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 d. 2. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 d. 3. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512700_WAGNOR-512697_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512700_WAGNOR-512640_OKAYGR_Ckt1 | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513570_CHOUTEAUCRK516100-512651_CLARMR_Ckt1 | 3 Phase fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV a. Apply fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301344_5CDRCRST-512648_MAID_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301344_5CDRCRST-301345_2CDRCRST_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301344_5CDRCRST-512655_TAHLQH_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300739_7BLACKBERRY-300949_7JASPER_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300739_7BLACKBERRY-532797_WOLFCRK7_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300739_7BLACKBERRY-532793_NEOSHO_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300741_5SPORTSMAN-301348_5CHOTEAU2_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt2 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509852_TNO--7-510406_NES-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509852_TNO--7-512694_CLEVLND7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509852_TNO--7-509755_WEKIWA-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512654_PENSA-512669_KETCHUM5_Ckt1 | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512654_PENSA-512628_PENSA_3Winding | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PENSA (512841) to trip transformer at PENSA 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509790_CATOOSA4-509752_INOLATP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509790_CATOOSA4-509835_TERNITP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512640_OKAYGR-505560_FT_Ckt1 | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512640_OKAYGR-512646_OKAYGR_3Winding | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OKAY1 (512848) to trip transformer at OKAY1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512697_WAGNOR-512700_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512697_WAGNOR-512801_WAGCTY12_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 b. 2. Drop load from bus WAGCTY22 (512759) 69.0 kV bus b. 3. Drop load from bus WAGCTY12 (512801) 69.0 kV bus b. 4. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 c. 2. Reclose branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 d. 2. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512697_WAGNOR-300958_2HIGHLND_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 b. 2. Drop load from bus 2WAGNERW (300972) 69.0 kV bus b. 3. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 b. 4. Drop load from bus 2COWETA (300955) 69.0 kV bus b. 5. Drop load from bus 2HIGHLND (300958) 69.0 kV bus b. 6. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 c. 2. Reclose branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 c. 3. Reclose branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 d. 2. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 d. 3. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512697_WAGNOR-512690_WAGNRTP2_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512651_CLARMR-510396_NES-4_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR4 (512813) to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 c. 2. Reclose branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 d. 2. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512651_CLARMR-512679_CLARMR_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR2 (512815) to trip transformer at CLARMR2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301345_2CDRCRST-301344_5CDRCRST_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301345_2CDRCRST-513059_HULBERKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 b. 2. Drop load from bus 2PEGGS (300962) 69.0 kV bus b. 3. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 b. 4. Drop load from bus 2HULBERT (300975) 69.0 kV bus b. 5. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 c. 2. Reclose branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 c. 3. Reclose branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 d. 2. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 d. 3. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_301345_2CDRCRST-513062_TAHLWESTKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 b. 2. Drop load from bus 2LOWERY (300960) 69.0 kV bus b. 3. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 b. 4. Drop load from bus 2SLEEPYH (300968) 69.0 kV bus b. 5. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 c. 2. Reclose branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 c. 3. Reclose branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 d. 2. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 d. 3. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512655_TAHLQH-515956_7CLANS_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512655_TAHLQH-513044_BRIGSKM_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300949_7JASPER-300045_7MORGAN_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_300949_7JASPER-300794_5LAMAR_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 b. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 c. 2. Reclose branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 d. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532797_WOLFCRK7-532794_ROSEHIL7_Ckt1 | 3 Phase fault on WOLFCRK7 (532797) 345.0 kV a. Apply fault on WOLFCRK7 (532797) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509755_WEKIWA-7-514803_SOONER_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_510406_NES-7-510380_DELWARE7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512694_CLEVLND7-560056_G15-066T_Ckt1 | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512694_CLEVLND7-300138_4CLEVLND_3Winding | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CLEVLND1 (512817) to trip transformer at CLEVLND1 13.8 kV bus b. 2. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509895_TNO2-4-509817_TNO--4_Ckt1 | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509895_TNO2-4-509852_TNO--7_3Winding | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt1 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513591_HERRON-513596_IGLOOV_3Winding | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 b. 2. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt2 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512671_HUNT-512656_GRDA1_3Winding | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 b. 3. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 4. Drop load from bus HUNT (512671) 69.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_512671_HUNT-512810_PRYORC12_Ckt1 | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 b. 2. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 3. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 b. 4. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 5. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 c. 2. Reclose branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 c. 3. Reclose branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 d. 2. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 d. 3. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_506934_FLINTCR5-504201_GENTRY_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509817_TNO--4-509842_CDC-WT_Ckt1 | 3 Phase fault on T.NO.--4 (509817) 138.0 kV a. Apply fault on T.NO.--4 (509817) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512648_MAID | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a. Apply single-phase fault on MAID (512648) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 b. 2. Trip branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 3. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 4. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 5. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 6. Trip branch from NWMAID5 (512757) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 7. Drop load from bus WMAIN (512742) 161.0 kV bus b. 8. Trip branch from WMAIN (512742) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-300740_7SPORTSMAN | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345.0 kV bus a. Apply single-phase fault on 7SPORTSMAN (300740) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 5SPORTSMAN (300741) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-513596_IGLOOV | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a. Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Disconnect IGLOTER1 (513592) 13.2 kV bus to trip transformer at IGLOTER1 1 13.200 (513592) 13.2 kV bus b. 3. Trip branch from IGLOOV1 (513593) 161.0 kV bus to HERRON (513591) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512635_KERR | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 b. 4. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512638_CATSAGR5 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 kV bus to 5ELMCRK (300993) 161.0 kV bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 kV bus to COLINS (512627) 161.0 kV bus CKT 1 b. 5. Trip branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512626_MAID | Single Phase Fault with Stuck Breaker on MAID (512626) 69.0 kV bus a. Apply single-phase fault on MAID (512626) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 kV bus to AMERCAST (512681) 69.0 kV bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 kV bus to CPPTAP (512661) 69.0 kV bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 kV bus to PRYORCHEM2 (512699) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 kV bus to AIRPROD2 (512687) 69.0 kV bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 kV bus to HUNT (512671) 69.0 kV bus CKT 1 b. 9. Disconnect MAITER1 (512836) 13.2 kV bus to trip transformer at MAITER1 1 13.200 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512700_WAGNOR | Single Phase Fault with Stuck Breaker on WAGNOR (512700) 161.0 kV bus a. Apply single-phase fault on WAGNOR (512700) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR1 (512818) 13.8 kV bus to trip transformer at WAGNOR1 13.8 kV bus b. 2. Trip branch from WAGNOR (512700) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-301344_5CDRCRST | Single Phase Fault with Stuck Breaker on 5CDRCRST (301344) 161.0 kV bus a. Apply single-phase fault on 5CDRCRST (301344) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to LOCSTGVKM (513050) 161.0 kV bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 4. Trip branch from 5CDRCRST (301344) 161.0 kV bus to 2CDRCRST (301345) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-300739_7BLACKBERRY | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345.0 kV bus a. Apply single-phase fault on 7BLACKBERRY (300739) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-300741_5SPORTSMAN | Single Phase Fault with Stuck Breaker on 5SPORTSMAN (300741) 161.0 kV bus a. Apply single-phase fault on 5SPORTSMAN (300741) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 b. 2. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 7SPORTSMAN (300740) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512654_PENSA | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a. Apply single-phase fault on PENSA (512654) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 3. Disconnect PENSA (512841) 13.8 kV bus to trip transformer at PENSA 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509790_CATOOSA4 | Single Phase Fault with Stuck Breaker on CATOOSA4 (509790) 138.0 kV bus a. Apply single-phase fault on CATOOSA4 (509790) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 b. 2. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512651_CLARMR | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CLARMR4 (512813) 13.8 kV bus to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 kV bus to OOLOGAHKM (513124) 138.0 kV bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 kV bus to N.E.S.-4 (510396) 138.0 kV bus CKT 1 b. 5. Disconnect CLARMR2 (512815) 13.8 kV bus to trip transformer at CLARMR2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512655_TAHLQH | Single Phase Fault with Stuck Breaker on TAHLQH (512655) 161.0 kV bus a. Apply single-phase fault on TAHLQH (512655) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 kV bus to 7CLANS (515956) 161.0 kV bus CKT 1 b. 3. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-532797_WOLFCRK7 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a. Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 b. 2. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-512671_HUNT | Single Phase Fault with Stuck Breaker on HUNT (512671) 69.0 kV bus a. Apply single-phase fault on HUNT (512671) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 kV bus to MAIDTP2 (512625) 69.0 kV bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 kV bus to GRDA1 (512727) 69.0 kV bus CKT 1 b. 3. Disconnect GRDA1 (512816) 13.8 kV bus to trip transformer at GRDA1 1 13.8 kV bus b. 4. Trip branch from HUNT (512671) 69.0 kV bus to PRY0RC22 (512639) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 6. Trip branch from PRY0RC22 (512639) 69.0 kV bus to PRYORC32 (512622) 69.0 kV bus CKT 1 b. 7. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 8. Trip branch from PRYORC32 (512622) 69.0 kV bus to PRYORC12 (512810) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509817_TNO--4 | Single Phase Fault with Stuck Breaker on T.NO.--4 (509817) 138.0 kV bus a. Apply single-phase fault on T.NO.--4 (509817) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-755000_WWDBORDT_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515375_WWRDEHV7-515376_WWRDEHV4_3Winding | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV31 (515795) to trip transformer at WWDEHV31 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt2 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt1 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515852_DGRASSE7-515853_DGRASSE4_3Winding | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt2 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt1 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_755000_WWDBORDT-525832_TUCO_INT_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_755000_WWDBORDT-511553_CHISHOLM7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515376_WWRDEHV4-515533_REDCLFT4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 c. 2. Reclose branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 d. 2. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515376_WWRDEHV4-515375_WWRDEHV7_3Winding | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV21 (515799) to trip transformer at WWDEHV21 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515376_WWRDEHV4-514785_WOODWRD4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 b. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 c. 2. Reclose branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 d. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511553_CHISHOLM7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511553_CHISHOLM7-511557_CHISHOLM6_3Winding | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515853_DGRASSE4-520436_ROSEVLY4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515853_DGRASSE4-514795_KNOBHIL4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515853_DGRASSE4-515852_DGRASSE7_3Winding | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515853_DGRASSE4-520999_MOORLND4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_560078_G16-037-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511557_CHISHOLM6-511541_SWEETWT6_Ckt1 | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511557_CHISHOLM6-511458_ELKCTY-4_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 b. 2. Disconnect bus at ELKC2-1 (511482) to trip transformer at ELKC2-1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511557_CHISHOLM6-511553_CHISHOLM7_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515375_WWRDEHV7 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345.0 kV bus a. Apply single-phase fault on WWRDEHV7 (515375) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515407_TATONGA7 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345.0 kV bus a. Apply single-phase fault on TATONGA7 (515407) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515852_DGRASSE7 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345.0 kV bus a. Apply single-phase fault on DGRASSE7 (515852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-560071_G16-003-TAP | Single Phase Fault with Stuck Breaker on G16-003-TAP (560071) 345.0 kV bus a. Apply single-phase fault on G16-003-TAP (560071) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 b. 2. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-755000_WWDBORDT | Single Phase Fault with Stuck Breaker on WWDBORDT (755000) 345.0 kV bus a. Apply single-phase fault on WWDBORDT (755000) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515376_WWRDEHV4 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138.0 kV bus a. Apply single-phase fault on WWRDEHV4 (515376) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 kV bus to IODINE-4 (514796) 138.0 kV bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 kV bus to REDCLFT4 (515533) 138.0 kV bus CKT 1 b. 4. Disconnect WWDEHV31 (515795) 13.8 kV bus to trip transformer at WWDEHV31 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-511553_CHISHOLM7 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345.0 kV bus a. Apply single-phase fault on CHISHOLM7 (511553) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 b. 2. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515497_MATHWSN7 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345.0 kV bus a. Apply single-phase fault on MATHWSN7 (515497) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-539801_THISTLE7 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345.0 kV bus a. Apply single-phase fault on THISTLE7 (539801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515677_BADGER | Single Phase Fault with Stuck Breaker on BADGER (515677) 345.0 kV bus a. Apply single-phase fault on BADGER (515677) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511541_SWEETWT6-511557_CHISHOLM6_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2019-013 (763541) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511541_SWEETWT6-523777_WHEELER_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523777_WHEELER-523771_GRAPEVINE_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523777_WHEELER-511541_SWEETWT6_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523777_WHEELER-523776_WHEELER_3Winding | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WHEELER_TR1113.200 (523774) to trip transformer at WHEELER_TR1113.200 (523774) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_511553_CHISHOLM7-755000_WWDBORDT_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_755000_WWDBORDT-515375_WWRDEHV7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514795_KNOBHIL4-514794_KNOBHIL2_3Winding | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt2 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt1 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520436_ROSEVLY4-520430_NOELSW_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520436_ROSEVLY4-520601_AVARD_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AVARD (520601) 138.0 kV bus b. 2. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-520848_CDRDLTP4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 c. 2. Reclose branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 d. 2. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-514778_CLEOCOR4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 b. 2. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 3. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 4. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 c. 2. Reclose branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 d. 2. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-515785_WINDFRM4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-520553_SEILING4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SEILING4 (520553) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-520462_ASPEN_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus ASPEN (520462) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-521197_CRTSJCT2_3Winding | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MLNDTERT (521180) to trip transformer at MLNDTERT 2.4000 (521180) 2.4000000953674316 kV bus b. 2. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520999_MOORLND4-520957_IODINE_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus IODINE (520957) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_539801_THISTLE7-539638_FLATRDG4_3Winding | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at THISTLE (539802) to trip transformer at THISTLE T1 13.8 kV bus b. 2. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_520430_NOELSW-521200_DRIFTWD4_Ckt1 | 3 Phase fault on NOELSW (520430) 138.0 kV a. Apply fault on NOELSW (520430) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 2. Reclose branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 3. Reclose branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 2. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514794_KNOBHIL2-514795_KNOBHIL4_3Winding | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514794_KNOBHIL2-514792_ALVAOGE2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_514794_KNOBHIL2-515371_HELENAT2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 b. 2. Drop load from bus CZYCRVT2 (515560) 69.0 kV bus b. 3. Drop fixed shunt from bus CZYCRVT2 (515560) 69.0 kV bus b. 4. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 b. 5. Drop load from bus SALINE (514716) 69.0 kV bus b. 6. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 c. 2. Reclose branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 c. 3. Reclose branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 d. 2. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 d. 3. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt1 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt2 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_521200_DRIFTWD4-520430_NOELSW_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 2. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 4. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 5. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 6. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 2. Reclose branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 3. Reclose branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 2. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 3. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_521200_DRIFTWD4-520432_BYRONTP4_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_521200_DRIFTWD4-521201_DRIFTWD2_3Winding | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DRFTWDTERT (521185) to trip transformer at DRFTWDTERT 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-515853_DGRASSE4 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138.0 kV bus a. Apply single-phase fault on DGRASSE4 (515853) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-514795_KNOBHIL4 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138.0 kV bus a. Apply single-phase fault on KNOBHIL4 (514795) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Disconnect KNOBHIL1 (515732) 13.2 kV bus to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-520436_ROSEVLY4 | Single Phase Fault with Stuck Breaker on ROSEVLY4 (520436) 138.0 kV bus a. Apply single-phase fault on ROSEVLY4 (520436) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-520999_MOORLND4 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138.0 kV bus a. Apply single-phase fault on MOORLND4 (520999) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 kV bus to CDRDLTP4 (520848) 138.0 kV bus CKT 1 b. 4. Trip branch from MOORLND4 (520999) 138.0 kV bus to GLASMTN4 (514788) 138.0 kV bus CKT 1 b. 5. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 6. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 7. Trip branch from GLASMTN4 (514788) 138.0 kV bus to CLEOCOR4 (514778) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-520430_NOELSW | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a. Apply single-phase fault on NOELSW (520430) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 kV bus to DRIFTWD4 (521200) 138.0 kV bus CKT 1 b. 7. Trip branch from NOELSW (520430) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-532782_BUFFALO7 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345.0 kV bus a. Apply single-phase fault on BUFFALO7 (532782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_763010_G19-065-TAP-509076_NWHENDR4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 2. Drop load from bus LONDON (509072) 138.0 kV bus b. 3. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 6. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 7. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 2. Reclose branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 4. Reclose branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 2. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 4. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_763010_G19-065-TAP-509080_OVERTON4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509080_OVERTON4-508548_KNOXLEE4_Ckt1 | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 2. Reclose branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 4. Reclose branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 2. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 4. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509080_OVERTON4-509079_OVERTON2_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509080_OVERTON4-509241_CROCKET7_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 3. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 4. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 5. Drop load from bus ALTO (509320) 138.0 kV bus b. 6. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 7. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 8. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 9. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 10. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 11. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 b. 12. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 13. Drop switching device from bus OVERTON4 (509080) 138.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 2. Reclose branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 3. Reclose branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 5. Reclose branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 6. Reclose branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 3. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 5. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 6. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509241_CROCKET7-508585_TENRUSK7_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509241_CROCKET7-334028_7GRIMES%_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509241_CROCKET7-509080_OVERTON4_3Winding | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 2. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 3. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 4. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 5. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 6. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 7. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 8. Drop load from bus ALTO (509320) 138.0 kV bus b. 9. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 10. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 11. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 12. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 2. Reclose branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 3. Reclose branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 5. Reclose branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 6. Reclose branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 2. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 3. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 5. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 6. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509079_OVERTON2-508546_KILGORE2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509079_OVERTON2-509080_OVERTON4_3Winding | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509079_OVERTON2-509089_TURNERT2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus TURNERT2 (509089) 69.0 kV bus b. 2. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509076_NWHENDR4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 c. 2. Reclose branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 d. 2. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509080_OVERTON4 | Single Phase Fault with Stuck Breaker on OVERTON4 (509080) 138.0 kV bus a. Apply single-phase fault on OVERTON4 (509080) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 kV bus to LEVERET4 (509069) 138.0 kV bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 kV bus to KILGORR4 (509067) 138.0 kV bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 kV bus to MONROER4 (509073) 138.0 kV bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 kV bus to KNOXLEE4 (508548) 138.0 kV bus CKT 1 b. 8. Trip branch from OVERTON4 (509080) 138.0 kV bus to G19-065-TAP (763010) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509076_NWHENDR4-509075_NWHENDR2_3Winding | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509076_NWHENDR4-763010_G19-065-TAP_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 2. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 3. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 6. Drop load from bus LONDON (509072) 138.0 kV bus b. 7. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 2. Reclose branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 4. Reclose branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 2. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 4. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-508562_PIRKEY_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 c. 2. Reclose branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. 3. Reclose branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 d. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. 3. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-509059_CHEROKE4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CHEROKE4 (509059) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-509080_OVERTON4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 2. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 3. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 6. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 7. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 2. Reclose branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 4. Reclose branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 2. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 4. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-508544_HARRISN4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-508570_SOTXEST4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SOTXEST4 (508570) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508548_KNOXLEE4-508568_SELONGV2_3Winding | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KXLEE-1 (508584) to trip transformer at KXLEE-1 12.470 (508584) 12.470000267028809 kV bus b. 2. Drop load from bus KNOXLEE2 (508547) 69.0 kV bus b. 3. Drop switching device from bus KNOXLEE2 (508547) 69.0 kV bus b. 4. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_334028_7GRIMES%-334026_4GRIMES%_3Winding | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_334028_7GRIMES%-334027_6GRIMES!_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_334028_7GRIMES%-334197_7ROCKYCRK%_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508585_TENRUSK7-508572_LEBROCK7_Ckt1 | 3 Phase fault on TENRUSK7 (508585) 345.0 kV a. Apply fault on TENRUSK7 (508585) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508546_KILGORE2-508573_SPIPETP2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 b. 2. Drop load from bus HOWELL (508545) 69.0 kV bus b. 3. Drop switching device from bus HOWELL (508545) 69.0 kV bus b. 4. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 b. 5. Drop load from bus SABINE (508565) 69.0 kV bus b. 6. Drop switching device from bus SABINE (508565) 69.0 kV bus b. 7. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 c. 2. Reclose branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 c. 3. Reclose branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 d. 2. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 d. 3. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508546_KILGORE2-508574_WHITNEY2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 b. 2. Drop load from bus MONROCR2 (508558) 69.0 kV bus b. 3. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 c. 2. Reclose branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 d. 2. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509075_NWHENDR2-509081_POYNTER2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509075_NWHENDR2-509076_NWHENDR4_3Winding | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_509075_NWHENDR2-509061_EVENSID2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_334026_4GRIMES%-334028_7GRIMES%_3Winding | 3 Phase fault on 4GRIMES% (334026) 138.0 kV a. Apply fault on 4GRIMES% (334026) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt2 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt1 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509241_CROCKET7 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509079_OVERTON2 | Single Phase Fault with Stuck Breaker on OVERTON2 (509079) 69.0 kV bus a. Apply single-phase fault on OVERTON2 (509079) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 b. 2. Disconnect OVTON2-1 (509098) 13.2 kV bus to trip transformer at OVTON2-1 13.200 (509098) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-509076_NWHENDR4 | Single Phase Fault with Stuck Breaker on NWHENDR4 (509076) 138.0 kV bus a. Apply single-phase fault on NWHENDR4 (509076) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 kV bus to OAK1HIL4 (509077) 138.0 kV bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 kV bus to OAK2HIL4 (509078) 138.0 kV bus CKT 1 b. 5. Disconnect NWHEN1-1 (509095) 13.2 kV bus to trip transformer at NWHEN1-1 13.200 (509095) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508548_KNOXLEE4 | Single Phase Fault with Stuck Breaker on KNOXLEE4 (508548) 138.0 kV bus a. Apply single-phase fault on KNOXLEE4 (508548) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to BRANDYBR (508596) 138.0 kV bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 b. 5. Drop load from bus KNOXL5-1 (509398) 22.0 kV bus b. 6. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to KNOXL5-1 (509398) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-334028_7GRIMES% | Single Phase Fault with Stuck Breaker on 7GRIMES% (334028) 345.0 kV bus a. Apply single-phase fault on 7GRIMES% (334028) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508585_TENRUSK7 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip branch from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-508586_TENGEN | Single Phase Fault with Stuck Breaker on TENGEN (508586) 345.0 kV bus a. Apply single-phase fault on TENGEN (508586) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506745) 18.0 kV bus CKT 1 b. 2. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506746) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-334026_4GRIMES% | Single Phase Fault with Stuck Breaker on 4GRIMES% (334026) 138.0 kV bus a. Apply single-phase fault on 4GRIMES% (334026) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus b. 2. Disconnect 1GRIMES_2 (334018) 13.8 kV bus to trip transformer at 1GRIMES_2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-300997_5KETONVL-ConID-109484 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-300997_5KETONVL-ConID-109485 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-500250_DOLHILL7-ConID-80023 | Single Phase Fault with Stuck Breaker on DOLHILL7 (500250) 345.0 kV bus a. Apply single-phase fault on DOLHILL7 (500250) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DOLHILL7 (500250) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84210 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84211 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84212 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84213 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506935_FLINTCR7-ConID-84214 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84207 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84208 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506945_CHAMSPR7-ConID-84209 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-506979_SHIPERD7-ConID-84215 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345.0 kV bus a. Apply single-phase fault on SHIPERD7 (506979) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from SHIPERD7 (506979) 345.0 kV bus to SHIPERD5 (506980) 161.0 kV bus to SHIPERD1 (506981) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507455_TURK-ConID-84200 | Single Phase Fault with Stuck Breaker on TURK (507455) 345.0 kV bus a. Apply single-phase fault on TURK (507455) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from TURK (507454) 138.0 kV bus to TURK (507455) 345.0 kV bus to TURK (507457) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507760_SW-ConID-84164 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507760_SW-ConID-84165 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507760_SW-ConID-84166 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507760_SW-ConID-84167 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-507760_SW-ConID-84168 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84194 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84197 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84198 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508072_NWTXARK7-ConID-84199 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84187 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84189 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84195 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84196 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-84206 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 4. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508298_LYDIA-ConID-91933 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508359_WELSH-ConID-84181 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508359_WELSH-ConID-84184 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508359_WELSH-ConID-84190 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84154 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84155 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84156 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84157 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84159 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84160 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84161 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84162 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508563_PIRKEY-ConID-84163 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508572_LEBROCK7-ConID-84153 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508572_LEBROCK7-ConID-84158 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84150 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 b. 3. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84151 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508585_TENRUSK7-ConID-84152 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84169 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84170 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84171 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508809_LONGWD-ConID-84172 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84173 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84174 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84175 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84176 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84177 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84178 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508832_DIANA-ConID-84179 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508841_WILKES-ConID-84180 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-508841_WILKES-ConID-84182 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509241_CROCKET7-ConID-84148 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509241_CROCKET7-ConID-84149 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84185 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84186 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509404_WELSH1-1-ConID-84191 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509406_WELSH3-1-ConID-84188 | Single Phase Fault with Stuck Breaker on WELSH3-1 (509406) 18.0 kV bus a. Apply single-phase fault on WELSH3-1 (509406) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509409_WILKE3-1-ConID-84183 | Single Phase Fault with Stuck Breaker on WILKE3-1 (509409) 22.0 kV bus a. Apply single-phase fault on WILKE3-1 (509409) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84239 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84240 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509755_WEKIWA-7-ConID-84241 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509782_RSS-7-ConID-84233 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip transformer from RSS (509773) 138.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus to RSST1 (509882) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509782_RSS-7-ConID-84234 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to COGENT (509834) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84248 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84249 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84256 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84257 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84258 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84259 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84260 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84262 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84263 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 b. 2. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84265 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509807_ONETA--7-ConID-84266 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84242 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84243 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509852_TNO--7-ConID-84244 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip line from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509870_SAPLPRD7-ConID-84236 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from SAPLPRD7 (509870) 345.0 kV bus to SAPLPRD4 (509871) 138.0 kV bus to SAPLPRD1 (509872) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509870_SAPLPRD7-ConID-84237 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509874_ONETA5-1-ConID-84264 | Single Phase Fault with Stuck Breaker on ONETA5-1 (509874) 34.5 kV bus a. Apply single-phase fault on ONETA5-1 (509874) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-509881_ONETA1-1-ConID-84261 | Single Phase Fault with Stuck Breaker on ONETA1-1 (509881) 13.8 kV bus a. Apply single-phase fault on ONETA1-1 (509881) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510370_DELAWAR1-ConID-8425301 | Single Phase Fault with Stuck Breaker on DELAWAR1 (510370) 13.8 kV bus a. Apply single-phase fault on DELAWAR1 (510370) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84253 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-842530 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84254 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-842540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510380_DELWARE7-ConID-84255 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510406_NES-7-ConID-84250 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510406_NES-7-ConID-84251 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510406_NES-7-ConID-84252 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84223 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84224 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84225 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84226 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510907_PITTSB-7-ConID-84227 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84201 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84202 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-84203 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-510911_VALIANT7-ConID-91932 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511411_LES#5-1-ConID-8422101 | Single Phase Fault with Stuck Breaker on LES#5-1 (511411) 13.8 kV bus a. Apply single-phase fault on LES#5-1 (511411) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511456_OKU-7-ConID-84217 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511467_LES-4-ConID-9193401 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-84218 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-842180 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-84221 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-842210 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-84222 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-842720 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-842730 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-91934 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-919340 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-91937 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-919370 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511468_LES-7-ConID-9193701 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84272 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-8427201 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84273 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-8427301 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511568_TERRYRD7-ConID-84274 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-511840_NES3-1-ConID-84247 | Single Phase Fault with Stuck Breaker on NES3-1 (511840) 22.0 kV bus a. Apply single-phase fault on NES3-1 (511840) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512635_KERR-ConID-109452 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512635_KERR-ConID-109453 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512635_KERR-ConID-109454 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512771) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512638_CATSAGR5-ConID-109479 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Trip transformer from CATOOSA4 (509790) 138.0 kV bus to CATSAGR5 (512638) 161.0 kV bus to CATTER2 (512834) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512651_CLARMR-ConID-109481 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512651_CLARMR-ConID-109482 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109486 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR (512700) 161.0 kV bus b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109487 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA2 (512826) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512656_GRDA1-ConID-109488 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512686_SALINA-ConID-109461 | Single Phase Fault with Stuck Breaker on SALINA (512686) 161.0 kV bus a. Apply single-phase fault on SALINA (512686) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SALINA (512686) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512707_CLARMR-ConID-109480 | Single Phase Fault with Stuck Breaker on CLARMR (512707) 138.0 kV bus a. Apply single-phase fault on CLARMR (512707) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR2 (512815) 13.8 kV bus CKT 2 b. 2. Disconnect CLARMR (512707) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-512714_KANSATP5-ConID-109462 | Single Phase Fault with Stuck Breaker on KANSATP5 (512714) 161.0 kV bus a. Apply single-phase fault on KANSATP5 (512714) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SILSPWW5 (512642) 161.0 kV bus b. 2. Disconnect KANSATP5 (512714) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118718 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118719 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from JOHNCO (514808) 138.0 kV bus to JOHNCO (514809) 345.0 kV bus to JOHNCO11 (514810) 13.8 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-514808_JOHNCO-ConID-118720 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515136_SUNNYSD7-ConID-118867 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515136_SUNNYSD7-ConID-1188670 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515405_SUNYSD-ConID-11886701 | Single Phase Fault with Stuck Breaker on SUNYSD (515405) 13.8 kV bus a. Apply single-phase fault on SUNYSD (515405) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from G17-075-TAP (560088) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-118540 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BALKOW (515618) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-80821 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to PALDR2W7 (515590) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515802_GRACMNT4-ConID-118667 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 2. Trip line from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-532777_G17-009-TAP-ConID-8425401 | Single Phase Fault with Stuck Breaker on G17-009-TAP (532777) 345.0 kV bus a. Apply single-phase fault on G17-009-TAP (532777) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-587744_G16-091-TAP-ConID-8421801 | Single Phase Fault with Stuck Breaker on G16-091-TAP (587744) 345.0 kV bus a. Apply single-phase fault on G16-091-TAP (587744) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-507760_SW-ConID-AEPW-10 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a.Apply single-phase fault on SW (507760) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 3. Clear fault from SW (507760) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508359_WELSH-ConID-AEPW-3 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508359_WELSH-ConID-AEPW-4 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-4 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) b. 3. Drop generator from LEBROCG1 (506752 ID 1) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-5 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-8 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-9 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508832_DIANA-ConID-AEPW-6 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508832_DIANA-ConID-AEPW-7 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-508841_WILKES-ConID-AEPW-5 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a.Apply single-phase fault on WILKES (508841) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Clear fault from WILKES (508841) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-509807_ONETA--7-ConID-AEPW-82 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a.Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from ONETA--7 (509807) 345.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from ONETA--7 (509807) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 3. Clear fault from ONETA--7 (509807) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512635_KERR-ConID-GRDA-68 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512635_KERR-ConID-GRDA-69 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 b. 4. Disconnect SALNCRK5 (512805) 161.0 kV bus b. 5. Disconnect SALINA (512686) 161.0 kV bus b. 6. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 10. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 11. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 16. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 17. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 22. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 23. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-58 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-59 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-60 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-61 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER2 (512837) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-62 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-63 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-64 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-65 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512648_MAID-ConID-GRDA-66 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-46 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-47 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-48 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-49 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA17-1 (512688) 22.799999237060547 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-71 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-72 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-73 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512654_PENSA-ConID-GRDA-74 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Drop generator from PENSA_U4 (512605 ID 4) 13.2 kV bus b. 4. Drop generator from PENSA_U5 (512607 ID 5) 13.2 kV bus b. 5. Drop generator from PENSA_U6 (512606 ID 6) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-53 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Disconnect WAGNOR (512700) 161.0 kV bus b. 4. Disconnect WAGNOR1 (512818) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-54 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Open branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512669_KETCHUM5-ConID-GRDA-70 | Single Phase Fault with Stuck Breaker on KETCHUM5 (512669) 161.0 kV bus a.Apply single-phase fault on KETCHUM5 (512669) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Disconnect AFTON (512632) 161.0 kV bus b. 2. Clear fault from KETCHUM5 (512669) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 4. Drop load from KETCHUM5 (512669 ID 1) 161.0 kV bus b. 5. Disconnect KETCHUM5 (512669) 161.0 kV bus b. 6. Disconnect AFTON1 (512845) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-55 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-56 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-57 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-77 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-78 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Disconnect TONECE1 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512751_TONECE5-ConID-GRDA-76 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512805_SALNCRK5-ConID-GRDA-75 | Single Phase Fault with Stuck Breaker on SALNCRK5 (512805) 161.0 kV bus a.Apply single-phase fault on SALNCRK5 (512805) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from SALNCRK5 (512805) b. 3. Disconnect SALINA (512686) 161.0 kV bus b. 4. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 5. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 6. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 10. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 11. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 16. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 17. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512865_GREC-ConID-GRDA-50 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECSTG_1 (512615) 21.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-512865_GREC-ConID-GRDA-51 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECCTG_1 (512614) 20.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-513596_IGLOOV-ConID-GRDA-52 | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a.Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from IGLOOV (513596) b. 3. Disconnect IGLOTER1 (513592) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-514803_SOONER-ConID-OKGE-29 | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a.Apply single-phase fault on SOONER (514803) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SOONER (515760) 13.8 kV bus b. 2. Open branch from G15-066T (560056) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 b. 3. Clear fault from SOONER (514803) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-514809_JOHNCO-ConID-OKGE-21 | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a.Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Open branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 3. Clear fault from JOHNCO (514809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515045_SEMINOL7-ConID-OKGE-28 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a.Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Disconnect SEMINO21 (515757) 14.399999618530273 kV bus b. 3. Clear fault from SEMINOL7 (515045) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515136_SUNNYSD7-ConID-OKGE-18 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a.Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SUNYSD (515405) 13.8 kV bus b. 2. Open branch from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 b. 3. Clear fault from SUNNYSD7 (515136) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515339_VBI-ConID-OKGE-32 | Single Phase Fault with Stuck Breaker on VBI (515339) 161.0 kV bus a.Apply single-phase fault on VBI (515339) 161.0 kV bus b.Run for 23.52 cycles and trip the following elements: b. 1. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 2. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 3. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 4. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 5. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 11.28 cycles and trip the following elements: b. 6. Close branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 7. Close branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 8. Close branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 9. Close branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 10. Close branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 1.62 cycles and trip the following elements: b. 11. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 9.18 cycles and trip the following elements: b. 12. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 4.02 cycles and trip the following elements: b. 13. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 4.2 cycles and trip the following elements: b. 14. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 2.4 cycles and trip the following elements: b. 15. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 0.18 cycles and trip the following elements: b. 16. Close branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 2.82 cycles and trip the following elements: b. 17. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 6.36 cycles and trip the following elements: b. 18. Close branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 1.44 cycles and trip the following elements: b. 19. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 19.38 cycles and trip the following elements: b. 20. Disconnect VBI (515769) 13.8 kV bus b.Run for 23.82 cycles and trip the following elements: b. 21. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 18.36 cycles and trip the following elements: b. 22. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b. 23. Clear fault from VBI (515339) b. 24. Drop load from HWY59 (504191 ID A1) 161.0 kV bus b. 25. Drop load from GRANDPR5 (504192 ID A1) 161.0 kV bus b. 26. Drop load from SIMMONS5 (515332 ID 1) 161.0 kV bus b. 27. Drop load from SIMMONS5 (515332 ID A1) 161.0 kV bus b. 28. Drop load from DYER (515333 ID A1) 161.0 kV bus b. 29. Drop load from ALMA (515334 ID 1) 161.0 kV bus b. 30. Drop load from RUDY (515337 ID A1) 161.0 kV bus b. 31. Drop load from OAKGROV5 (515340 ID A1) 161.0 kV bus b. 32. Drop load from WHITESD5 (515341 ID 1) 161.0 kV bus b. 33. Drop load from PUDDIN (515346 ID A1) 161.0 kV bus b. 34. Drop load from NITROUS5 (515350 ID 1) 161.0 kV bus b. 35. Drop load from GERBER (515351 ID 1) 161.0 kV bus b. 36. Drop load from TWNBRDG5 (515360 ID 1) 161.0 kV bus b. 37. Drop load from ADABELL5 (515406 ID 1) 161.0 kV bus b. 38. Disconnect HWY59 (504191) 161.0 kV bus b. 39. Disconnect GRANDPR5 (504192) 161.0 kV bus b. 40. Disconnect GERBRTP5 (515326) 161.0 kV bus b. 41. Disconnect NITROTP5 (515329) 161.0 kV bus b. 42. Disconnect SIMMONS5 (515332) 161.0 kV bus b. 43. Disconnect DYER (515333) 161.0 kV bus b. 44. Disconnect ALMA (515334) 161.0 kV bus b. 45. Disconnect RUDY (515337) 161.0 kV bus b. 46. Disconnect OAKGROV5 (515340) 161.0 kV bus b. 47. Disconnect WHITESD5 (515341) 161.0 kV bus b. 48. Disconnect PUDDIN (515346) 161.0 kV bus b. 49. Disconnect NALCOTP5 (515348) 161.0 kV bus b. 50. Disconnect NITROUS5 (515350) 161.0 kV bus b. 51. Disconnect GERBER (515351) 161.0 kV bus b. 52. Disconnect TWNBRDG5 (515360) 161.0 kV bus b. 53. Disconnect ADABELL5 (515406) 161.0 kV bus b. 54. Disconnect GRNDPRT5 (515524) 161.0 kV bus b. 55. Disconnect HWY59TP5 (515527) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515554_BVRCNTY7-ConID-OKGE-16 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a.Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 3. Clear fault from BVRCNTY7 (515554) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515576_RANCHRD7-ConID-OKGE-25 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345.0 kV bus a.Apply single-phase fault on RANCHRD7 (515576) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from SOONER (514803) 345.0 kV bus to RANCHRD7 (515576) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to FRNTWND7 (515688) 345.0 kV bus CKT 1 b. 3. Clear fault from RANCHRD7 (515576) b. 4. Drop generator from FRNTWDG1 (515691 ID 1) 0.65 kV bus b. 5. Drop load from FRNTWD11 (515689 ID S1) 34.5 kV bus b. 6. Disconnect FRNTWND7 (515688) 345.0 kV bus b. 7. Disconnect FRNTWD11 (515689) 34.5 kV bus b. 8. Disconnect FRNTWDC1 (515690) 34.5 kV bus b. 9. Disconnect FRNTWDG1 (515691) 0.65 kV bus b. 10. Disconnect FRNTWDT1 (515692) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515621_OPENSKY7-ConID-OKGE-23 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345.0 kV bus a.Apply single-phase fault on OPENSKY7 (515621) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 b. 3. Clear fault from OPENSKY7 (515621) b. 4. Drop generator from KAYWNDG1 (515651 ID 1) 0.69 kV bus b. 5. Drop generator from KAYWNDG2 (515652 ID 1) 0.69 kV bus b. 6. Drop load from KAYWND11 (515622 ID S1) 34.5 kV bus b. 7. Drop load from KAYWND12 (515623 ID S1) 34.5 kV bus b. 8. Disconnect KAYWIND7 (514825) 345.0 kV bus b. 9. Disconnect KAYWNDT1 (515619) 12.5 kV bus b. 10. Disconnect KAYWNDT2 (515620) 12.5 kV bus b. 11. Disconnect OPENSKY7 (515621) 345.0 kV bus b. 12. Disconnect KAYWND11 (515622) 34.5 kV bus b. 13. Disconnect KAYWND12 (515623) 34.5 kV bus b. 14. Disconnect KAYWNDG1 (515651) 0.69 kV bus b. 15. Disconnect KAYWNDG2 (515652) 0.69 kV bus b. 16. Disconnect KAYWNDC1 (515653) 34.5 kV bus b. 17. Disconnect KAYWNDC2 (515654) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515785_WINDFRM4-ConID-OKGE-17 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138.0 kV bus a.Apply single-phase fault on WINDFRM4 (515785) 138.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WINDFRM4 (515785) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 b. 2. Open branch from WOODWRD4 (514785) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 b. 3. Clear fault from WINDFRM4 (515785) b. 4. Drop generator from FPLWNDG1 (515895 ID 1) 0.69 kV bus b. 5. Drop load from FPLWND11 (515787 ID S1) 34.5 kV bus b. 6. Disconnect WINDFRM4 (515785) 138.0 kV bus b. 7. Disconnect FPLWIND4 (515786) 138.0 kV bus b. 8. Disconnect FPLWND11 (515787) 34.5 kV bus b. 9. Disconnect FLPWND21 (515790) 13.8 kV bus b. 10. Disconnect FPLWNDG1 (515895) 0.69 kV bus b. 11. Disconnect FPLWNDC1 (515896) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515800_GRACMNT7-ConID-OKGE-22 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a.Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from LES (587744) None kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Open branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 3. Clear fault from GRACMNT7 (515800) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-520430_NOELSW-ConID-WFEC-59 | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a.Apply single-phase fault on NOELSW (520430) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DRIFTWD4 (521200) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 b. 3. Open branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 4. Clear fault from NOELSW (520430) b. 5. Drop load from CHRKCTY4 (520431 ID 1) 138.0 kV bus b. 6. Drop load from SALTPLN4 (520437 ID 1) 138.0 kV bus b. 7. Drop load from SALTPLN4 (520437 ID 2) 138.0 kV bus b. 8. Disconnect CHRKCTY4 (520431) 138.0 kV bus b. 9. Disconnect SALTPLN4 (520437) 138.0 kV bus b. 10. Drop load from ROSEVLY4 (520436 ID 1) 138.0 kV bus b. 11. Drop load from AVARD (520601 ID 1) 138.0 kV bus b. 12. Disconnect ROSEVLY4 (520436) 138.0 kV bus b. 13. Disconnect AVARD (520601) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-520814_ANADARK4-ConID-WFEC-51 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138.0 kV bus a.Apply single-phase fault on ANADARK4 (520814) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SUNSHIN4 (521059) 138.0 kV bus to BRIDGCR4 (520501) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 3. Open branch from ANADRK5 (520812) 13.8 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 4. Open branch from ANADARK4 (520814) 138.0 kV bus to POCASET4 (521031) 138.0 kV bus CKT 1 b. 5. Clear fault from ANADARK4 (520814) b. 6. Drop generator from ANADRK5 (520812 ID 1) 13.8 kV bus b. 7. Drop load from ANADRK5 (520812 ID F1) 13.8 kV bus b. 8. Drop load from ANADRK5 (520812 ID V1) 13.8 kV bus b. 9. Disconnect ANADRK5 (520812) 13.8 kV bus b. 10. Drop load from TUTTLE (520496 ID 1) 138.0 kV bus b. 11. Drop load from BRIDGCR4 (520501 ID 1) 138.0 kV bus b. 12. Drop load from POCASET4 (521031 ID 1) 138.0 kV bus b. 13. Disconnect TUTTLE (520496) 138.0 kV bus b. 14. Disconnect BRIDGCR4 (520501) 138.0 kV bus b. 15. Disconnect POCASET4 (521031) 138.0 kV bus b. 16. Disconnect TUTLETP4 (521072) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-520920_FTSUPLY4-ConID-WFEC-55 | Single Phase Fault with Stuck Breaker on FTSUPLY4 (520920) 138.0 kV bus a.Apply single-phase fault on FTSUPLY4 (520920) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SLEEPBR4 (520922) 138.0 kV bus to FTSUPLY4 (520920) 138.0 kV bus CKT 1 b. 2. Drop generator from SLP (521145 ID 1) 0.6000000238418579 kV bus b. 3. Disconnect SLEEPBR4 (520922) 138.0 kV bus b. 4. Disconnect SLP (521141) 34.5 kV bus b. 5. Disconnect SLP (521144) 34.5 kV bus b. 6. Disconnect SLP (521145) 0.6000000238418579 kV bus b. 7. Disconnect SLP (521151) 9.949999809265137 kV bus b.Run for 9.0 cycles and trip the following elements: b. 8. Open branch from MOORLND4 (520999) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 9. Clear fault from FTSUPLY4 (520920) b. 10. Open branch from FTSUPLY4 (520920) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 11. Drop load from IODINE (520957 ID 1) 138.0 kV bus b. 12. Disconnect IODINE (520957) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-521016_OKEENE-ConID-WFEC-60 | Single Phase Fault with Stuck Breaker on OKEENE (521016) 138.0 kV bus a.Apply single-phase fault on OKEENE (521016) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DOVERSW4 (520882) 138.0 kV bus to OKEENE (521016) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 3. Clear fault from OKEENE (521016) b. 4. Drop load from PIC4 (520425 ID 1) 138.0 kV bus b. 5. Drop load from CEDRDAL4 (520507 ID 1) 138.0 kV bus b. 6. Disconnect PIC4 (520425) 138.0 kV bus b. 7. Disconnect CDRDLTP4 (520848) 138.0 kV bus b. 8. Disconnect CEDRDAL4 (520507) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-65 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from CLINTJC4 (511485) 138.0 kV bus to CLINTON4 (520856) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b. 3. Open branch from WASHITA4 (521089) 138.0 kV bus to ONEY (521017) 138.0 kV bus CKT 1 b. 4. Clear fault from WASHITA4 (521089) b. 5. Drop load from HINTON (520468 ID 1) 138.0 kV bus b. 6. Drop load from DEERCR (520503 ID 1) 138.0 kV bus b. 7. Drop load from CLINTON4 (520856 ID 1) 138.0 kV bus b. 8. Drop load from HYDRO (520950 ID 1) 138.0 kV bus b. 9. Drop load from NIJECT (521010 ID 1) 138.0 kV bus b. 10. Drop load from NIJECT (521010 ID 2) 138.0 kV bus b. 11. Drop load from ONEY (521017 ID 1) 138.0 kV bus b. 12. Drop load from SICKLES4 (521050 ID 1) 138.0 kV bus b. 13. Drop load from WEATHFD4 (521092 ID 1) 138.0 kV bus b. 14. Disconnect HINTON (520468) 138.0 kV bus b. 15. Disconnect DEERCR (520503) 138.0 kV bus b. 16. Disconnect BINGERJ4 (520827) 138.0 kV bus b. 17. Disconnect CLINTON4 (520856) 138.0 kV bus b. 18. Disconnect HYDRO (520950) 138.0 kV bus b. 19. Disconnect NIJECT (521010) 138.0 kV bus b. 20. Disconnect ONEY (521017) 138.0 kV bus b. 21. Disconnect SICKLES4 (521050) 138.0 kV bus b. 22. Disconnect WEATHFD4 (521092) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-66 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 3. Clear fault from WASHITA4 (521089) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523777_WHEELER-ConID-SPS-140 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from WHEELER (523777) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT &1 b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523777_WHEELER-ConID-SPS-143 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532791_BENTON-ConID-Evergy-105 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532791_BENTON-ConID-Evergy-106 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Disconnect ROSEH3 (532831) 13.8 kV bus b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-152 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Disconnect ROSEH3 (532831) 13.8 kV bus b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-121 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Disconnect WOLFCRK1 (532962) 17.0 kV bus b. 4. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 5. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542965_WGRDNR7-ConID-Evergy-150 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345.0 kV bus a.Apply single-phase fault on W.GRDNR7 (542965) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from W.GRDNR7 (542965) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 b. 2. Open branch from STILWEL7 (542968) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 3. Clear fault from W.GRDNR7 (542965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542968_STILWEL7-ConID-Evergy-148 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345.0 kV bus a.Apply single-phase fault on STILWEL7 (542968) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from PECULR (541198) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 3. Clear fault from STILWEL7 (542968) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-140 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-141 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-142 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-143 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542956) 24.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-547469_RIV4525-ConID-EMDE-34 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161.0 kV bus a.Apply single-phase fault on RIV4525 (547469) 161.0 kV bus b.Run for 7.0 cycles and trip the following elements: b. 1. Open branch from RIV4525 (547469) 161.0 kV bus to NEOSHO (532937) 161.0 kV bus CKT 1 b.Run for 86.0 cycles and trip the following elements: b. 4. Open branch from BAX488 (547729) 161.0 kV bus to HOC404 (547487) 161.0 kV bus CKT 1 b. 5. Clear fault from RIV4525 (547469) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523097_HITCHLAND-523823_CARPENTER_Ckt1 | 3 Phase fault on HITCHLAND (523097) 345.0 kV a. Apply fault on HITCHLAND (523097) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523323_MCDWL_CREEK623000-523309_MOORE_CNTY_Ckt1 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523323_MCDWL_CREEK623000-523322_MCDWL_CREEK311500_3Winding | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MCDWL_CRKTR113.200 (523321) to trip transformer at MCDWL_CRKTR113.200 (523321) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-523323_MCDWL_CREEK623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-523869_CHAN+TASCOS623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-523979_HARRNG_EST_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-524010_ROLLHILLS_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523959_POTTER_CO-524267_BUSHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523961_POTTER_CO-523097_HITCHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523977_HARRNG_WST-524010_ROLLHILLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523977_HARRNG_WST-524044_NICHOLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523977_HARRNG_WST-524162_EAST_PLANT_3Winding | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 b. 2. Disconnect bus at EPLANT_TR3 (524160) to trip transformer at EPLANT_TR3 113.200 (524160) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523978_HARRNG_MID-523977_HARRNG_WST_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523978_HARRNG_MID-524044_NICHOLS_Ckt2 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523978_HARRNG_MID-524365_RANDALL_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523979_HARRNG_EST-523266_PRINGLE_3Winding | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 b. 2. Disconnect bus at PRINGLE_TR (523265) to trip transformer at PRINGLE_TR 113.200 (523265) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_523979_HARRNG_EST-523978_HARRNG_MID_Ckt1 | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524415_AMA_SOUTH-524044_NICHOLS_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524415_AMA_SOUTH-524365_RANDALL_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524415_AMA_SOUTH-524414_AMA_SOUTH_3Winding | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at AMA_SO_TR1 (524410) to trip transformer at AMA_SO_TR1 113.200 (524410) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524746_CASTRO_CNTY311500-524734_DS-#21_Ckt1 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV a. Apply fault on CASTRO_CNTY3115.00 (524746) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 2. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524768_PLSNT_HILL-524770_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524768_PLSNT_HILL-524822_CURRY_Ckt1 | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 b. 2. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 3. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 c. 2. Reclose branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 d. 2. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524770_PLSNT_HILL-524768_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524770_PLSNT_HILL-524875_OASIS_Ckt1 | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524822_CURRY-524669_DS-#20_Ckt1 | 3 Phase fault on CURRY (524822) 115.0 kV a. Apply fault on CURRY (524822) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 2. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524874_OASIS-524764_NORRIS_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 b. 2. Drop load from bus FE-CHZPLT (524863) 115.0 kV bus b. 3. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 c. 2. Reclose branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 d. 2. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524874_OASIS-524790_CANNON_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 b. 2. Drop load from bus PERIMETER (524797) 115.0 kV bus b. 3. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 c. 2. Reclose branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 d. 2. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524874_OASIS-524875_OASIS_3Winding | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524874_OASIS-524924_PORTALES_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524875_OASIS-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524875_OASIS-524874_OASIS_3Winding | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524875_OASIS-524885_SN_JUAN_TAP623000_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524885_SN_JUAN_TAP623000-527483_CHAVES_CNTY623000_Ckt1 | 3 Phase fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV a. Apply fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524908_ROOSEVELT-524822_CURRY_Ckt2 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524908_ROOSEVELT-524909_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524908_ROOSEVELT-524924_PORTALES_Ckt1 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-524875_OASIS_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-524908_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt2 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_524909_ROOSEVELT-599955_PNM-DC6_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop switching device from bus PNM-DC6 (599955) 230.0 kV bus b. 2. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525192_KRESS_INT-525213_SWISHER_3Winding | 3 Phase fault on KRESS_INT (525192) 115.0 kV a. Apply fault on KRESS_INT (525192) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 b. 2. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525213_SWISHER-524415_AMA_SOUTH_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525213_SWISHER-525192_KRESS_INT_3Winding | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 2. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525213_SWISHER-525830_TUCO_INT_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525414_LAMTON-525413_LAMTON_3Winding | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMTON_TR1 (525412) to trip transformer at LAMTON_TR1 113.200 (525412) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525414_LAMTON-525446_RKYFORD_TP_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 b. 2. Drop load from bus LC-S_OLTON+3115.00 (525440) 115.0 kV bus b. 3. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 c. 2. Reclose branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 d. 2. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525414_LAMTON-525454_HALE_CNTY_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525414_LAMTON-525460_NEWHART_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525460_NEWHART-524746_CASTRO_CNTY311500_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525460_NEWHART-525192_KRESS_INT_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525460_NEWHART-525414_LAMTON_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525460_NEWHART-525461_NEWHART_3Winding | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525461_NEWHART-523959_POTTER_CO_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525461_NEWHART-525213_SWISHER_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525461_NEWHART-525460_NEWHART_3Winding | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525461_NEWHART-525481_PLANT_X_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525480_PLANT_X-525019_MULSHVLY_TP311500_Ckt1 | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525480_PLANT_X-525481_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-525461_NEWHART_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-525480_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt2 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-526435_SUNDOWN_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525481_PLANT_X-760498_G17-146-TAP_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525549_TOLK_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525586_NEEDMORE_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525636_LAMB_CNTY_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 b. 2. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525637_LAMB_CNTY_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525531_TOLK-525830_TUCO_INT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525549_TOLK-523961_POTTER_CO_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525549_TOLK-525531_TOLK_3Winding | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525549_TOLK-527656_CROSSROADS_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525586_NEEDMORE-525581_BLUECLDGEN_CktZ1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 b. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 b. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 b. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 b. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 c. 2. Reclose branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 c. 3. Reclose branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 c. 4. Reclose branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 c. 5. Reclose branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 d. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 d. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 d. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 d. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525586_NEEDMORE-526935_YOAKUM_Ckt1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525635_LAMB_CNTY-525636_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525635) 69.0 kV a. Apply fault on LAMB_CNTY (525635) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525636_LAMB_CNTY-525480_PLANT_X_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525636_LAMB_CNTY-525531_TOLK_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525636_LAMB_CNTY-525635_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525636_LAMB_CNTY-526020_HOCKLEY_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525828_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525828) 115.0 kV a. Apply fault on TUCO_INT (525828) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-525213_SWISHER_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-525531_TOLK_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-525828_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-525832_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR1 (525824) to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-526161_CARLISLE_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525830_TUCO_INT-526337_JONES_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-515458_BORDER_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 2. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR2 (525825) to trip transformer at TUCO_TR2 113.200 (525825) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-526936_YOAKUM_345_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526020_HOCKLEY-526019_HOCKLEY_3Winding | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOCKLEY_TR1113.200 (526017) to trip transformer at HOCKLEY_TR1113.200 (526017) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526020_HOCKLEY-526434_SUNDOWN_Ckt1 | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 b. 2. Drop load from bus LC-OPDYKE (526036) 115.0 kV bus b. 3. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 c. 2. Reclose branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 d. 2. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526435_SUNDOWN-526434_SUNDOWN_3Winding | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNDOWN_TR1113.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526435_SUNDOWN-526525_WOLFFORTH_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526435_SUNDOWN-526935_YOAKUM_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 b. 2. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 3. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. 2. Reclose branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. 2. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526934_YOAKUM-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526934) 115.0 kV a. Apply fault on YOAKUM (526934) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-525586_NEEDMORE_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-526460_AMOCO_SS_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 2. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-526934_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-526936_YOAKUM_345_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-527009_BRU_SUB_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-527028_INK_BASIN_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526935_YOAKUM-527149_MUSTANG_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526936_YOAKUM_345-525832_TUCO_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526936_YOAKUM_345-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_526936_YOAKUM_345-527896_HOBBS_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527009_BRU_SUB-527010_OXYBRU_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OXYBRU (527010) 230.0 kV bus b. 2. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527009_BRU_SUB-527011_XTO_MAHONEY623000_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527011_XTO_MAHONEY623000-526784_AMOCOWASSON623000_Ckt1 | 3 Phase fault on XTO_MAHONEY6230.00 (527011) 230.0 kV a. Apply fault on XTO_MAHONEY6230.00 (527011) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 2. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 3. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 4. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-239 GEN1 & GEN2 (761358 & 761361) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527149_MUSTANG-527276_SEMINOLE_Ckt1 | 3 Phase fault on MUSTANG (527149) 230.0 kV a. Apply fault on MUSTANG (527149) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527656_CROSSROADS-527802_EDDY_CNTY_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt2 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527802_EDDY_CNTY-527799_EDDY_NORTH_3Winding | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at EDDY_TR (527796) to trip transformer at EDDY_TR 113.200 (527796) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527802_EDDY_CNTY-527965_KIOWA_Ckt1 | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527894_HOBBS_INT-527896_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527894_HOBBS_INT-528604_ANDREWS_Ckt1 | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-527894_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-527965_KIOWA_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_527965_KIOWA-528185_N_LOVING_Ckt1 | 3 Phase fault on KIOWA (527965) 345.0 kV a. Apply fault on KIOWA (527965) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P1_762216_G17-151TAP-762467_G18-015-TAP_Ckt1 | 3 Phase fault on G17-151TAP (762216) 345.0 kV a. Apply fault on G17-151TAP (762216) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-523097_HITCHLAND | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Trip branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-523959_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a. Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-523961_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523961) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524746_CASTRO_CNTY311500 | Single Phase Fault with Stuck Breaker on CASTRO_CNTY3115.00 (524746) 115.0 kV bus a. Apply single-phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CASTRO_TR1 (524744) 13.2 kV bus to trip transformer at CASTRO_CNTY2 (524745) 69.0 kV bus b. 2. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 3. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 kV bus to DS-#21 (524734) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524768_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524768) 115.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524768) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus b. 2. Trip branch from PLSNT_HILL (524768) 115.0 kV bus to E_CLOVIS (524773) 115.0 kV bus CKT 1 b. 3. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 4. Trip branch from E_CLOVIS (524773) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524770_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524770) 230.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524770) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524822_CURRY | Single Phase Fault with Stuck Breaker on CURRY (524822) 115.0 kV bus a. Apply single-phase fault on CURRY (524822) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CURRY (524822) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 2 b. 2. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 3. Trip branch from CURRY (524822) 115.0 kV bus to DS-#20 (524669) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524875_OASIS | Single Phase Fault with Stuck Breaker on OASIS (524875) 230.0 kV bus a. Apply single-phase fault on OASIS (524875) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524908_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524908) 115.0 kV bus a. Apply single-phase fault on ROOSEVELT (524908) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus b. 2. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524909_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524909) 230.0 kV bus a. Apply single-phase fault on ROOSEVELT (524909) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 b. 2. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-524924_PORTALES | Single Phase Fault with Stuck Breaker on PORTALES (524924) 115.0 kV bus a. Apply single-phase fault on PORTALES (524924) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PORTALES (524924) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 1 b. 2. Trip branch from PORTALES (524924) 115.0 kV bus to OASIS (524874) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525192_KRESS_INT | Single Phase Fault with Stuck Breaker on KRESS_INT (525192) 115.0 kV bus a. Apply single-phase fault on KRESS_INT (525192) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 kV bus to SWISHER (525212) 115.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from KRESS_INT (525192) 115.0 kV bus to NEWHART (525460) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525213_SWISHER | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a. Apply single-phase fault on SWISHER (525213) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from SWISHER (525212) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525460_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525460) 115.0 kV bus a. Apply single-phase fault on NEWHART (525460) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 b. 2. Disconnect NEWHART_TR2113.200 (525458) 13.2 kV bus to trip transformer at NEWHART_TR2113.200 (525458) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525461_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525461) 230.0 kV bus a. Apply single-phase fault on NEWHART (525461) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 b. 2. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525480_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525480) 115.0 kV bus a. Apply single-phase fault on PLANT_X (525480) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLANTX_TR1 (525479) 13.2 kV bus to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus b. 2. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525481_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525481) 230.0 kV bus a. Apply single-phase fault on PLANT_X (525481) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 b. 2. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525531_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525531) 230.0 kV bus a. Apply single-phase fault on TOLK (525531) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus b. 2. Disconnect TOLK_TR (525538) 13.2 kV bus to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525549_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525549) 345.0 kV bus a. Apply single-phase fault on TOLK (525549) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525635_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525635) 69.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525635) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR2 (525632) 13.2 kV bus to trip transformer at LAMB_TR2 113.200 (525632) 13.2 kV bus b. 2. Disconnect LAMB_TR1 (525631) 13.2 kV bus to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525636_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525636) 115.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525636) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR3 (525633) 13.2 kV bus to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 3. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525828_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525828) 115.0 kV bus a. Apply single-phase fault on TUCO_INT (525828) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TUCO_TR4 (525821) 13.2 kV bus to trip transformer at TUCO_TR4 113.200 (525821) 13.2 kV bus b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525830_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a. Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-526934_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526934) 115.0 kV bus a. Apply single-phase fault on YOAKUM (526934) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus to trip transformer at YOAKUM_TR1 113.200 (526931) 13.2 kV bus b. 2. Disconnect YOAKUM_TR2 (526932) 13.2 kV bus to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-526935_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a. Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-526936_YOAKUM_345 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-527149_MUSTANG | Single Phase Fault with Stuck Breaker on MUSTANG (527149) 230.0 kV bus a. Apply single-phase fault on MUSTANG (527149) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to AMOCOWASSON6 (526784) 230.0 kV bus CKT 1 b. 2. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-527656_CROSSROADS | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-527894_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527894) 230.0 kV bus a. Apply single-phase fault on HOBBS_INT (527894) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect HOBBS_TR3 (527895) 13.2 kV bus to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus b. 2. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-527896_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a. Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-527965_KIOWA | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 2. Trip branch from KIOWA (527965) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_HOL-528027_RDRUNNER | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-108426 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1 (523111) 115.0 kV bus b. 5. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-92600 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-523097_HITCHLAND-ConID-108427 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Disconnect HITCHLAND (523097) 345.0 kV bus b. 3. Trip transformer from HITCHLD_TR2113.200 (523094) 13.2 kV bus to HITCHLAND (523095) 230.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-523124_GRPLNS-CB4-134500-ConID-108428 | Single Phase Fault with Stuck Breaker on GRPLNS-CB4-134.500 (523124) 34.5 kV bus a. Apply single-phase fault on GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect NOBLE_TR (523102) 13.8 kV bus b. 3. Disconnect NOBLE_WND (523103) 115.0 kV bus b. 4. Disconnect GRPLNS-HV4-3115.00 (523130) 115.0 kV bus b. 5. Disconnect GRPLNS-HV2-3115.00 (523131) 115.0 kV bus b. 6. Disconnect GRPLNS-LV4-134.500 (523127) 34.5 kV bus b. 7. Disconnect GRPLNS-LV2-134.500 (523129) 34.5 kV bus b. 8. Disconnect GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. 9. Disconnect GRPLNS-CB2-134.500 (523126) 34.5 kV bus b. 10. Disconnect GRPLNS-WT4-10.5750 (523121) 0.574999988079071 kV bus b. 11. Disconnect GRPLNS-WT2-10.5750 (523123) 0.574999988079071 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-523961_POTTER_CO-ConID-108433 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Trip transformer from POTTER_TR (523957) 13.2 kV bus to POTTER_CO (523959) 230.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 3. Disconnect POTTER_CO (523961) 345.0 kV bus b. 4. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 5. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527656_CROSSROADS-ConID-108421 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Trip line from RSVLT_CC_E (527655) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 4. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 5. Disconnect MILO_WIND (527653) 0.7 kV bus b. 6. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 7. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 8. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 9. Disconnect CROSSROADS (527656) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108422 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108423 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108424 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108440 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527965_KIOWA-ConID-108429 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-527965_KIOWA-ConID-108441 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528027_RDRUNNER-ConID-108445 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRUNNER (528027) 345.0 kV bus | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | High Voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528027_RDRUNNER-ConID-108447 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect PHANTOM (528011) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108430 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108431 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108432 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_CON-528185_N_LOVING-ConID-108443 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-118 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to BVRCNTY7 (515554) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus b. 5. Disconnect NOVUS1 (523111) 115.0 kV bus b. 6. Disconnect NOVUS1 (523112) 345.0 kV bus b. 7. Disconnect G06-44 (560577) 115.0 kV bus b. 8. Disconnect NOVUS1_TR2 (560578) 13.8 kV bus b. 9. Disconnect G06-44-2 (560581) 34.5 kV bus b. 10. Disconnect G06-44-3 (560582) 34.5 kV bus b. 11. Disconnect G06-44-4 (560583) 34.5 kV bus b. 12. Disconnect G06-44-2 (560584) 4.16 kV bus b. 13. Disconnect G06-44-3 (560585) 4.16 kV bus b. 14. Disconnect G06-44-4 (560586) 4.16 kV bus b. 15. Drop generator from NOVUS_WND (523107 ID 1) 4.16 kV bus b. 16. Drop generator from G06-44-2 (560584 ID 1) 4.16 kV bus b. 17. Drop generator from G06-44-3 (560585 ID 1) 4.16 kV bus b. 18. Drop generator from G06-44-4 (560586 ID 1) 4.16 kV bus b. 19. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-142 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b. 3. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523853_FINNEY-ConID-SPS-117 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345.0 kV bus a.Apply single-phase fault on FINNEY (523853) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOLCOMB7 (531449) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 2. Open branch from CARPENTER (523823) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 3. Disconnect FINNEY (523853) 345.0 kV bus b. 4. Disconnect LAMAR7 (599950) 345.0 kV bus b. 5. Disconnect LAMAR (599951) 345.0 kV bus b. 6. Disconnect BUFF_DUNES (523118) 345.0 kV bus b. 7. Disconnect BUFF_DN_TR1113.200 (523114) 13.2 kV bus b. 8. Disconnect BUFF_DN_TR2113.200 (523115) 13.2 kV bus b. 9. Disconnect BUFF_DUNES1134.500 (523116) 34.5 kV bus b. 10. Disconnect BUFF_DUNES2134.500 (523117) 34.5 kV bus b. 11. Clear fault from FINNEY (523853) b. 12. Drop generator from BUFF_DUNES230.6900 (523061 ID 1) 0.69 kV bus b. 13. Drop generator from BUFF_DUNES130.6900 (523062 ID 1) 0.69 kV bus b. 14. Disconnect BUFF_DUNES230.6900 (523061) 0.69 kV bus b. 15. Disconnect BUFF_DUNES130.6900 (523062) 0.69 kV bus b. 16. Disconnect BUFF_DUNES2234.500 (523063) 34.5 kV bus b. 17. Disconnect BUFF_DUNES1234.500 (523064) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523959_POTTER_CO-ConID-SPS-136 | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a.Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 2. Open branch from ROLLHILLS (524010) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Clear fault from POTTER_CO (523959) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-125 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Disconnect POTTER_TR (523957) 13.2 kV bus b. 4. Disconnect POTTER_CO (523961) 345.0 kV bus b. 5. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 6. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 7. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 8. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 9. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 10. Clear fault from POTTER_CO (523961) b. 11. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-144 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect POTTER_TR (523957) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Clear fault from POTTER_CO (523961) b.Run for 5.0 cycles and trip the following elements: b. 4. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 5. Disconnect POTTER_TR (523957) 13.2 kV bus b. 6. Disconnect POTTER_CO (523961) 345.0 kV bus b. 7. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 8. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 9. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 10. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 11. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 12. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523977_HARRNG_WST-ConID-SPS-149 | Single Phase Fault with Stuck Breaker on HARRNG_WST (523977) 230.0 kV bus a.Apply single-phase fault on HARRNG_WST (523977) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_WST (523977) 230.0 kV bus to EAST_PLANT (524163) 230.0 kV bus CKT 1 b. 3. Open branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 4. Disconnect HARRNG_WST (523977) 230.0 kV bus b. 5. Disconnect HARRNGTON1 (523971) 24.0 kV bus b. 6. Clear fault from HARRNG_WST (523977) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-150 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 3. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 4. Disconnect HARRNGTON2 (523972) 24.0 kV bus b. 5. Clear fault from HARRNG_MID (523978) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-153 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 2. Clear fault from HARRNG_MID (523978) b. 3. Drop generator from HARRNGTON2 (523972 ID 1) 24.0 kV bus b. 4. Drop load from HARRNGTON2 (523972 ID S1) 24.0 kV bus b. 5. Disconnect HARRNGTON2 (523972) 24.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-523979_HARRNG_EST-ConID-SPS-151 | Single Phase Fault with Stuck Breaker on HARRNG_EST (523979) 230.0 kV bus a.Apply single-phase fault on HARRNG_EST (523979) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_EST (523979) 230.0 kV bus to PRINGLE (523267) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_EST (523979) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Disconnect HARRNG_EST (523979) 230.0 kV bus b. 4. Disconnect HARRNGTON3 (523973) 24.0 kV bus b. 5. Clear fault from HARRNG_EST (523979) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-524044_NICHOLS-ConID-SPS-134 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230.0 kV bus a.Apply single-phase fault on NICHOLS (524044) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 2. Open branch from HUTCHISON (523551) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 3. Clear fault from NICHOLS (524044) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-524267_BUSHLAND-ConID-SPS-148 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230.0 kV bus a.Apply single-phase fault on BUSHLAND (524267) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to WILDOR2_JUS6230.00 (524290) 230.0 kV bus CKT 1 b. 2. Trip switching device at bus 524267 (BUSHLAND) 230.0 kV bus b. 3. Disconnect BSHLND_TR1 (524263) 13.2 kV bus b. 4. Disconnect WILDORA_GEN10.6900 (524285) 0.69 kV bus b. 5. Disconnect GS-PHWD_GEN10.6900 (524287) 0.69 kV bus b. 6. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b.Run for 16.0 cycles and trip the following elements: b. 7. Open branch from BUSHLAND (524267) 230.0 kV bus to DEAFSMITH (524623) 230.0 kV bus CKT 1 b. 8. Clear fault from BUSHLAND (524267) b. 9. Disconnect WILDOR_WND (524275) 34.5 kV bus b. 10. Disconnect WILDOR_WND (524276) 230.0 kV bus b. 11. Disconnect GS-PHWDRNCH134.500 (524289) 34.5 kV bus b. 12. Disconnect WILDOR2_JUS6230.00 (524290) 230.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525213_SWISHER-ConID-SPS-146 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a.Apply single-phase fault on SWISHER (525213) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525213 (SWISHER) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 b. 3. Clear fault from SWISHER (525213) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525830_TUCO_INT-ConID-SPS-147 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a.Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525830 (TUCO_INT) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525830) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526935_YOAKUM-ConID-SPS-137 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a.Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 b. 3. Clear fault from YOAKUM (526935) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-109 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 2. Open branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 4. Disconnect MILO_WIND (527653) 0.7 kV bus b. 5. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 6. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 7. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 8. Clear fault from CROSSROADS (527656) b. 9. Drop generator from SAGSFT3_2.210.7000 (527605 ID 1) 0.7 kV bus b. 10. Drop generator from SAGSFT4_2.210.7000 (527607 ID 1) 0.7 kV bus b. 11. Drop generator from SAGSFT1_2.210.7000 (527614 ID 1) 0.7 kV bus b. 12. Drop generator from SAGSFT1_2.010.7000 (527615 ID 1) 0.7 kV bus b. 13. Drop generator from SAGSFT2_2.210.7000 (527617 ID 1) 0.7 kV bus b. 14. Drop generator from SAGSFT2_2.010.7000 (527618 ID 1) 0.7 kV bus b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 25. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 26. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 27. Disconnect SUB (527608) 34.5 kV bus b. 28. Disconnect SUB (527609) 34.5 kV bus b. 29. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 30. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 31. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 32. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 33. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 34. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 35. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 36. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 37. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 38. Disconnect SAGA_NCLTR3113.8 kV bus b. 39. Disconnect SAGA_NCLTR4113.8 kV bus b. 40. Disconnect SAGA_SCLTR1113.8 kV bus b. 41. Disconnect SAGA_SCLTR2113.8 kV bus b. 42. Disconnect SUB (527628) 34.5 kV bus b. 43. Disconnect SUB (527629) 34.5 kV bus b. 44. Disconnect CROSSROADS (527656) 345.0 kV bus b. 45. Disconnect RSVLT_WIND1134.500 (527658) 34.5 kV bus b. 46. Disconnect RSVLT_WIND2134.500 (527659) 34.5 kV bus b. 47. Disconnect RSVLT_COL1 (527660) 34.5 kV bus b. 48. Disconnect RSVLT_COL2 (527661) 34.5 kV bus b. 49. Disconnect RSVLT_TR1 (527662) 13.2 kV bus b. 50. Disconnect RSVLT_TR2 (527663) 13.2 kV bus b. 51. Disconnect RSVLT_COL1 (527666) 345.0 kV bus b. 52. Disconnect RSVLT_COL2 (527667) 345.0 kV bus b. 53. Disconnect MILO_CB (577120) 34.5 kV bus b. 54. Disconnect MILO_WND (577121) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-110 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Open branch from CROSSROADS (527656) 345.0 kV bus to SAGA_SCOL (527610) 345.0 kV bus CKT 1 b. 3. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 4. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 5. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 6. Disconnect SUB (527608) 34.5 kV bus b. 7. Disconnect SUB (527609) 34.5 kV bus b. 8. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 9. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 10. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 11. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 12. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 13. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 14. Clear fault from CROSSROADS (527656) b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 25. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 26. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 27. Disconnect SAGA_NCLTR3113.8 kV bus b. 28. Disconnect SAGA_NCLTR4113.8 kV bus b. 29. Disconnect SAGA_SCLTR1113.8 kV bus b. 30. Disconnect SAGA_SCLTR2113.8 kV bus b. 31. Disconnect SUB (527628) 34.5 kV bus b. 32. Disconnect SUB (527629) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-114 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-115 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-116 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 7. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527896_HOBBS_INT-ConID-SPS-119 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a.Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Open branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Disconnect HOBBS_TR3 (527895) 13.2 kV bus b. 4. Disconnect HOBBS_INT (527896) 345.0 kV bus b. 5. Clear fault from HOBBS_INT (527896) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527965_KIOWA-ConID-SPS-120 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b.Run for 16.0 cycles and trip the following elements: b. 2. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 5. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-527965_KIOWA-ConID-SPS-121 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 20.0 cycles and trip the following elements: b. 1. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-126 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-127 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 6. Disconnect RDRUNNER (528027) 345.0 kV bus b. 7. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-128 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-122 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-123 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus b. 7. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25S | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-124 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523097_HITCHLAND-523823_CARPENTER_Ckt1 | 3 Phase fault on HITCHLAND (523097) 345.0 kV a. Apply fault on HITCHLAND (523097) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523323_MCDWL_CREEK623000-523309_MOORE_CNTY_Ckt1 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MCDWL_CREEK6230.00 (523323) 230.0 kV bus to MOORE_CNTY (523309) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523323_MCDWL_CREEK623000-523322_MCDWL_CREEK311500_3Winding | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230.0 kV a. Apply fault on MCDWL_CREEK6230.00 (523323) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MCDWL_CRKTR113.200 (523321) to trip transformer at MCDWL_CRKTR113.200 (523321) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-523323_MCDWL_CREEK623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-523869_CHAN+TASCOS623000_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to CHAN+TASCOS6230.00 (523869) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-523961_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 bus to POTTER_CO (523961) 230.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-523979_HARRNG_EST_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-524010_ROLLHILLS_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523959_POTTER_CO-524267_BUSHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523959) 230.0 kV a. Apply fault on POTTER_CO (523959) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to BUSHLAND (524267) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523961_POTTER_CO-523097_HITCHLAND_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt1 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523961_POTTER_CO-523959_POTTER_CO_Ckt2 | 3 Phase fault on POTTER_CO (523961) 345.0 kV a. Apply fault on POTTER_CO (523961) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from POTTER_CO (523961) 345.0 bus to POTTER_CO (523959) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523977_HARRNG_WST-524010_ROLLHILLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523977_HARRNG_WST-524044_NICHOLS_Ckt1 | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523977_HARRNG_WST-524162_EAST_PLANT_3Winding | 3 Phase fault on HARRNG_WST (523977) 230.0 kV a. Apply fault on HARRNG_WST (523977) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 b. 2. Disconnect bus at EPLANT_TR3 (524160) to trip transformer at EPLANT_TR3 113.200 (524160) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_WST (523977) 230.0 bus to EAST_PLANT (524163) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523978_HARRNG_MID-523977_HARRNG_WST_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to HARRNG_WST (523977) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523978_HARRNG_MID-524044_NICHOLS_Ckt2 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523978_HARRNG_MID-524365_RANDALL_Ckt1 | 3 Phase fault on HARRNG_MID (523978) 230.0 kV a. Apply fault on HARRNG_MID (523978) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523979_HARRNG_EST-523266_PRINGLE_3Winding | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 b. 2. Disconnect bus at PRINGLE_TR (523265) to trip transformer at PRINGLE_TR 113.200 (523265) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 bus to PRINGLE (523267) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_523979_HARRNG_EST-523978_HARRNG_MID_Ckt1 | 3 Phase fault on HARRNG_EST (523979) 230.0 kV a. Apply fault on HARRNG_EST (523979) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HARRNG_EST (523979) 230.0 kV bus to HARRNG_MID (523978) 230.0 kV bus CKT @1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524415_AMA_SOUTH-524044_NICHOLS_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524415_AMA_SOUTH-524365_RANDALL_Ckt1 | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from AMA_SOUTH (524415) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524415_AMA_SOUTH-524414_AMA_SOUTH_3Winding | 3 Phase fault on AMA_SOUTH (524415) 230.0 kV a. Apply fault on AMA_SOUTH (524415) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at AMA_SO_TR1 (524410) to trip transformer at AMA_SO_TR1 113.200 (524410) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524746_CASTRO_CNTY311500-524734_DS-#21_Ckt1 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV a. Apply fault on CASTRO_CNTY3115.00 (524746) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 2. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 bus to DS-#21 (524734) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524768_PLSNT_HILL-524770_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524768_PLSNT_HILL-524822_CURRY_Ckt1 | 3 Phase fault on PLSNT_HILL (524768) 115.0 kV a. Apply fault on PLSNT_HILL (524768) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 b. 2. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 3. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 c. 2. Reclose branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524768) 115.0 bus to E_CLOVIS (524773) 115.0 bus CKT 1 d. 2. Trip branch from E_CLOVIS (524773) 115.0 bus to CURRY (524822) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524770_PLSNT_HILL-524768_PLSNT_HILL_3Winding | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLSNHIL_TR1113.200 (524767) to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524770_PLSNT_HILL-524875_OASIS_Ckt1 | 3 Phase fault on PLSNT_HILL (524770) 230.0 kV a. Apply fault on PLSNT_HILL (524770) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524822_CURRY-524669_DS-#20_Ckt1 | 3 Phase fault on CURRY (524822) 115.0 kV a. Apply fault on CURRY (524822) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 2. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CURRY (524822) 115.0 bus to DS-#20 (524669) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524874_OASIS-524764_NORRIS_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 b. 2. Drop load from bus FE-CHZPLT (524863) 115.0 kV bus b. 3. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 c. 2. Reclose branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to FE-CHZPLT (524863) 115.0 bus CKT 1 d. 2. Trip branch from FE-CHZPLT (524863) 115.0 bus to NORRIS_TP (524764) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524874_OASIS-524790_CANNON_TP_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 b. 2. Drop load from bus PERIMETER (524797) 115.0 kV bus b. 3. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 c. 2. Reclose branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 bus to PERIMETER (524797) 115.0 bus CKT 1 d. 2. Trip branch from PERIMETER (524797) 115.0 bus to CANNON_TP (524790) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524874_OASIS-524875_OASIS_3Winding | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524874_OASIS-524924_PORTALES_Ckt1 | 3 Phase fault on OASIS (524874) 115.0 kV a. Apply fault on OASIS (524874) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524874) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524875_OASIS-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524875_OASIS-524874_OASIS_3Winding | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OASIS_TR1 (524872) to trip transformer at OASIS_TR1 113.200 (524872) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524875_OASIS-524885_SN_JUAN_TAP623000_Ckt1 | 3 Phase fault on OASIS (524875) 230.0 kV a. Apply fault on OASIS (524875) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524885_SN_JUAN_TAP623000-527483_CHAVES_CNTY623000_Ckt1 | 3 Phase fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV a. Apply fault on SN_JUAN_TAP6230.00 (524885) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SN_JUAN_TAP6230.00 (524885) 230.0 kV bus to CHAVES_CNTY6230.00 (527483) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524908_ROOSEVELT-524822_CURRY_Ckt2 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524908_ROOSEVELT-524909_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524908_ROOSEVELT-524924_PORTALES_Ckt1 | 3 Phase fault on ROOSEVELT (524908) 115.0 kV a. Apply fault on ROOSEVELT (524908) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524908) 115.0 kV bus to PORTALES (524924) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-524770_PLSNT_HILL_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to PLSNT_HILL (524770) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-524875_OASIS_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-524908_ROOSEVELT_3Winding | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at ROSEVLT_TR1113.200 (524907) to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-525531_TOLK_Ckt2 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_524909_ROOSEVELT-599955_PNM-DC6_Ckt1 | 3 Phase fault on ROOSEVELT (524909) 230.0 kV a. Apply fault on ROOSEVELT (524909) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop switching device from bus PNM-DC6 (599955) 230.0 kV bus b. 2. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROOSEVELT (524909) 230.0 bus to PNM-DC6 (599955) 230.0 bus CKT @1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525192_KRESS_INT-525213_SWISHER_3Winding | 3 Phase fault on KRESS_INT (525192) 115.0 kV a. Apply fault on KRESS_INT (525192) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 b. 2. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KRESS_INT (525192) 115.0 bus to SWISHER (525212) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525213_SWISHER-524415_AMA_SOUTH_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to AMA_SOUTH (524415) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525213_SWISHER-525192_KRESS_INT_3Winding | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWISHER_TR1113.200 (525211) to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 2. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525212) 115.0 bus to KRESS_INT (525192) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525213_SWISHER-525830_TUCO_INT_Ckt1 | 3 Phase fault on SWISHER (525213) 230.0 kV a. Apply fault on SWISHER (525213) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525414_LAMTON-525413_LAMTON_3Winding | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMTON_TR1 (525412) to trip transformer at LAMTON_TR1 113.200 (525412) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525414_LAMTON-525446_RKYFORD_TP_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 b. 2. Drop load from bus LC-S_OLTON+3115.00 (525440) 115.0 kV bus b. 3. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 c. 2. Reclose branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to LC-S_OLTON+3115.00 (525440) 115.0 bus CKT 1 d. 2. Trip branch from LC-S_OLTON+3115.00 (525440) 115.0 bus to RKYFORD_TP (525446) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525414_LAMTON-525454_HALE_CNTY_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 kV bus to HALE_CNTY (525454) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525414_LAMTON-525460_NEWHART_Ckt1 | 3 Phase fault on LAMTON (525414) 115.0 kV a. Apply fault on LAMTON (525414) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMTON (525414) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to NEWHART (525460) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525460_NEWHART-524746_CASTRO_CNTY311500_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to CASTRO_CNTY3115.00 (524746) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525460_NEWHART-525192_KRESS_INT_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525460_NEWHART-525414_LAMTON_Ckt1 | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 b. 2. Drop load from bus HART_INDUST3115.00 (525124) 115.0 kV bus b. 3. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 c. 2. Reclose branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525460) 115.0 bus to HART_INDUST3115.00 (525124) 115.0 bus CKT 1 d. 2. Trip branch from HART_INDUST3115.00 (525124) 115.0 bus to LAMTON (525414) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525460_NEWHART-525461_NEWHART_3Winding | 3 Phase fault on NEWHART (525460) 115.0 kV a. Apply fault on NEWHART (525460) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525461_NEWHART-523959_POTTER_CO_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525461_NEWHART-525213_SWISHER_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525461_NEWHART-525460_NEWHART_3Winding | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEWHART_TR1113.200 (525459) to trip transformer at NEWHART_TR1113.200 (525459) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525461_NEWHART-525481_PLANT_X_Ckt1 | 3 Phase fault on NEWHART (525461) 230.0 kV a. Apply fault on NEWHART (525461) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and Frequency protection trips G18-089 (763189) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525480_PLANT_X-525019_MULSHVLY_TP311500_Ckt1 | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525480_PLANT_X-525481_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525480) 115.0 kV a. Apply fault on PLANT_X (525480) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-525461_NEWHART_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-525480_PLANT_X_3Winding | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PLANTX_TR1 (525479) to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-525531_TOLK_Ckt2 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-526435_SUNDOWN_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to SUNDOWN (526435) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525481_PLANT_X-760498_G17-146-TAP_Ckt1 | 3 Phase fault on PLANT_X (525481) 230.0 kV a. Apply fault on PLANT_X (525481) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to G17-146-TAP (760498) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-524909_ROOSEVELT_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525481_PLANT_X_Ckt2 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525549_TOLK_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525586_NEEDMORE_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525636_LAMB_CNTY_3Winding | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 b. 2. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525637_LAMB_CNTY_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 bus to LAMB_CNTY (525637) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525531_TOLK-525830_TUCO_INT_Ckt1 | 3 Phase fault on TOLK (525531) 230.0 kV a. Apply fault on TOLK (525531) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525531) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525549_TOLK-523961_POTTER_CO_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525549_TOLK-525531_TOLK_3Winding | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TOLK_TR (525538) to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525549_TOLK-527656_CROSSROADS_Ckt1 | 3 Phase fault on TOLK (525549) 345.0 kV a. Apply fault on TOLK (525549) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525586_NEEDMORE-525581_BLUECLDGEN_CktZ1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 b. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 b. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 b. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 b. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 c. 2. Reclose branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 c. 3. Reclose branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 c. 4. Reclose branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 c. 5. Reclose branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 bus to BLUECLDPOI (525585) 230.0 bus CKT Z1 d. 2. Trip branch from BLUECLDPOI (525585) 230.0 bus to BLUECLDCOL (525584) 230.0 bus CKT 1 d. 3. Trip branch from BLUECLDCOL (525584) 230.0 bus to BLUECLDCOL (525583) 230.0 bus CKT 1 d. 4. Trip branch from BLUECLDCOL (525583) 34.5 bus to BBLUECLD (525582) 34.5 bus CKT 1 d. 5. Trip branch from BBLUECLD (525582) 34.5 bus to BLUECLDGEN (525581) 34.5 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525586_NEEDMORE-526935_YOAKUM_Ckt1 | 3 Phase fault on NEEDMORE (525586) 230.0 kV a. Apply fault on NEEDMORE (525586) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525635_LAMB_CNTY-525636_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525635) 69.0 kV a. Apply fault on LAMB_CNTY (525635) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525636_LAMB_CNTY-525480_PLANT_X_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to PLANT_X (525480) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525636_LAMB_CNTY-525531_TOLK_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR3 (525633) to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525637) 230.0 bus to TOLK (525531) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525636_LAMB_CNTY-525635_LAMB_CNTY_3Winding | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LAMB_TR1 (525631) to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525636_LAMB_CNTY-526020_HOCKLEY_Ckt1 | 3 Phase fault on LAMB_CNTY (525636) 115.0 kV a. Apply fault on LAMB_CNTY (525636) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525828_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525828) 115.0 kV a. Apply fault on TUCO_INT (525828) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-525213_SWISHER_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-525531_TOLK_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-525828_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR3 (525819) to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-525832_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR1 (525824) to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-526161_CARLISLE_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to CARLISLE (526161) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525830_TUCO_INT-526337_JONES_Ckt1 | 3 Phase fault on TUCO_INT (525830) 230.0 kV a. Apply fault on TUCO_INT (525830) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to JONES (526337) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-515458_BORDER_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 2. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-525830_TUCO_INT_3Winding | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TUCO_TR2 (525825) to trip transformer at TUCO_TR2 113.200 (525825) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-526936_YOAKUM_345_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526020_HOCKLEY-526019_HOCKLEY_3Winding | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOCKLEY_TR1113.200 (526017) to trip transformer at HOCKLEY_TR1113.200 (526017) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526020_HOCKLEY-526434_SUNDOWN_Ckt1 | 3 Phase fault on HOCKLEY (526020) 115.0 kV a. Apply fault on HOCKLEY (526020) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 b. 2. Drop load from bus LC-OPDYKE (526036) 115.0 kV bus b. 3. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 c. 2. Reclose branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOCKLEY (526020) 115.0 bus to LC-OPDYKE (526036) 115.0 bus CKT 1 d. 2. Trip branch from LC-OPDYKE (526036) 115.0 bus to SUNDOWN (526434) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526435_SUNDOWN-526434_SUNDOWN_3Winding | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNDOWN_TR1113.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526435_SUNDOWN-526525_WOLFFORTH_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 kV bus to WOLFFORTH (526525) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526435_SUNDOWN-526935_YOAKUM_Ckt1 | 3 Phase fault on SUNDOWN (526435) 230.0 kV a. Apply fault on SUNDOWN (526435) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 b. 2. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 3. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. 2. Reclose branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNDOWN (526435) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. 2. Trip branch from AMOCO_SS (526460) 230.0 bus to YOAKUM (526935) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526934_YOAKUM-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526934) 115.0 kV a. Apply fault on YOAKUM (526934) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-525586_NEEDMORE_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to NEEDMORE (525586) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-526460_AMOCO_SS_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCO_SS (526460) 230.0 kV bus b. 2. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 bus to AMOCO_SS (526460) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-526934_YOAKUM_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR2 (526932) to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-526936_YOAKUM_345_3Winding | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-527009_BRU_SUB_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-527028_INK_BASIN_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to INK_BASIN (527028) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526935_YOAKUM-527149_MUSTANG_Ckt1 | 3 Phase fault on YOAKUM (526935) 230.0 kV a. Apply fault on YOAKUM (526935) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526936_YOAKUM_345-525832_TUCO_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526936_YOAKUM_345-526935_YOAKUM_3Winding | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at YOAKUM_TR1 (526937) to trip transformer at YOAKUM_TR1 13.200 (526937) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_526936_YOAKUM_345-527896_HOBBS_INT_Ckt1 | 3 Phase fault on YOAKUM_345 (526936) 345.0 kV a. Apply fault on YOAKUM_345 (526936) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527009_BRU_SUB-527010_OXYBRU_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OXYBRU (527010) 230.0 kV bus b. 2. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 bus to OXYBRU (527010) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527009_BRU_SUB-527011_XTO_MAHONEY623000_Ckt1 | 3 Phase fault on BRU_SUB (527009) 230.0 kV a. Apply fault on BRU_SUB (527009) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BRU_SUB (527009) 230.0 kV bus to XTO_MAHONEY6230.00 (527011) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527011_XTO_MAHONEY623000-526784_AMOCOWASSON623000_Ckt1 | 3 Phase fault on XTO_MAHONEY6230.00 (527011) 230.0 kV a. Apply fault on XTO_MAHONEY6230.00 (527011) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 2. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 3. Drop load from bus AMOCOWASSON6230.00 (526784) 230.0 kV bus b. 4. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from XTO_MAHONEY6230.00 (527011) 230.0 bus to AMOCOWASSON6230.00 (526784) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-239 GEN1 & GEN2 (761358 & 761361) | Protection disabled with no impact to stability.
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527149_MUSTANG-527276_SEMINOLE_Ckt1 | 3 Phase fault on MUSTANG (527149) 230.0 kV a. Apply fault on MUSTANG (527149) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527656_CROSSROADS-527802_EDDY_CNTY_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt1 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527656_CROSSROADS-527896_HOBBS_INT_Ckt2 | 3 Phase fault on CROSSROADS (527656) 345.0 kV a. Apply fault on CROSSROADS (527656) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527802_EDDY_CNTY-527799_EDDY_NORTH_3Winding | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at EDDY_TR (527796) to trip transformer at EDDY_TR 113.200 (527796) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527802_EDDY_CNTY-527965_KIOWA_Ckt1 | 3 Phase fault on EDDY_CNTY (527802) 345.0 kV a. Apply fault on EDDY_CNTY (527802) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527894_HOBBS_INT-527896_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527894_HOBBS_INT-528604_ANDREWS_Ckt1 | 3 Phase fault on HOBBS_INT (527894) 230.0 kV a. Apply fault on HOBBS_INT (527894) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-527656_CROSSROADS_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-527894_HOBBS_INT_3Winding | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at HOBBS_TR3 (527895) to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-527965_KIOWA_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt1 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527896_HOBBS_INT-528027_RDRUNNER_Ckt2 | 3 Phase fault on HOBBS_INT (527896) 345.0 kV a. Apply fault on HOBBS_INT (527896) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_527965_KIOWA-528185_N_LOVING_Ckt1 | 3 Phase fault on KIOWA (527965) 345.0 kV a. Apply fault on KIOWA (527965) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P1_762216_G17-151TAP-762467_G18-015-TAP_Ckt1 | 3 Phase fault on G17-151TAP (762216) 345.0 kV a. Apply fault on G17-151TAP (762216) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-151TAP (762216) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-523097_HITCHLAND | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Trip branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-523959_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a. Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523959) 230.0 kV bus to MCDWL_CREEK6230.00 (523323) 230.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523959) 230.0 kV bus to HARRNG_EST (523979) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-523961_POTTER_CO | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO (523961) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip branch from POTTER_CO (523961) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524746_CASTRO_CNTY311500 | Single Phase Fault with Stuck Breaker on CASTRO_CNTY3115.00 (524746) 115.0 kV bus a. Apply single-phase fault on CASTRO_CNTY3115.00 (524746) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CASTRO_TR1 (524744) 13.2 kV bus to trip transformer at CASTRO_CNTY2 (524745) 69.0 kV bus b. 2. Drop load from bus DS-#21 (524734) 115.0 kV bus b. 3. Trip branch from CASTRO_CNTY3115.00 (524746) 115.0 kV bus to DS-#21 (524734) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524768_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524768) 115.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524768) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus b. 2. Trip branch from PLSNT_HILL (524768) 115.0 kV bus to E_CLOVIS (524773) 115.0 kV bus CKT 1 b. 3. Drop load from bus E_CLOVIS (524773) 115.0 kV bus b. 4. Trip branch from E_CLOVIS (524773) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524770_PLSNT_HILL | Single Phase Fault with Stuck Breaker on PLSNT_HILL (524770) 230.0 kV bus a. Apply single-phase fault on PLSNT_HILL (524770) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL (524770) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Disconnect PLSNHIL_TR1113.200 (524767) 13.2 kV bus to trip transformer at PLSNHIL_TR1113.200 (524767) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524822_CURRY | Single Phase Fault with Stuck Breaker on CURRY (524822) 115.0 kV bus a. Apply single-phase fault on CURRY (524822) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CURRY (524822) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 2 b. 2. Drop load from bus DS-#20 (524669) 115.0 kV bus b. 3. Trip branch from CURRY (524822) 115.0 kV bus to DS-#20 (524669) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524875_OASIS | Single Phase Fault with Stuck Breaker on OASIS (524875) 230.0 kV bus a. Apply single-phase fault on OASIS (524875) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OASIS (524875) 230.0 kV bus to ROOSEVELT (524909) 230.0 kV bus CKT 1 b. 2. Trip branch from OASIS (524875) 230.0 kV bus to SN_JUAN_TAP6230.00 (524885) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524908_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524908) 115.0 kV bus a. Apply single-phase fault on ROOSEVELT (524908) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus b. 2. Trip branch from ROOSEVELT (524908) 115.0 kV bus to CURRY (524822) 115.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524909_ROOSEVELT | Single Phase Fault with Stuck Breaker on ROOSEVELT (524909) 230.0 kV bus a. Apply single-phase fault on ROOSEVELT (524909) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT (524909) 230.0 kV bus to OASIS (524875) 230.0 kV bus CKT 1 b. 2. Disconnect ROSEVLT_TR1113.200 (524907) 13.2 kV bus to trip transformer at ROSEVLT_TR1113.200 (524907) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-524924_PORTALES | Single Phase Fault with Stuck Breaker on PORTALES (524924) 115.0 kV bus a. Apply single-phase fault on PORTALES (524924) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PORTALES (524924) 115.0 kV bus to ROOSEVELT (524908) 115.0 kV bus CKT 1 b. 2. Trip branch from PORTALES (524924) 115.0 kV bus to OASIS (524874) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525192_KRESS_INT | Single Phase Fault with Stuck Breaker on KRESS_INT (525192) 115.0 kV bus a. Apply single-phase fault on KRESS_INT (525192) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT (525192) 115.0 kV bus to SWISHER (525212) 115.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from KRESS_INT (525192) 115.0 kV bus to NEWHART (525460) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525213_SWISHER | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a. Apply single-phase fault on SWISHER (525213) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER (525213) 230.0 kV bus to NEWHART (525461) 230.0 kV bus CKT 1 b. 2. Disconnect SWISHER_TR1113.200 (525211) 13.2 kV bus to trip transformer at SWISHER_TR1113.200 (525211) 13.2 kV bus b. 3. Trip branch from SWISHER (525212) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525460_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525460) 115.0 kV bus a. Apply single-phase fault on NEWHART (525460) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525460) 115.0 kV bus to KRESS_INT (525192) 115.0 kV bus CKT 1 b. 2. Disconnect NEWHART_TR2113.200 (525458) 13.2 kV bus to trip transformer at NEWHART_TR2113.200 (525458) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525461_NEWHART | Single Phase Fault with Stuck Breaker on NEWHART (525461) 230.0 kV bus a. Apply single-phase fault on NEWHART (525461) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART (525461) 230.0 kV bus to SWISHER (525213) 230.0 kV bus CKT 1 b. 2. Trip branch from NEWHART (525461) 230.0 kV bus to PLANT_X (525481) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525480_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525480) 115.0 kV bus a. Apply single-phase fault on PLANT_X (525480) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect PLANTX_TR1 (525479) 13.2 kV bus to trip transformer at PLANTX_TR1 113.200 (525479) 13.2 kV bus b. 2. Trip branch from PLANT_X (525480) 115.0 kV bus to MULSHVLY_TP3115.00 (525019) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525481_PLANT_X | Single Phase Fault with Stuck Breaker on PLANT_X (525481) 230.0 kV bus a. Apply single-phase fault on PLANT_X (525481) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 2 b. 2. Trip branch from PLANT_X (525481) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525531_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525531) 230.0 kV bus a. Apply single-phase fault on TOLK (525531) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus b. 2. Disconnect TOLK_TR (525538) 13.2 kV bus to trip transformer at TOLK_TR 2 113.200 (525538) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525549_TOLK | Single Phase Fault with Stuck Breaker on TOLK (525549) 345.0 kV bus a. Apply single-phase fault on TOLK (525549) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TOLK (525549) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect TOLK_TR (525537) 13.2 kV bus to trip transformer at TOLK_TR 113.200 (525537) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G01-036 (524779). High Voltage issues observed. | Protection disabled with no impact to stability. Operational steady state fixes (existing caps/taps/gen set points).
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525635_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525635) 69.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525635) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR2 (525632) 13.2 kV bus to trip transformer at LAMB_TR2 113.200 (525632) 13.2 kV bus b. 2. Disconnect LAMB_TR1 (525631) 13.2 kV bus to trip transformer at LAMB_TR1 113.200 (525631) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525636_LAMB_CNTY | Single Phase Fault with Stuck Breaker on LAMB_CNTY (525636) 115.0 kV bus a. Apply single-phase fault on LAMB_CNTY (525636) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LAMB_TR3 (525633) 13.2 kV bus to trip transformer at LAMB_TR3 113.200 (525633) 13.2 kV bus b. 2. Trip branch from LAMB_CNTY (525637) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 3. Trip branch from LAMB_CNTY (525636) 115.0 kV bus to HOCKLEY (526020) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525828_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525828) 115.0 kV bus a. Apply single-phase fault on TUCO_INT (525828) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TUCO_TR4 (525821) 13.2 kV bus to trip transformer at TUCO_TR4 113.200 (525821) 13.2 kV bus b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus to trip transformer at TUCO_TR3 113.200 (525819) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525830_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a. Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525830) 230.0 kV bus to TOLK (525531) 230.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus to trip transformer at TUCO_TR1 113.200 (525824) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-526934_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526934) 115.0 kV bus a. Apply single-phase fault on YOAKUM (526934) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus to trip transformer at YOAKUM_TR1 113.200 (526931) 13.2 kV bus b. 2. Disconnect YOAKUM_TR2 (526932) 13.2 kV bus to trip transformer at YOAKUM_TR2 113.200 (526932) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-526935_YOAKUM | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a. Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM (526935) 230.0 kV bus to BRU_SUB (527009) 230.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM (526935) 230.0 kV bus to MUSTANG (527149) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-526936_YOAKUM_345 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-527149_MUSTANG | Single Phase Fault with Stuck Breaker on MUSTANG (527149) 230.0 kV bus a. Apply single-phase fault on MUSTANG (527149) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG (527149) 230.0 kV bus to AMOCOWASSON6 (526784) 230.0 kV bus CKT 1 b. 2. Trip branch from MUSTANG (527149) 230.0 kV bus to SEMINOLE (527276) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-527656_CROSSROADS | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Trip branch from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-527894_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527894) 230.0 kV bus a. Apply single-phase fault on HOBBS_INT (527894) 230.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect HOBBS_TR3 (527895) 13.2 kV bus to trip transformer at HOBBS_TR3 113.200 (527895) 13.2 kV bus b. 2. Trip branch from HOBBS_INT (527894) 230.0 kV bus to ANDREWS (528604) 230.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-527896_HOBBS_INT | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a. Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-527965_KIOWA | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 2. Trip branch from KIOWA (527965) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_HOL-528027_RDRUNNER | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 2. Trip branch from RDRUNNER (528027) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-108426 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1 (523111) 115.0 kV bus b. 5. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-515554_BVRCNTY7-ConID-92600 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-523097_HITCHLAND-ConID-108427 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a. Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to CARPENTER (523823) 345.0 kV bus CKT 1 b. 2. Disconnect HITCHLAND (523097) 345.0 kV bus b. 3. Trip transformer from HITCHLD_TR2113.200 (523094) 13.2 kV bus to HITCHLAND (523095) 230.0 kV bus to HITCHLAND (523097) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-523124_GRPLNS-CB4-134500-ConID-108428 | Single Phase Fault with Stuck Breaker on GRPLNS-CB4-134.500 (523124) 34.5 kV bus a. Apply single-phase fault on GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect NOBLE_TR (523102) 13.8 kV bus b. 3. Disconnect NOBLE_WND (523103) 115.0 kV bus b. 4. Disconnect GRPLNS-HV4-3115.00 (523130) 115.0 kV bus b. 5. Disconnect GRPLNS-HV2-3115.00 (523131) 115.0 kV bus b. 6. Disconnect GRPLNS-LV4-134.500 (523127) 34.5 kV bus b. 7. Disconnect GRPLNS-LV2-134.500 (523129) 34.5 kV bus b. 8. Disconnect GRPLNS-CB4-134.500 (523124) 34.5 kV bus b. 9. Disconnect GRPLNS-CB2-134.500 (523126) 34.5 kV bus b. 10. Disconnect GRPLNS-WT4-10.5750 (523121) 0.574999988079071 kV bus b. 11. Disconnect GRPLNS-WT2-10.5750 (523123) 0.574999988079071 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-523961_POTTER_CO-ConID-108433 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a. Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Trip transformer from POTTER_TR (523957) 13.2 kV bus to POTTER_CO (523959) 230.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 3. Disconnect POTTER_CO (523961) 345.0 kV bus b. 4. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 5. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527656_CROSSROADS-ConID-108421 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a. Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Trip line from RSVLT_CC_E (527655) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 4. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 5. Disconnect MILO_WIND (527653) 0.7 kV bus b. 6. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 7. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 8. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 9. Disconnect CROSSROADS (527656) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108422 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108423 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108424 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Trip transformer from EDDY_TR (527796) 13.2 kV bus to EDDY_NORTH (527799) 230.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527802_EDDY_CNTY-ConID-108440 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a. Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Trip line from CROSSROADS (527656) 345.0 kV bus to EDDY_CNTY (527802) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_CNTY (527802) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527965_KIOWA-ConID-108429 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-527965_KIOWA-ConID-108441 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a. Apply single-phase fault on KIOWA (527965) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Disconnect HOBBS_TR3 (527895) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528027_RDRUNNER-ConID-108445 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRUNNER (528027) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528027_RDRUNNER-ConID-108447 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a. Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PHANTOM (528015) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect PHANTOM (528011) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108430 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108431 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108432 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from NORTH_LOVNG3115.00 (528182) 115.0 kV bus to N_LOVING (528185) 345.0 kV bus to N_LOVING (528186) 13.2 kV bus CKT 1 b. 2. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_CON-528185_N_LOVING-ConID-108443 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a. Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 2. Trip line from KIOWA (527965) 345.0 kV bus to N_LOVING (528185) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528185) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-118 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to BVRCNTY7 (515554) 345.0 kV bus CKT 2 b. 2. Disconnect NOVUS_WND (523107) 4.16 kV bus b. 3. Disconnect NOVUS1 (523109) 34.5 kV bus b. 4. Disconnect NOVUS1_TR1 (523110) 13.8 kV bus b. 5. Disconnect NOVUS1 (523111) 115.0 kV bus b. 6. Disconnect NOVUS1 (523112) 345.0 kV bus b. 7. Disconnect G06-44 (560577) 115.0 kV bus b. 8. Disconnect NOVUS1_TR2 (560578) 13.8 kV bus b. 9. Disconnect G06-44-2 (560581) 34.5 kV bus b. 10. Disconnect G06-44-3 (560582) 34.5 kV bus b. 11. Disconnect G06-44-4 (560583) 34.5 kV bus b. 12. Disconnect G06-44-2 (560584) 4.16 kV bus b. 13. Disconnect G06-44-3 (560585) 4.16 kV bus b. 14. Disconnect G06-44-4 (560586) 4.16 kV bus b. 15. Drop generator from NOVUS_WND (523107 ID 1) 4.16 kV bus b. 16. Drop generator from G06-44-2 (560584 ID 1) 4.16 kV bus b. 17. Drop generator from G06-44-3 (560585 ID 1) 4.16 kV bus b. 18. Drop generator from G06-44-4 (560586 ID 1) 4.16 kV bus b. 19. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523097_HITCHLAND-ConID-SPS-142 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345.0 kV bus a.Apply single-phase fault on HITCHLAND (523097) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect HITCHLD_TR0113.200 (523091) 13.2 kV bus b. 3. Clear fault from HITCHLAND (523097) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523853_FINNEY-ConID-SPS-117 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345.0 kV bus a.Apply single-phase fault on FINNEY (523853) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOLCOMB7 (531449) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 2. Open branch from CARPENTER (523823) 345.0 kV bus to FINNEY (523853) 345.0 kV bus CKT 1 b. 3. Disconnect FINNEY (523853) 345.0 kV bus b. 4. Disconnect LAMAR7 (599950) 345.0 kV bus b. 5. Disconnect LAMAR (599951) 345.0 kV bus b. 6. Disconnect BUFF_DUNES (523118) 345.0 kV bus b. 7. Disconnect BUFF_DN_TR1113.200 (523114) 13.2 kV bus b. 8. Disconnect BUFF_DN_TR2113.200 (523115) 13.2 kV bus b. 9. Disconnect BUFF_DUNES1134.500 (523116) 34.5 kV bus b. 10. Disconnect BUFF_DUNES2134.500 (523117) 34.5 kV bus b. 11. Clear fault from FINNEY (523853) b. 12. Drop generator from BUFF_DUNES230.6900 (523061 ID 1) 0.69 kV bus b. 13. Drop generator from BUFF_DUNES130.6900 (523062 ID 1) 0.69 kV bus b. 14. Disconnect BUFF_DUNES230.6900 (523061) 0.69 kV bus b. 15. Disconnect BUFF_DUNES130.6900 (523062) 0.69 kV bus b. 16. Disconnect BUFF_DUNES2234.500 (523063) 34.5 kV bus b. 17. Disconnect BUFF_DUNES1234.500 (523064) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523959_POTTER_CO-ConID-SPS-136 | Single Phase Fault with Stuck Breaker on POTTER_CO (523959) 230.0 kV bus a.Apply single-phase fault on POTTER_CO (523959) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 2. Open branch from ROLLHILLS (524010) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Clear fault from POTTER_CO (523959) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-125 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Disconnect POTTER_TR (523957) 13.2 kV bus b. 4. Disconnect POTTER_CO (523961) 345.0 kV bus b. 5. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 6. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 7. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 8. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 9. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 10. Clear fault from POTTER_CO (523961) b. 11. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523961_POTTER_CO-ConID-SPS-144 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345.0 kV bus a.Apply single-phase fault on POTTER_CO (523961) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect POTTER_TR (523957) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect POTTER_TR (523957) 13.2 kV bus b. 3. Clear fault from POTTER_CO (523961) b.Run for 5.0 cycles and trip the following elements: b. 4. Open branch from HITCHLAND (523097) 345.0 kV bus to POTTER_CO (523961) 345.0 kV bus CKT 1 b. 5. Disconnect POTTER_TR (523957) 13.2 kV bus b. 6. Disconnect POTTER_CO (523961) 345.0 kV bus b. 7. Disconnect SPNSPUR_WND7345.00 (524296) 345.0 kV bus b. 8. Disconnect SPNSPUR_COL7345.00 (524299) 345.0 kV bus b. 9. Disconnect SPNSPUR_COL134.500 (524298) 34.5 kV bus b. 10. Disconnect SPNSPUR_WND134.500 (524294) 34.5 kV bus b. 11. Disconnect SPNSPUR_GEN10.6900 (524295) 0.69 kV bus b. 12. Disconnect SPNSPUR_TR1113.200 (524297) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523977_HARRNG_WST-ConID-SPS-149 | Single Phase Fault with Stuck Breaker on HARRNG_WST (523977) 230.0 kV bus a.Apply single-phase fault on HARRNG_WST (523977) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_WST (523977) 230.0 kV bus to ROLLHILLS (524010) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_WST (523977) 230.0 kV bus to EAST_PLANT (524163) 230.0 kV bus CKT 1 b. 3. Open branch from HARRNG_WST (523977) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 4. Disconnect HARRNG_WST (523977) 230.0 kV bus b. 5. Disconnect HARRNGTON1 (523971) 24.0 kV bus b. 6. Clear fault from HARRNG_WST (523977) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-150 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to RANDALL (524365) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 3. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 4. Disconnect HARRNGTON2 (523972) 24.0 kV bus b. 5. Clear fault from HARRNG_MID (523978) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523978_HARRNG_MID-ConID-SPS-153 | Single Phase Fault with Stuck Breaker on HARRNG_MID (523978) 230.0 kV bus a.Apply single-phase fault on HARRNG_MID (523978) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect HARRNG_MID (523978) 230.0 kV bus b. 2. Clear fault from HARRNG_MID (523978) b. 3. Drop generator from HARRNGTON2 (523972 ID 1) 24.0 kV bus b. 4. Drop load from HARRNGTON2 (523972 ID S1) 24.0 kV bus b. 5. Disconnect HARRNGTON2 (523972) 24.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-523979_HARRNG_EST-ConID-SPS-151 | Single Phase Fault with Stuck Breaker on HARRNG_EST (523979) 230.0 kV bus a.Apply single-phase fault on HARRNG_EST (523979) 230.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_EST (523979) 230.0 kV bus to PRINGLE (523267) 230.0 kV bus CKT 1 b. 2. Open branch from HARRNG_EST (523979) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b. 3. Disconnect HARRNG_EST (523979) 230.0 kV bus b. 4. Disconnect HARRNGTON3 (523973) 24.0 kV bus b. 5. Clear fault from HARRNG_EST (523979) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-524044_NICHOLS-ConID-SPS-134 | Single Phase Fault with Stuck Breaker on NICHOLS (524044) 230.0 kV bus a.Apply single-phase fault on NICHOLS (524044) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HARRNG_MID (523978) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 2 b. 2. Open branch from HUTCHISON (523551) 230.0 kV bus to NICHOLS (524044) 230.0 kV bus CKT 1 b. 3. Clear fault from NICHOLS (524044) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-524267_BUSHLAND-ConID-SPS-148 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230.0 kV bus a.Apply single-phase fault on BUSHLAND (524267) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from BUSHLAND (524267) 230.0 kV bus to WILDOR2_JUS6230.00 (524290) 230.0 kV bus CKT 1 b. 2. Trip switching device at bus 524267 (BUSHLAND) 230.0 kV bus b. 3. Disconnect BSHLND_TR1 (524263) 13.2 kV bus b. 4. Disconnect WILDORA_GEN10.6900 (524285) 0.69 kV bus b. 5. Disconnect GS-PHWD_GEN10.6900 (524287) 0.69 kV bus b. 6. Open branch from BUSHLAND (524267) 230.0 kV bus to POTTER_CO (523959) 230.0 kV bus CKT 1 b.Run for 16.0 cycles and trip the following elements: b. 7. Open branch from BUSHLAND (524267) 230.0 kV bus to DEAFSMITH (524623) 230.0 kV bus CKT 1 b. 8. Clear fault from BUSHLAND (524267) b. 9. Disconnect WILDOR_WND (524275) 34.5 kV bus b. 10. Disconnect WILDOR_WND (524276) 230.0 kV bus b. 11. Disconnect GS-PHWDRNCH134.500 (524289) 34.5 kV bus b. 12. Disconnect WILDOR2_JUS6230.00 (524290) 230.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525213_SWISHER-ConID-SPS-146 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230.0 kV bus a.Apply single-phase fault on SWISHER (525213) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525213 (SWISHER) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from SWISHER (525213) 230.0 kV bus to TUCO_INT (525830) 230.0 kV bus CKT 1 b. 3. Clear fault from SWISHER (525213) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525830_TUCO_INT-ConID-SPS-147 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230.0 kV bus a.Apply single-phase fault on TUCO_INT (525830) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Trip switching device at bus 525830 (TUCO_INT) 230.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect TUCO_TR3 (525819) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525830) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526935_YOAKUM-ConID-SPS-137 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230.0 kV bus a.Apply single-phase fault on YOAKUM (526935) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526931) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from NEEDMORE (525586) 230.0 kV bus to YOAKUM (526935) 230.0 kV bus CKT 1 b. 3. Clear fault from YOAKUM (526935) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-109 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 2. Open branch from TOLK (525549) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect RSVLT_CC_E (527655) 345.0 kV bus b. 4. Disconnect MILO_WIND (527653) 0.7 kV bus b. 5. Disconnect RSVLT_GEN1 (527651) 0.69 kV bus b. 6. Disconnect RSVLT_GEN2 (527652) 0.69 kV bus b. 7. Disconnect RSVLT_CC_W (527654) 345.0 kV bus b. 8. Clear fault from CROSSROADS (527656) b. 9. Drop generator from SAGSFT3_2.210.7000 (527605 ID 1) 0.7 kV bus b. 10. Drop generator from SAGSFT4_2.210.7000 (527607 ID 1) 0.7 kV bus b. 11. Drop generator from SAGSFT1_2.210.7000 (527614 ID 1) 0.7 kV bus b. 12. Drop generator from SAGSFT1_2.010.7000 (527615 ID 1) 0.7 kV bus b. 13. Drop generator from SAGSFT2_2.210.7000 (527617 ID 1) 0.7 kV bus b. 14. Drop generator from SAGSFT2_2.010.7000 (527618 ID 1) 0.7 kV bus b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 25. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 26. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 27. Disconnect SUB (527608) 34.5 kV bus b. 28. Disconnect SUB (527609) 34.5 kV bus b. 29. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 30. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 31. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 32. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 33. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 34. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 35. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 36. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 37. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 38. Disconnect SAGA_NCLTR3113.8 kV bus b. 39. Disconnect SAGA_NCLTR4113.8 kV bus b. 40. Disconnect SAGA_SCLTR1113.8 kV bus b. 41. Disconnect SAGA_SCLTR2113.8 kV bus b. 42. Disconnect SUB (527628) 34.5 kV bus b. 43. Disconnect SUB (527629) 34.5 kV bus b. 44. Disconnect CROSSROADS (527656) 345.0 kV bus b. 45. Disconnect RSVLT_WIND1134.500 (527658) 34.5 kV bus b. 46. Disconnect RSVLT_WIND2134.500 (527659) 34.5 kV bus b. 47. Disconnect RSVLT_COL1 (527660) 34.5 kV bus b. 48. Disconnect RSVLT_COL2 (527661) 34.5 kV bus b. 49. Disconnect RSVLT_TR1 (527662) 13.2 kV bus b. 50. Disconnect RSVLT_TR2 (527663) 13.2 kV bus b. 51. Disconnect RSVLT_COL1 (527666) 345.0 kV bus b. 52. Disconnect RSVLT_COL2 (527667) 345.0 kV bus b. 53. Disconnect MILO_CB (577120) 34.5 kV bus b. 54. Disconnect MILO_WND (577121) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527656_CROSSROADS-ConID-SPS-110 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345.0 kV bus a.Apply single-phase fault on CROSSROADS (527656) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from CROSSROADS (527656) 345.0 kV bus to TOLK (525549) 345.0 kV bus CKT 1 b. 2. Open branch from CROSSROADS (527656) 345.0 kV bus to SAGA_SCOL (527610) 345.0 kV bus CKT 1 b. 3. Disconnect SAGSFT3_2.210.7000 (527605) 0.7 kV bus b. 4. Disconnect GRDXFR4 (527606) 0.5 kV bus b. 5. Disconnect SAGSFT4_2.210.7000 (527607) 0.7 kV bus b. 6. Disconnect SUB (527608) 34.5 kV bus b. 7. Disconnect SUB (527609) 34.5 kV bus b. 8. Disconnect GRDXFR1 (527613) 0.5 kV bus b. 9. Disconnect SAGSFT1_2.210.7000 (527614) 0.7 kV bus b. 10. Disconnect SAGSFT1_2.010.7000 (527615) 0.7 kV bus b. 11. Disconnect GRDXFR2 (527616) 0.5 kV bus b. 12. Disconnect SAGSFT2_2.210.7000 (527617) 0.7 kV bus b. 13. Disconnect SAGSFT2_2.010.7000 (527618) 0.7 kV bus b. 14. Clear fault from CROSSROADS (527656) b. 15. Drop load from SAGA_SCOL (527610 ID 1) 345.0 kV bus b. 16. Drop load from SAGA_SCOL (527610 ID 2) 345.0 kV bus b. 17. Disconnect SAGA_NDCOL (527598) 345.0 kV bus b. 18. Disconnect SAGA_SDCOL (527599) 345.0 kV bus b. 19. Disconnect SAGA_SMEAS (527600) 345.0 kV bus b. 20. Disconnect SAGA_NCOL (527601) 345.0 kV bus b. 21. Disconnect SAGANCOL1 (527602) 34.5 kV bus b. 22. Disconnect SAGANCOL2 (527603) 34.5 kV bus b. 23. Disconnect GRDXFR3 (527604) 0.5 kV bus b. 24. Disconnect SAGA_SCOL (527610) 345.0 kV bus b. 25. Disconnect SAGASCOL1 (527611) 34.5 kV bus b. 26. Disconnect SAGASCOL2 (527612) 34.5 kV bus b. 27. Disconnect SAGA_NCLTR3113.8 kV bus b. 28. Disconnect SAGA_NCLTR4113.8 kV bus b. 29. Disconnect SAGA_SCLTR1113.8 kV bus b. 30. Disconnect SAGA_SCLTR2113.8 kV bus b. 31. Disconnect SUB (527628) 34.5 kV bus b. 32. Disconnect SUB (527629) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-114 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Disconnect EDDY_TR (527796) 13.2 kV bus b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-115 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 6. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527802_EDDY_CNTY-ConID-SPS-116 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345.0 kV bus a.Apply single-phase fault on EDDY_CNTY (527802) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect EDDY_TR (527796) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from EDDY_CNTY (527802) 345.0 kV bus to CROSSROADS (527656) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from EDDY_CNTY (527802) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect EDDY_TR (527796) 13.2 kV bus b. 5. Disconnect EDDY_TR (527796) 13.2 kV bus b. 6. Disconnect EDDY_CNTY (527802) 345.0 kV bus b. 7. Clear fault from EDDY_CNTY (527802) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527896_HOBBS_INT-ConID-SPS-119 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345.0 kV bus a.Apply single-phase fault on HOBBS_INT (527896) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from HOBBS_INT (527896) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 2. Open branch from HOBBS_INT (527896) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Disconnect HOBBS_TR3 (527895) 13.2 kV bus b. 4. Disconnect HOBBS_INT (527896) 345.0 kV bus b. 5. Clear fault from HOBBS_INT (527896) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527965_KIOWA-ConID-SPS-120 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b.Run for 16.0 cycles and trip the following elements: b. 2. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 5. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-527965_KIOWA-ConID-SPS-121 | Single Phase Fault with Stuck Breaker on KIOWA (527965) 345.0 kV bus a.Apply single-phase fault on KIOWA (527965) 345.0 kV bus b.Run for 20.0 cycles and trip the following elements: b. 1. Open branch from KIOWA (527965) 345.0 kV bus to RDRUNNER (528027) 345.0 kV bus CKT 1 b. 2. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 3. Disconnect KIOWA_TR1 (527964) 13.2 kV bus b. 4. Clear fault from KIOWA (527965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-126 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-127 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 6. Disconnect RDRUNNER (528027) 345.0 kV bus b. 7. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528027_RDRUNNER-ConID-SPS-128 | Single Phase Fault with Stuck Breaker on RDRUNNER (528027) 345.0 kV bus a.Apply single-phase fault on RDRUNNER (528027) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from RDRUNNER (528027) 345.0 kV bus to PHANTOM (528015) 345.0 kV bus CKT 1 b. 3. Open branch from RDRUNNER (528027) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect RDRNNER_TR1113.200 (528023) 13.2 kV bus b. 5. Disconnect RDRUNNER (528027) 345.0 kV bus b. 6. Clear fault from RDRUNNER (528027) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-122 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 3. Disconnect N_LOVING (528186) 13.2 kV bus b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-123 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528186) 13.2 kV bus b. 6. Disconnect N_LOVING (528185) 345.0 kV bus b. 7. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2018-002 / DISIS-2019-001 CF | 25W | Transfer | P4_TO-528185_N_LOVING-ConID-SPS-124 | Single Phase Fault with Stuck Breaker on N_LOVING (528185) 345.0 kV bus a.Apply single-phase fault on N_LOVING (528185) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect N_LOVING (528186) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from N_LOVING (528185) 345.0 kV bus to CHINA_DRAW (528223) 345.0 kV bus CKT 1 b. 3. Open branch from N_LOVING (528185) 345.0 kV bus to KIOWA (527965) 345.0 kV bus CKT 1 b. 4. Disconnect N_LOVING (528186) 13.2 kV bus b. 5. Disconnect N_LOVING (528185) 345.0 kV bus b. 6. Clear fault from N_LOVING (528185) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2018-067 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.7183 | 6.7532 | 0.0349
GEN-2018-067 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.2877 | 18.8995 | 0.6118
GEN-2018-067 | 01 NORTH | 652400 | WILISTN4 | 230 | 11 | 11.2308 | 0.2308
GEN-2018-067 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.6119 | 8.6335 | 0.0216
GEN-2018-067 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.2811 | 18.8903 | 0.6092
GEN-2018-067 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0356 | 5.0501 | 0.0145
GEN-2018-067 | 01 NORTH | 655776 | ALKABO -SH7 | 115 | 2.2789 | 2.3564 | 0.0775
GEN-2018-067 | 01 NORTH | 655777 | FORTUNA -SH7 | 115 | 1.8105 | 1.8591 | 0.0486
GEN-2018-067 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 5.4108 | 5.5618 | 0.151
GEN-2018-067 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 3.6986 | 3.7684 | 0.0698
GEN-2018-067 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.2412 | 1.242 | 0.0008
GEN-2018-067 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7354 | 5.7451 | 0.0097
GEN-2018-067 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.985 | 1.9873 | 0.0023
GEN-2018-067 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5699 | 3.5772 | 0.0073
GEN-2018-067 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 5.9678 | 6.0304 | 0.0626
GEN-2018-067 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.6119 | 8.6335 | 0.0216
GEN-2018-067 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.6974 | 6.7054 | 0.008
GEN-2018-067 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6291 | 4.6353 | 0.0062
GEN-2018-067 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.7689 | 4.7755 | 0.0066
GEN-2018-067 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.2848 | 8.3048 | 0.02
GEN-2018-067 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.2244 | 5.2323 | 0.0079
GEN-2018-067 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9004 | 3.9048 | 0.0044
GEN-2018-067 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.6643 | 4.6707 | 0.0064
GEN-2018-067 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.2715 | 4.2768 | 0.0053
GEN-2018-067 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.0987 | 3.1015 | 0.0028
GEN-2018-067 | 01 NORTH | 655915 | BARRBUTE-MW7 | 115 | 4.8577 | 5.2437 | 0.386
GEN-2018-067 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 14.4266 | 14.9103 | 0.4837
GEN-2018-067 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 14.5282 | 14.9241 | 0.3959
GEN-2018-067 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.4301 | 8.5617 | 0.1316
GEN-2018-067 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 9.397 | 10.0103 | 0.6133
GEN-2018-067 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 14.124 | 14.7178 | 0.5938
GEN-2018-067 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 13.0976 | 13.5427 | 0.4451
GEN-2018-067 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 11.7866 | 12.1155 | 0.3289
GEN-2018-067 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 12.819 | 13.2439 | 0.4249
GEN-2018-067 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 12.0153 | 12.3816 | 0.3663
GEN-2018-067 | 01 NORTH | 655940 | MONT -MW7 | 115 | 14.3461 | 15.2442 | 0.8981
GEN-2018-067 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 8.0195 | 9.5946 | 1.5751
GEN-2018-067 | 01 NORTH | 655954 | ELLISVIL-MW7 | 115 | 6.1674 | 6.3143 | 0.1469
GEN-2018-067 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 7.2925 | 7.599 | 0.3065
GEN-2018-067 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 11 | 11.5356 | 0.5356
GEN-2018-067 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 16.0038 | 16.6894 | 0.6856
GEN-2018-067 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 13.0643 | 13.5129 | 0.4486
GEN-2018-067 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.7621 | 6.8852 | 0.1231
GEN-2018-067 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 4.4571 | 4.4642 | 0.0071
GEN-2018-067 | 01 NORTH | 659145 | GRENORA_-UM7 | 115 | 4.6925 | 5.0334 | 0.3409
GEN-2018-067 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.7762 | 5.786 | 0.0098
GEN-2018-067 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.5044 | 6.5093 | 0.0049
GEN-2018-067 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.7876 | 5.801 | 0.0134
GEN-2018-067 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.6742 | 5.6849 | 0.0107
GEN-2018-067 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3591 | 11.4121 | 0.053
GEN-2018-067 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 8.2523 | 8.4176 | 0.1653
GEN-2018-067 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 10.939 | 11.16 | 0.221
GEN-2018-067 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.4993 | 6.5042 | 0.0049
GEN-2018-067 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 14.4266 | 14.9103 | 0.4837
GEN-2018-067 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.5274 | 7.6254 | 0.098
GEN-2018-067 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.1162 | 9.2676 | 0.1514
GEN-2018-067 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.17 | 8.2708 | 0.1008
GEN-2018-067 | 01 NORTH | 659430 | PIONEER2-BE7 | 115 | 13.7342 | 14.1747 | 0.4405
GEN-2018-067 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 7.5494 | 7.7315 | 0.1821
GEN-2018-067 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.6491 | 6.6834 | 0.0343
GEN-2018-067 | 01 NORTH | 661077 | PLNTYWD7 | 115 | 1.7504 | 1.7957 | 0.0453
GEN-2018-067 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 11.8926 | 12.0275 | 0.1349
GEN-2018-067 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 9.7369 | 9.8023 | 0.0654
GEN-2018-067 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.7123 | 5.7433 | 0.031
GEN-2018-067 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 6.9193 | 6.9883 | 0.069
GEN-2018-067 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 8.0195 | 9.5946 | 1.5751
GEN-2018-069 | 01 NORTH | 588550 | GEN-2017-010 | 230 | 4.4674 | 4.4944 | 0.027
GEN-2018-069 | 01 NORTH | 652200 | GLENDIVE7 | 115 | 7.0983 | 7.2403 | 0.142
GEN-2018-069 | 01 NORTH | 652212 | GLENDIVEP2T7 | 115 | 4.324 | 4.3802 | 0.0562
GEN-2018-069 | 01 NORTH | 652213 | FALLON 8 | 69 | 1.084 | 1.086 | 0.002
GEN-2018-069 | 01 NORTH | 652394 | TERRY TAP | 115 | 2.8984 | 2.9213 | 0.0229
GEN-2018-069 | 01 NORTH | 652395 | SHIRLEY TAP | 115 | 3.039 | 3.0625 | 0.0235
GEN-2018-069 | 01 NORTH | 652401 | CIRCLE 7 | 115 | 2.1956 | 2.2055 | 0.0099
GEN-2018-069 | 01 NORTH | 652403 | DAWSONC4 | 230 | 4.3042 | 4.4878 | 0.1836
GEN-2018-069 | 01 NORTH | 652404 | DAWSONC7 | 115 | 7.8432 | 8.0373 | 0.1941
GEN-2018-069 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.1652 | 2.1847 | 0.0195
GEN-2018-069 | 01 NORTH | 652406 | FTPECK 7 | 115 | 2.9913 | 3.0059 | 0.0146
GEN-2018-069 | 01 NORTH | 652407 | FALLON 7 | 115 | 3.1958 | 3.225 | 0.0292
GEN-2018-069 | 01 NORTH | 652409 | WOLFPT 7 | 115 | 2.9822 | 2.994 | 0.0118
GEN-2018-069 | 01 NORTH | 652411 | MI CTYE4 | 230 | 2.8323 | 2.8745 | 0.0422
GEN-2018-069 | 01 NORTH | 652412 | MI CTYE7 | 115 | 3.8688 | 3.9048 | 0.036
GEN-2018-069 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.7379 | 6.7953 | 0.0574
GEN-2018-069 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.5115 | 9.6412 | 0.1297
GEN-2018-069 | 01 NORTH | 652468 | HEBRON 4 | 230 | 5.7865 | 5.7996 | 0.0131
GEN-2018-069 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 4.1679 | 4.5412 | 0.3733
GEN-2018-069 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0453 | 5.0501 | 0.0048
GEN-2018-069 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7356 | 5.7451 | 0.0095
GEN-2018-069 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9865 | 1.9873 | 0.0008
GEN-2018-069 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5747 | 3.5772 | 0.0025
GEN-2018-069 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1533 | 4.1546 | 0.0013
GEN-2018-069 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 13.8175 | 13.8395 | 0.022
GEN-2018-069 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.8714 | 6.8769 | 0.0055
GEN-2018-069 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1074 | 3.1081 | 0.0007
GEN-2018-069 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.4902 | 5.4925 | 0.0023
GEN-2018-069 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.0495 | 4.0503 | 0.0008
GEN-2018-069 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2577 | 3.2583 | 0.0006
GEN-2018-069 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.2153 | 5.2168 | 0.0015
GEN-2018-069 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.1508 | 4.1518 | 0.001
GEN-2018-069 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4581 | 3.4588 | 0.0007
GEN-2018-069 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9005 | 2.9011 | 0.0006
GEN-2018-069 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5451 | 3.546 | 0.0009
GEN-2018-069 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.2479 | 8.2529 | 0.005
GEN-2018-069 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.4579 | 6.4602 | 0.0023
GEN-2018-069 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3141 | 2.3144 | 0.0003
GEN-2018-069 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1205 | 3.121 | 0.0005
GEN-2018-069 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.9807 | 2.9811 | 0.0004
GEN-2018-069 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7486 | 2.749 | 0.0004
GEN-2018-069 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6488 | 2.6492 | 0.0004
GEN-2018-069 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.904 | 3.9048 | 0.0008
GEN-2018-069 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4362 | 3.4369 | 0.0007
GEN-2018-069 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.2002 | 6.2023 | 0.0021
GEN-2018-069 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9965 | 3.9974 | 0.0009
GEN-2018-069 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.1911 | 6.1939 | 0.0028
GEN-2018-069 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5262 | 3.5272 | 0.001
GEN-2018-069 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 16.2286 | 16.2445 | 0.0159
GEN-2018-069 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.1684 | 7.2166 | 0.0482
GEN-2018-069 | 01 NORTH | 659125 | DICKINSN-BE7 | 115 | 9.4385 | 9.475 | 0.0365
GEN-2018-069 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.7764 | 5.786 | 0.0096
GEN-2018-069 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.9351 | 13.9575 | 0.0224
GEN-2018-069 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.424 | 10.4624 | 0.0384
GEN-2018-069 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7206 | 3.7222 | 0.0016
GEN-2018-069 | 01 NORTH | 659186 | E.SIDNEY-LY7 | 115 | 4.2895 | 4.2943 | 0.0048
GEN-2018-069 | 01 NORTH | 659195 | DICKINS2-BE7 | 115 | 9.4028 | 9.4389 | 0.0361
GEN-2018-069 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.5101 | 15.5246 | 0.0145
GEN-2018-069 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 16.2286 | 16.2445 | 0.0159
GEN-2018-069 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.6372 | 9.6383 | 0.0011
GEN-2018-069 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.232 | 7.2341 | 0.0021
GEN-2018-069 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.27 | 7.2707 | 0.0007
GEN-2018-069 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.306 | 5.4613 | 0.1553
GEN-2018-069 | 01 NORTH | 659259 | HEADRESS-CM7 | 115 | 2.976 | 2.9876 | 0.0116
GEN-2018-069 | 01 NORTH | 659263 | LITTL_MS-BE7 | 115 | 3.0209 | 3.0301 | 0.0092
GEN-2018-069 | 01 NORTH | 659265 | LITTL_MS-BE4 | 230 | 3.5535 | 3.579 | 0.0255
GEN-2018-069 | 01 NORTH | 659266 | RHAME___-BE4 | 230 | 4.5451 | 4.5731 | 0.028
GEN-2018-069 | 01 NORTH | 659267 | RHAME___-BE7 | 115 | 2.0361 | 2.0388 | 0.0027
GEN-2018-069 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3839 | 11.4121 | 0.0282
GEN-2018-069 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3046 | 2.3084 | 0.0038
GEN-2018-069 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.5115 | 9.6412 | 0.1297
GEN-2018-069 | 01 NORTH | 659339 | BOWMAN__-BE4 | 230 | 3.84 | 3.8564 | 0.0164
GEN-2018-069 | 01 NORTH | 659340 | BOWMAN__-BE7 | 115 | 3.5124 | 3.5192 | 0.0068
GEN-2018-069 | 01 NORTH | 659341 | NBURR___-GE7 | 115 | 1.8203 | 1.8222 | 0.0019
GEN-2018-069 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.1704 | 12.1759 | 0.0055
GEN-2018-069 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.1705 | 12.176 | 0.0055
GEN-2018-069 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.3897 | 9.4095 | 0.0198
GEN-2018-069 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.7592 | 11.7695 | 0.0103
GEN-2018-069 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.7269 | 8.7413 | 0.0144
GEN-2018-069 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 17.7945 | 17.8114 | 0.0169
GEN-2018-069 | 01 NORTH | 659400 | ND.SUN._-PP4 | 230 | 5.2419 | 5.2524 | 0.0105
GEN-2018-069 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9322 | 1.9348 | 0.0026
GEN-2018-069 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7389 | 1.741 | 0.0021
GEN-2018-069 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.5637 | 6.6188 | 0.0551
GEN-2018-069 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6148 | 3.6271 | 0.0123
GEN-2018-069 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 17.6983 | 17.7151 | 0.0168
GEN-2018-069 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 17.7097 | 17.7266 | 0.0169
GEN-2018-069 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 4.1679 | 4.5412 | 0.3733
GEN-2018-069 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.5461 | 3.6741 | 0.128
GEN-2018-069 | 01 NORTH | 659542 | REDWATER-MC7 | 115 | 2.1956 | 2.2055 | 0.0099
GEN-2018-069 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9322 | 1.9348 | 0.0026
GEN-2018-069 | 01 NORTH | 659550 | LNGBUTTE-RR4 | 230 | 5.6461 | 5.6586 | 0.0125
GEN-2018-069 | 01 NORTH | 659551 | LNGBUTTE-RR7 | 115 | 3.5361 | 3.5385 | 0.0024
GEN-2018-069 | 01 NORTH | 659553 | RAIDER__-RR7 | 115 | 2.3901 | 2.3913 | 0.0012
GEN-2018-069 | 01 NORTH | 659554 | REDTRAIL-RR7 | 115 | 2.3667 | 2.3678 | 0.0011
GEN-2018-069 | 01 NORTH | 659555 | RICHRDTN-RR7 | 115 | 2.1902 | 2.1911 | 0.0009
GEN-2018-069 | 01 NORTH | 661004 | BAKER 4 | 230 | 3.3179 | 3.3447 | 0.0268
GEN-2018-069 | 01 NORTH | 661005 | BAKER 7 | 115 | 3.5486 | 3.566 | 0.0174
GEN-2018-069 | 01 NORTH | 661010 | MILESCITYSW7 | 115 | 1.0262 | 1.0277 | 0.0015
GEN-2018-069 | 01 NORTH | 661019 | MATHSON7 | 115 | 8.3701 | 8.3978 | 0.0277
GEN-2018-069 | 01 NORTH | 661024 | WDICKSN7 | 115 | 6.6819 | 6.6996 | 0.0177
GEN-2018-069 | 01 NORTH | 661032 | GLENDCT7 | 115 | 6.4577 | 6.5561 | 0.0984
GEN-2018-069 | 01 NORTH | 661033 | CABINCR7 | 115 | 3.1838 | 3.2007 | 0.0169
GEN-2018-069 | 01 NORTH | 661034 | KEYXLPS14 7 | 115 | 3.258 | 3.2742 | 0.0162
GEN-2018-069 | 01 NORTH | 661053 | MANDAN 4 | 230 | 16.3967 | 16.4017 | 0.005
GEN-2018-069 | 01 NORTH | 661056 | LEWIS 7 | 115 | 5.8399 | 5.8509 | 0.011
GEN-2018-069 | 01 NORTH | 661070 | N ENGLN7 | 115 | 3.8239 | 3.8296 | 0.0057
GEN-2018-069 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 4.0931 | 4.4691 | 0.376
GEN-2018-074 | 01 NORTH | 45906 | J1590 SUB | 345 | 14.7932 | 14.7962 | 0.003
GEN-2018-074 | 01 NORTH | 87486 | J748GENTIE | 345 | 13.783 | 13.7855 | 0.0025
GEN-2018-074 | 01 NORTH | 87487 | J748POI | 345 | 15.6161 | 15.6193 | 0.0032
GEN-2018-074 | 01 NORTH | 300097 | 5MARYVB2 | 161 | 9.7411 | 9.7414 | 0.0003
GEN-2018-074 | 01 NORTH | 301556 | 5CLEARCK | 161 | 6.9794 | 6.9796 | 0.0002
GEN-2018-074 | 01 NORTH | 587760 | GEN-2016-094 | 230 | 8.9364 | 8.9364 | 0
GEN-2018-074 | 01 NORTH | 588590 | GEN-2017-014 | 230 | 4.5024 | 4.5024 | 0
GEN-2018-074 | 01 NORTH | 589320 | GEN-2017-094 | 230 | 6.4209 | 6.4209 | 0
GEN-2018-074 | 01 NORTH | 589324 | G17-094-TAP | 230 | 7.9611 | 7.9612 | 0.0001
GEN-2018-074 | 01 NORTH | 601006 | SPLT RK3 | 345 | 15.6193 | 15.622 | 0.0027
GEN-2018-074 | 01 NORTH | 628909 | HD HV 5 | 161 | 3 | 3.0025 | 0.0025
GEN-2018-074 | 01 NORTH | 628910 | HD WIND 5 | 161 | 5.5249 | 5.5331 | 0.0082
GEN-2018-074 | 01 NORTH | 630009 | ANITA 8 | 69 | 7.8272 | 7.835 | 0.0078
GEN-2018-074 | 01 NORTH | 630028 | EVERLYN8 | 69 | 7.4652 | 7.4654 | 0.0002
GEN-2018-074 | 01 NORTH | 631069 | ANTA TP5 | 161 | 7.4508 | 7.4726 | 0.0218
GEN-2018-074 | 01 NORTH | 631070 | ANITA 5 | 161 | 6.6395 | 6.6547 | 0.0152
GEN-2018-074 | 01 NORTH | 631164 | G298_WF5 | 161 | 10.3049 | 10.3053 | 0.0004
GEN-2018-074 | 01 NORTH | 631183 | CAYLER5 | 161 | 10.3456 | 10.3459 | 0.0003
GEN-2018-074 | 01 NORTH | 635056 | ADAMS 5 | 161 | 6.0063 | 6.0071 | 0.0008
GEN-2018-074 | 01 NORTH | 635200 | RAUN 3 | 345 | 27.3765 | 27.3961 | 0.0196
GEN-2018-074 | 01 NORTH | 635201 | RAUN 5 | 161 | 27.9004 | 27.9202 | 0.0198
GEN-2018-074 | 01 NORTH | 635221 | KELLOGG5 | 161 | 17.7421 | 17.7543 | 0.0122
GEN-2018-074 | 01 NORTH | 635223 | PLYMOTH5 | 161 | 21.1038 | 21.1318 | 0.028
GEN-2018-074 | 01 NORTH | 635224 | PLYMOTH8 | 69 | 22.3033 | 22.3164 | 0.0131
GEN-2018-074 | 01 NORTH | 635225 | MORNSD 5 | 161 | 11.2868 | 11.2931 | 0.0063
GEN-2018-074 | 01 NORTH | 635226 | LEEDS 5 | 161 | 16.4232 | 16.4359 | 0.0127
GEN-2018-074 | 01 NORTH | 635235 | SALIX 5 | 161 | 15.1796 | 15.188 | 0.0084
GEN-2018-074 | 01 NORTH | 635248 | JAMES 8 | 69 | 14.378 | 14.3831 | 0.0051
GEN-2018-074 | 01 NORTH | 635252 | J412 POI 3 | 345 | 10.0705 | 10.0719 | 0.0014
GEN-2018-074 | 01 NORTH | 635260 | LEMARST5 | 161 | 10.2104 | 10.2163 | 0.0059
GEN-2018-074 | 01 NORTH | 635261 | LEMARS S 5 | 161 | 6.1669 | 6.1691 | 0.0022
GEN-2018-074 | 01 NORTH | 635265 | LEMARSINDT 8 | 69 | 7.811 | 7.8125 | 0.0015
GEN-2018-074 | 01 NORTH | 635280 | BVISTA 5 | 161 | 8.583 | 8.5837 | 0.0007
GEN-2018-074 | 01 NORTH | 635322 | CAROL S8 | 69 | 8.1104 | 8.1147 | 0.0043
GEN-2018-074 | 01 NORTH | 635325 | TEMPLTN8 | 69 | 6.4543 | 6.4607 | 0.0064
GEN-2018-074 | 01 NORTH | 635360 | LTL SIOUX 5 | 161 | 6.8349 | 6.8366 | 0.0017
GEN-2018-074 | 01 NORTH | 635385 | HUDSON 8 | 69 | 6.3149 | 6.3157 | 0.0008
GEN-2018-074 | 01 NORTH | 635386 | SXRIVER8 | 69 | 3.4312 | 3.4314 | 0.0002
GEN-2018-074 | 01 NORTH | 635387 | ALCESTR8 | 69 | 1.6731 | 1.6731 | 0
GEN-2018-074 | 01 NORTH | 635390 | IRETON 8 | 69 | 2.9106 | 2.9108 | 0.0002
GEN-2018-074 | 01 NORTH | 635391 | IRETONT8 | 69 | 6.1419 | 6.1426 | 0.0007
GEN-2018-074 | 01 NORTH | 635392 | CRAIG 8 | 69 | 1.9999 | 2 | 0.0001
GEN-2018-074 | 01 NORTH | 635393 | MERRIL 8 | 69 | 6.1255 | 6.1264 | 0.0009
GEN-2018-074 | 01 NORTH | 635398 | REMSEN 3 | 345 | 15.0224 | 15.0256 | 0.0032
GEN-2018-074 | 01 NORTH | 635421 | TEMPLTNCAWF8 | 69 | 6.4543 | 6.4607 | 0.0064
GEN-2018-074 | 01 NORTH | 635645 | MCKSBRG 5 | 161 | 8.3394 | 8.341 | 0.0016
GEN-2018-074 | 01 NORTH | 640070 | BANCRFT7 | 115 | 5.2126 | 5.213 | 0.0004
GEN-2018-074 | 01 NORTH | 640080 | BELDEN 7 | 115 | 6.1764 | 6.1769 | 0.0005
GEN-2018-074 | 01 NORTH | 640081 | BELDEN 8 | 69 | 3.8621 | 3.8622 | 0.0001
GEN-2018-074 | 01 NORTH | 640126 | E.COL. 4 | 230 | 10.2829 | 10.2833 | 0.0004
GEN-2018-074 | 01 NORTH | 640131 | COLMB.W4 | 230 | 10.0538 | 10.0541 | 0.0003
GEN-2018-074 | 01 NORTH | 640133 | COLMBUS4 | 230 | 11.6825 | 11.683 | 0.0005
GEN-2018-074 | 01 NORTH | 640134 | KELLY 7 | 115 | 18.1506 | 18.1511 | 0.0005
GEN-2018-074 | 01 NORTH | 640163 | EMERSON7 | 115 | 5.5898 | 5.5906 | 0.0008
GEN-2018-074 | 01 NORTH | 640164 | EMERSONG | 69 | 3.9043 | 3.9045 | 0.0002
GEN-2018-074 | 01 NORTH | 640212 | HARTGTN7 | 115 | 5.4041 | 5.4044 | 0.0003
GEN-2018-074 | 01 NORTH | 640213 | HARTGTN8 | 69 | 3.663 | 3.6631 | 0.0001
GEN-2018-074 | 01 NORTH | 640226 | HOSKINS3 | 345 | 11.528 | 11.5301 | 0.0021
GEN-2018-074 | 01 NORTH | 640227 | HOSKINS4 | 230 | 9.4633 | 9.465 | 0.0017
GEN-2018-074 | 01 NORTH | 640228 | HOSKINS7 | 115 | 17.6182 | 17.6203 | 0.0021
GEN-2018-074 | 01 NORTH | 640305 | ONEILL 7 | 115 | 4.024 | 4.0241 | 0.0001
GEN-2018-074 | 01 NORTH | 640306 | ONEILL 8 | 69 | 4.3769 | 4.3769 | 0
GEN-2018-074 | 01 NORTH | 640343 | SHELCRK4 | 230 | 11.0553 | 11.0557 | 0.0004
GEN-2018-074 | 01 NORTH | 640349 | SPENCER7 | 115 | 4.7258 | 4.7258 | 0
GEN-2018-074 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.3543 | 8.3602 | 0.0059
GEN-2018-074 | 01 NORTH | 640387 | TWIN CH7 | 115 | 10.6688 | 10.6728 | 0.004
GEN-2018-074 | 01 NORTH | 640388 | TWIN CH8 | 69 | 7.9632 | 7.9645 | 0.0013
GEN-2018-074 | 01 NORTH | 640424 | S.SIOUXCITY7 | 115 | 7.4284 | 7.4304 | 0.002
GEN-2018-074 | 01 NORTH | 640425 | S.SIOUXCITY8 | 69 | 4.651 | 4.6515 | 0.0005
GEN-2018-074 | 01 NORTH | 640540 | MEADOWGROVE4 | 230 | 5.1963 | 5.1964 | 0.0001
GEN-2018-074 | 01 NORTH | 640560 | WAKEFIELD 4 | 230 | 6.4436 | 6.4459 | 0.0023
GEN-2018-074 | 01 NORTH | 640561 | RTLSNAKE.W 4 | 230 | 5.4899 | 5.4916 | 0.0017
GEN-2018-074 | 01 NORTH | 640588 | TURTLE.CRK 3 | 345 | 9.7186 | 9.7201 | 0.0015
GEN-2018-074 | 01 NORTH | 640589 | SHOLES.W 3 | 345 | 8.0134 | 8.0144 | 0.001
GEN-2018-074 | 01 NORTH | 640598 | HAYSTACK.WD3 | 345 | 7.4446 | 7.4455 | 0.0009
GEN-2018-074 | 01 NORTH | 643271 | PLUMBCR.W 3 | 345 | 9.536 | 9.5375 | 0.0015
GEN-2018-074 | 01 NORTH | 648506 | PR BRZ 4 | 230 | 3.5578 | 3.5579 | 0.0001
GEN-2018-074 | 01 NORTH | 652249 | ARMOUR 8 | 69 | 2.5446 | 2.5446 | 0
GEN-2018-074 | 01 NORTH | 652251 | MTVERNS8 | 69 | 2.348 | 2.348 | 0
GEN-2018-074 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 3.7725 | 3.7725 | 0
GEN-2018-074 | 01 NORTH | 652284 | HURON 8 | 69 | 4.3958 | 4.3958 | 0
GEN-2018-074 | 01 NORTH | 652286 | TYNDALL8 | 69 | 2.6092 | 2.6092 | 0
GEN-2018-074 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.2632 | 7.264 | 0.0008
GEN-2018-074 | 01 NORTH | 652475 | BONESTL7 | 115 | 3.6345 | 3.6345 | 0
GEN-2018-074 | 01 NORTH | 652478 | GREGORY7 | 115 | 2.2248 | 2.2248 | 0
GEN-2018-074 | 01 NORTH | 652501 | ARMOUR 7 | 115 | 4.2976 | 4.2976 | 0
GEN-2018-074 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.0373 | 9.0374 | 0.0001
GEN-2018-074 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 19.2798 | 19.2803 | 0.0005
GEN-2018-074 | 01 NORTH | 652509 | FTRANDL4 | 230 | 10.9792 | 10.9804 | 0.0012
GEN-2018-074 | 01 NORTH | 652510 | FTRANDL7 | 115 | 12.7573 | 12.7579 | 0.0006
GEN-2018-074 | 01 NORTH | 652514 | HURON 4 | 230 | 11.3937 | 11.3937 | 0
GEN-2018-074 | 01 NORTH | 652515 | HURON 7 | 115 | 15.695 | 15.6951 | 0.0001
GEN-2018-074 | 01 NORTH | 652516 | NORTHBEND4 | 230 | 9.0858 | 9.0859 | 0.0001
GEN-2018-074 | 01 NORTH | 652518 | MTVERN 7 | 115 | 4.4034 | 4.4034 | 0
GEN-2018-074 | 01 NORTH | 652519 | OAHE 4 | 230 | 12.2746 | 12.2746 | 0
GEN-2018-074 | 01 NORTH | 652520 | OAHE 7 | 115 | 10.4791 | 10.4791 | 0
GEN-2018-074 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 14.009 | 14.0115 | 0.0025
GEN-2018-074 | 01 NORTH | 652525 | TYNDALL7 | 115 | 3.9256 | 3.9257 | 0.0001
GEN-2018-074 | 01 NORTH | 652526 | UTICAJC4 | 230 | 8.4789 | 8.4806 | 0.0017
GEN-2018-074 | 01 NORTH | 652530 | WATERTN4 | 230 | 15.1424 | 15.1425 | 0.0001
GEN-2018-074 | 01 NORTH | 652540 | BIGBND14 | 230 | 11.8239 | 11.824 | 0.0001
GEN-2018-074 | 01 NORTH | 652541 | BIGBND24 | 230 | 11.746 | 11.7461 | 0.0001
GEN-2018-074 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.5212 | 20.5851 | 0.0639
GEN-2018-074 | 01 NORTH | 652560 | CRESTON5 | 161 | 10.1156 | 10.1197 | 0.0041
GEN-2018-074 | 01 NORTH | 652561 | DENISON5 | 161 | 6.2869 | 6.474 | 0.1871
GEN-2018-074 | 01 NORTH | 652563 | SPENCER5 | 161 | 10.5218 | 10.5226 | 0.0008
GEN-2018-074 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.7496 | 15.7704 | 0.0208
GEN-2018-074 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.5212 | 20.5851 | 0.0639
GEN-2018-074 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 21.5671 | 21.5984 | 0.0313
GEN-2018-074 | 01 NORTH | 652567 | DENISON4 | 230 | 5.1855 | 5.4081 | 0.2226
GEN-2018-074 | 01 NORTH | 652569 | CRESTON8 | 69 | 16.7938 | 16.7974 | 0.0036
GEN-2018-074 | 01 NORTH | 652574 | SIOUXCY8 | 69 | 19.2973 | 19.3079 | 0.0106
GEN-2018-074 | 01 NORTH | 652581 | SPENCER8 | 69 | 15.7952 | 15.7957 | 0.0005
GEN-2018-074 | 01 NORTH | 652583 | DENISON8 | 69 | 12.4019 | 12.6434 | 0.2415
GEN-2018-074 | 01 NORTH | 652603 | EXIRA 5 | 161 | 7.4044 | 7.434 | 0.0296
GEN-2018-074 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.9351 | 4.9353 | 0.0002
GEN-2018-074 | 01 NORTH | 652607 | WESSINGTON 4 | 230 | 5.9635 | 5.9636 | 0.0001
GEN-2018-074 | 01 NORTH | 652609 | LETCHER7 | 115 | 6.296 | 6.2961 | 0.0001
GEN-2018-074 | 01 NORTH | 652614 | CARPENTER 4 | 230 | 7.1907 | 7.1907 | 0
GEN-2018-074 | 01 NORTH | 652626 | UTICAJC7 | 115 | 9.1139 | 9.1145 | 0.0006
GEN-2018-074 | 01 NORTH | 652630 | WATERTNCAP 4 | 230 | 14.9633 | 14.9633 | 0
GEN-2018-074 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 8.9731 | 8.9732 | 0.0001
GEN-2018-074 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 9.0373 | 9.0374 | 0.0001
GEN-2018-074 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.5673 | 15.5875 | 0.0202
GEN-2018-074 | 01 NORTH | 654454 | PRVLNG13 | 115 | 3.5392 | 3.5393 | 0.0001
GEN-2018-074 | 01 NORTH | 654455 | PRVLNG23 | 115 | 6.6422 | 6.6426 | 0.0004
GEN-2018-074 | 01 NORTH | 654457 | PRVLNG16 | 230 | 8.4251 | 8.4268 | 0.0017
GEN-2018-074 | 01 NORTH | 655031 | MOS-LTCH-ER8 | 69 | 1.5519 | 1.5519 | 0
GEN-2018-074 | 01 NORTH | 655032 | MOS-PLNO-ER8 | 69 | 1.0182 | 1.0182 | 0
GEN-2018-074 | 01 NORTH | 655033 | SW-EMERY-ER8 | 69 | 0.8134 | 0.8134 | 0
GEN-2018-074 | 01 NORTH | 655053 | MOS-MILR-ER8 | 69 | 2.7087 | 2.7087 | 0
GEN-2018-074 | 01 NORTH | 655055 | SW-YALE-ER8 | 69 | 1.2786 | 1.2786 | 0
GEN-2018-074 | 01 NORTH | 655056 | SW-WILLO-ER8 | 69 | 1.6329 | 1.6329 | 0
GEN-2018-074 | 01 NORTH | 655058 | MOS-HRON-ER8 | 69 | 3.3742 | 3.3742 | 0
GEN-2018-074 | 01 NORTH | 655060 | MOS-POLO-ER8 | 69 | 1.0527 | 1.0527 | 0
GEN-2018-074 | 01 NORTH | 655062 | MOS-YALE-ER8 | 69 | 1.5332 | 1.5332 | 0
GEN-2018-074 | 01 NORTH | 655063 | SW-HURN1-ER8 | 69 | 4.3424 | 4.3424 | 0
GEN-2018-074 | 01 NORTH | 655064 | SW-HURN4-ER8 | 69 | 4.2884 | 4.2884 | 0
GEN-2018-074 | 01 NORTH | 655065 | MOS-YLTI-ER8 | 69 | 1.7989 | 1.7989 | 0
GEN-2018-074 | 01 NORTH | 655066 | SW-HURN2-ER8 | 69 | 4.3742 | 4.3742 | 0
GEN-2018-074 | 01 NORTH | 655067 | SW-HURN3-ER8 | 69 | 4.3797 | 4.3797 | 0
GEN-2018-074 | 01 NORTH | 655069 | MOS-WOLS-ER8 | 69 | 2.9222 | 2.9222 | 0
GEN-2018-074 | 01 NORTH | 655070 | MOS-VRCV-ER8 | 69 | 1.4251 | 1.4251 | 0
GEN-2018-074 | 01 NORTH | 655071 | MOS-DAK-ER8 | 69 | 1.1913 | 1.1913 | 0
GEN-2018-074 | 01 NORTH | 655073 | MOS-CRPN-ER8 | 69 | 2.5522 | 2.5522 | 0
GEN-2018-074 | 01 NORTH | 655074 | SW401-ER8 | 69 | 1.529 | 1.529 | 0
GEN-2018-074 | 01 NORTH | 655075 | MOS-WHTL-ER8 | 69 | 1.0058 | 1.0058 | 0
GEN-2018-074 | 01 NORTH | 655076 | MOS-PLAT-ER8 | 69 | 1.4985 | 1.4985 | 0
GEN-2018-074 | 01 NORTH | 655077 | SW-STORL-ER8 | 69 | 1.8772 | 1.8772 | 0
GEN-2018-074 | 01 NORTH | 655078 | SW412-ER8 | 69 | 0.8275 | 0.8275 | 0
GEN-2018-074 | 01 NORTH | 655079 | MOS-KLKP-ER8 | 69 | 0.8058 | 0.8058 | 0
GEN-2018-074 | 01 NORTH | 655080 | MOS-HLTP-ER8 | 69 | 1.3696 | 1.3696 | 0
GEN-2018-074 | 01 NORTH | 655081 | MOS-KMBL-ER8 | 69 | 0.7457 | 0.7457 | 0
GEN-2018-074 | 01 NORTH | 655091 | MOS-AMR1-ER8 | 69 | 2.2538 | 2.2538 | 0
GEN-2018-074 | 01 NORTH | 655092 | MOS-TRIP-ER8 | 69 | 2.1456 | 2.1456 | 0
GEN-2018-074 | 01 NORTH | 655093 | SW-HARSN-ER8 | 69 | 1.0886 | 1.0886 | 0
GEN-2018-074 | 01 NORTH | 655094 | MOS-PRKS-ER8 | 69 | 1.5902 | 1.5902 | 0
GEN-2018-074 | 01 NORTH | 655095 | MOS-TABR-ER8 | 69 | 1.8155 | 1.8155 | 0
GEN-2018-074 | 01 NORTH | 655096 | SW-TRIPP-ER8 | 69 | 1.2124 | 1.2124 | 0
GEN-2018-074 | 01 NORTH | 655097 | SW616-ER8 | 69 | 1.4656 | 1.4656 | 0
GEN-2018-074 | 01 NORTH | 655098 | SW-GEDES-ER8 | 69 | 1.3708 | 1.3708 | 0
GEN-2018-074 | 01 NORTH | 655099 | SW-HILLS-ER8 | 69 | 1.2521 | 1.2521 | 0
GEN-2018-074 | 01 NORTH | 655100 | MOS-WVLN-ER8 | 69 | 1.3594 | 1.3594 | 0
GEN-2018-074 | 01 NORTH | 655101 | MOS-TND1-ER8 | 69 | 2.6062 | 2.6063 | 0.0001
GEN-2018-074 | 01 NORTH | 655102 | MOS-AVON-ER8 | 69 | 2.5951 | 2.5951 | 0
GEN-2018-074 | 01 NORTH | 655103 | PARKSTON-ER8 | 69 | 0.9797 | 0.9797 | 0
GEN-2018-074 | 01 NORTH | 655104 | MOS-NTRP-ER8 | 69 | 1.2258 | 1.2258 | 0
GEN-2018-074 | 01 NORTH | 655106 | SW640-ER8 | 69 | 0.7917 | 0.7917 | 0
GEN-2018-074 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 2.0225 | 2.0226 | 0.0001
GEN-2018-074 | 01 NORTH | 655129 | SW806-ER8 | 69 | 0.8791 | 0.8791 | 0
GEN-2018-074 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.5421 | 2.5423 | 0.0002
GEN-2018-074 | 01 NORTH | 655133 | SW822-ER8 | 69 | 2.1967 | 2.1968 | 0.0001
GEN-2018-074 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.6246 | 2.6248 | 0.0002
GEN-2018-074 | 01 NORTH | 655137 | SW833-ER8 | 69 | 2.0954 | 2.0955 | 0.0001
GEN-2018-074 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.8906 | 2.8908 | 0.0002
GEN-2018-074 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.8893 | 2.8895 | 0.0002
GEN-2018-074 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.5428 | 2.543 | 0.0002
GEN-2018-074 | 01 NORTH | 655151 | MOS-BGSP-ER8 | 69 | 1.3653 | 1.3653 | 0
GEN-2018-074 | 01 NORTH | 655152 | SW894-ER8 | 69 | 2.0683 | 2.0684 | 0.0001
GEN-2018-074 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 3.6998 | 3.6998 | 0
GEN-2018-074 | 01 NORTH | 655155 | MOS-SLY1-ER8 | 69 | 2.453 | 2.453 | 0
GEN-2018-074 | 01 NORTH | 655158 | MOS-HYDE-ER8 | 69 | 2.2112 | 2.2112 | 0
GEN-2018-074 | 01 NORTH | 655183 | MITCHELL-ER8 | 69 | 1.2222 | 1.2222 | 0
GEN-2018-074 | 01 NORTH | 655189 | FARMER-ER8 | 69 | 0.8309 | 0.8309 | 0
GEN-2018-074 | 01 NORTH | 655193 | MTVERNON-ER8 | 69 | 1.8653 | 1.8653 | 0
GEN-2018-074 | 01 NORTH | 655205 | PLANO-ER8 | 69 | 0.8665 | 0.8665 | 0
GEN-2018-074 | 01 NORTH | 655206 | EMERY-ER8 | 69 | 0.7256 | 0.7256 | 0
GEN-2018-074 | 01 NORTH | 655211 | DESMET-ER8 | 69 | 1.0996 | 1.0996 | 0
GEN-2018-074 | 01 NORTH | 655228 | YALE-ER8 | 69 | 1.2583 | 1.2583 | 0
GEN-2018-074 | 01 NORTH | 655229 | WILLOWLK-ER8 | 69 | 1.1936 | 1.1936 | 0
GEN-2018-074 | 01 NORTH | 655231 | HURON-ER8 | 69 | 3.3695 | 3.3695 | 0
GEN-2018-074 | 01 NORTH | 655233 | POLO-ER8 | 69 | 0.6609 | 0.6609 | 0
GEN-2018-074 | 01 NORTH | 655234 | MILLER-ER8 | 69 | 1.0613 | 1.0613 | 0
GEN-2018-074 | 01 NORTH | 655236 | MORNINGS-ER8 | 69 | 2.077 | 2.077 | 0
GEN-2018-074 | 01 NORTH | 655237 | BONILLA-ER8 | 69 | 1.7733 | 1.7733 | 0
GEN-2018-074 | 01 NORTH | 655239 | WOLSEY-ER8 | 69 | 2.0957 | 2.0957 | 0
GEN-2018-074 | 01 NORTH | 655240 | HGHMORE-ER8 | 69 | 1.6057 | 1.6057 | 0
GEN-2018-074 | 01 NORTH | 655241 | VIRGIL-ER8 | 69 | 2.3075 | 2.3075 | 0
GEN-2018-074 | 01 NORTH | 655242 | CAVOUR-ER8 | 69 | 1.3624 | 1.3624 | 0
GEN-2018-074 | 01 NORTH | 655244 | DAKOTA-ER8 | 69 | 1.0985 | 1.0985 | 0
GEN-2018-074 | 01 NORTH | 655247 | PLANKCTY-ER8 | 69 | 1.562 | 1.562 | 0
GEN-2018-074 | 01 NORTH | 655248 | STORLA-ER8 | 69 | 1.0683 | 1.0683 | 0
GEN-2018-074 | 01 NORTH | 655249 | WILBUR-ER8 | 69 | 0.8027 | 0.8027 | 0
GEN-2018-074 | 01 NORTH | 655250 | CHMBRLAN-ER8 | 69 | 1.6576 | 1.6576 | 0
GEN-2018-074 | 01 NORTH | 655251 | PLATTE-ER8 | 69 | 2.1742 | 2.1742 | 0
GEN-2018-074 | 01 NORTH | 655252 | RIVERVW-ER8 | 69 | 1.5248 | 1.5248 | 0
GEN-2018-074 | 01 NORTH | 655253 | PUKWANA-ER8 | 69 | 1.1634 | 1.1634 | 0
GEN-2018-074 | 01 NORTH | 655254 | HILLTOP-ER8 | 69 | 1.1667 | 1.1667 | 0
GEN-2018-074 | 01 NORTH | 655255 | KIMBALL-ER8 | 69 | 0.698 | 0.698 | 0
GEN-2018-074 | 01 NORTH | 655271 | WAGNER-ER8 | 69 | 1.313 | 1.313 | 0
GEN-2018-074 | 01 NORTH | 655272 | TYNDALL-ER8 | 69 | 2.6018 | 2.6018 | 0
GEN-2018-074 | 01 NORTH | 655273 | ARMOUR-ER8 | 69 | 2.1552 | 2.1552 | 0
GEN-2018-074 | 01 NORTH | 655274 | HARRISON-ER8 | 69 | 1.0763 | 1.0763 | 0
GEN-2018-074 | 01 NORTH | 655275 | TABOR-ER8 | 69 | 1.5297 | 1.5297 | 0
GEN-2018-074 | 01 NORTH | 655276 | UTICA-ER8 | 69 | 1.1904 | 1.1904 | 0
GEN-2018-074 | 01 NORTH | 655277 | GEDDES-ER8 | 69 | 0.9679 | 0.9679 | 0
GEN-2018-074 | 01 NORTH | 655278 | HILLSIDE-ER8 | 69 | 1.2005 | 1.2005 | 0
GEN-2018-074 | 01 NORTH | 655279 | GAVINSPT-ER8 | 69 | 1.1316 | 1.1316 | 0
GEN-2018-074 | 01 NORTH | 655280 | AVON-ER8 | 69 | 1.6487 | 1.6487 | 0
GEN-2018-074 | 01 NORTH | 655281 | SPRNGFLD-ER8 | 69 | 1.781 | 1.781 | 0
GEN-2018-074 | 01 NORTH | 655282 | TRIPP-ER8 | 69 | 1.1495 | 1.1495 | 0
GEN-2018-074 | 01 NORTH | 655283 | MENNO-ER8 | 69 | 0.8815 | 0.8815 | 0
GEN-2018-074 | 01 NORTH | 655284 | TRKYRDGE-ER8 | 69 | 0.7788 | 0.7788 | 0
GEN-2018-074 | 01 NORTH | 655285 | BYWATER-ER8 | 69 | 1.283 | 1.283 | 0
GEN-2018-074 | 01 NORTH | 655308 | ALCESTER-ER8 | 69 | 1.0267 | 1.0267 | 0
GEN-2018-074 | 01 NORTH | 655311 | AKRON-ER8 | 69 | 1.5318 | 1.5318 | 0
GEN-2018-074 | 01 NORTH | 655313 | RICHLAND-ER8 | 69 | 2.5338 | 2.534 | 0.0002
GEN-2018-074 | 01 NORTH | 655314 | ELKPNTCY-ER8 | 69 | 1.9394 | 1.9395 | 0.0001
GEN-2018-074 | 01 NORTH | 655315 | ELKPOINT-ER8 | 69 | 1.9387 | 1.9388 | 0.0001
GEN-2018-074 | 01 NORTH | 655316 | BURBANK-ER8 | 69 | 1.8813 | 1.8814 | 0.0001
GEN-2018-074 | 01 NORTH | 655326 | BGSPRING-ER8 | 69 | 1.1813 | 1.1813 | 0
GEN-2018-074 | 01 NORTH | 655327 | UNIONCRK-ER8 | 69 | 2.0025 | 2.0026 | 0.0001
GEN-2018-074 | 01 NORTH | 655328 | BIGBEND-ER8 | 69 | 2.9024 | 2.9024 | 0
GEN-2018-074 | 01 NORTH | 655329 | GANNVALL-ER8 | 69 | 0.872 | 0.872 | 0
GEN-2018-074 | 01 NORTH | 655332 | LOGAN-ER8 | 69 | 1.1433 | 1.1433 | 0
GEN-2018-074 | 01 NORTH | 655333 | ONIDA-ER8 | 69 | 1.5778 | 1.5778 | 0
GEN-2018-074 | 01 NORTH | 655334 | OKOBOJO-ER8 | 69 | 2.4565 | 2.4565 | 0
GEN-2018-074 | 01 NORTH | 655352 | AMES-ER8 | 69 | 1.3206 | 1.3206 | 0
GEN-2018-074 | 01 NORTH | 655359 | JEFERSON-ER8 | 69 | 1.6887 | 1.6888 | 0.0001
GEN-2018-074 | 01 NORTH | 655362 | LINCOLN-ER7 | 115 | 3.3359 | 3.336 | 0.0001
GEN-2018-074 | 01 NORTH | 655372 | LOGANSUB-ER8 | 69 | 1.1428 | 1.1428 | 0
GEN-2018-074 | 01 NORTH | 655373 | MOS-SLY2-ER8 | 69 | 2.4633 | 2.4633 | 0
GEN-2018-074 | 01 NORTH | 655374 | MOS-TND2-ER8 | 69 | 2.6056 | 2.6056 | 0
GEN-2018-074 | 01 NORTH | 655375 | MOS-WGNR-ER8 | 69 | 1.3136 | 1.3136 | 0
GEN-2018-074 | 01 NORTH | 655376 | MOS-AMR2-ER8 | 69 | 2.3363 | 2.3363 | 0
GEN-2018-074 | 01 NORTH | 655378 | NWPS3680-ER8 | 69 | 1.0799 | 1.0799 | 0
GEN-2018-074 | 01 NORTH | 655384 | NWPS8645-ER8 | 69 | 1.6261 | 1.6261 | 0
GEN-2018-074 | 01 NORTH | 655385 | MOS-LKPL-ER8 | 69 | 4.1828 | 4.1828 | 0
GEN-2018-074 | 01 NORTH | 655386 | MOS-RVR1-ER8 | 69 | 2.1854 | 2.1854 | 0
GEN-2018-074 | 01 NORTH | 655387 | MOS-RVR2-ER8 | 69 | 2.1748 | 2.1748 | 0
GEN-2018-074 | 01 NORTH | 655388 | NWPS7632-ER8 | 69 | 1.5708 | 1.5708 | 0
GEN-2018-074 | 01 NORTH | 655393 | SWR5123-ER8 | 69 | 0.9792 | 0.9792 | 0
GEN-2018-074 | 01 NORTH | 655394 | SW425-ER8 | 69 | 1.3141 | 1.3141 | 0
GEN-2018-074 | 01 NORTH | 655404 | HRRISBRG-ER7 | 115 | 3.3599 | 3.3599 | 0
GEN-2018-074 | 01 NORTH | 655405 | SHINDLER-ER7 | 115 | 2.8574 | 2.8575 | 0.0001
GEN-2018-074 | 01 NORTH | 655406 | 6MILE RD-ER7 | 115 | 2.675 | 2.6751 | 0.0001
GEN-2018-074 | 01 NORTH | 655408 | SXFCHCLR-ER7 | 115 | 3.4422 | 3.4423 | 0.0001
GEN-2018-074 | 01 NORTH | 655410 | SYCAMORE-ER7 | 115 | 3.0724 | 3.0724 | 0
GEN-2018-074 | 01 NORTH | 655412 | CRPNTR-ER8 | 69 | 2.9524 | 2.9524 | 0
GEN-2018-074 | 01 NORTH | 655417 | ROSWELL-ER7 | 115 | 2.7257 | 2.7257 | 0
GEN-2018-074 | 01 NORTH | 655418 | FREEMAN-ER7 | 115 | 2.6822 | 2.6822 | 0
GEN-2018-074 | 01 NORTH | 655423 | GREYGOOS-ER8 | 69 | 1.5756 | 1.5756 | 0
GEN-2018-074 | 01 NORTH | 655425 | MOS-BYWT-ER8 | 69 | 1.283 | 1.283 | 0
GEN-2018-074 | 01 NORTH | 655426 | MOS-GVPT-ER8 | 69 | 1.2035 | 1.2035 | 0
GEN-2018-074 | 01 NORTH | 655427 | MOS-ALC2-ER8 | 69 | 1.0267 | 1.0267 | 0
GEN-2018-074 | 01 NORTH | 655428 | BIGSPRGS-ER8 | 69 | 1.1813 | 1.1813 | 0
GEN-2018-074 | 01 NORTH | 655439 | SXFALLS-ER7 | 115 | 3.3639 | 3.364 | 0.0001
GEN-2018-074 | 01 NORTH | 655440 | MARIONRD-ER7 | 115 | 2.5611 | 2.5612 | 0.0001
GEN-2018-074 | 01 NORTH | 655441 | BUCKSNRT-ER7 | 115 | 3.9593 | 3.9595 | 0.0002
GEN-2018-074 | 01 NORTH | 655444 | DELAPRE-ER7 | 115 | 3.6554 | 3.6555 | 0.0001
GEN-2018-074 | 01 NORTH | 655445 | SUNDOWN-ER7 | 115 | 3.7676 | 3.7677 | 0.0001
GEN-2018-074 | 01 NORTH | 655446 | SW1109-ER7 | 115 | 3.8257 | 3.8258 | 0.0001
GEN-2018-074 | 01 NORTH | 655448 | WILOWCRK-ER7 | 115 | 3.4727 | 3.4728 | 0.0001
GEN-2018-074 | 01 NORTH | 655450 | MOS-ELIS-ER7 | 115 | 3.0916 | 3.0917 | 0.0001
GEN-2018-074 | 01 NORTH | 655452 | MOS-MRRD-ER7 | 115 | 2.9078 | 2.9079 | 0.0001
GEN-2018-074 | 01 NORTH | 655468 | VFODNES-ER7 | 115 | 5.1873 | 5.1875 | 0.0002
GEN-2018-074 | 01 NORTH | 655469 | VFODNES-ER8 | 69 | 4.4 | 4.4001 | 0.0001
GEN-2018-074 | 01 NORTH | 655475 | LAKPLAT-ER4 | 230 | 5.7648 | 5.765 | 0.0002
GEN-2018-074 | 01 NORTH | 655476 | LAKPLAT-ER8 | 69 | 4.198 | 4.198 | 0
GEN-2018-074 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.9596 | 6.9641 | 0.0045
GEN-2018-074 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.3209 | 3.3212 | 0.0003
GEN-2018-074 | 01 NORTH | 655487 | SULLYBT-ER4 | 230 | 6.1421 | 6.1421 | 0
GEN-2018-074 | 01 NORTH | 655488 | SULLYBT-ER8 | 69 | 2.467 | 2.467 | 0
GEN-2018-074 | 01 NORTH | 655490 | WHTSWAN-ER7 | 115 | 12.4463 | 12.4469 | 0.0006
GEN-2018-074 | 01 NORTH | 655499 | CARPENTR-ER8 | 69 | 3.329 | 3.329 | 0
GEN-2018-074 | 01 NORTH | 655504 | YANKTON-ER8 | 69 | 1.2568 | 1.2568 | 0
GEN-2018-074 | 01 NORTH | 655505 | SW660-ER8 | 69 | 1.3041 | 1.3041 | 0
GEN-2018-074 | 01 NORTH | 655506 | SXFALLS2-ER7 | 115 | 3.5127 | 3.5128 | 0.0001
GEN-2018-074 | 01 NORTH | 655509 | SW-MILRC-ER8 | 69 | 1.0926 | 1.0926 | 0
GEN-2018-074 | 01 NORTH | 655518 | DAYTON__-ER7 | 115 | 3.618 | 3.6181 | 0.0001
GEN-2018-074 | 01 NORTH | 656233 | CAROLTON8 | 69 | 5.2712 | 5.2738 | 0.0026
GEN-2018-074 | 01 NORTH | 656237 | COONRPDS G | 69 | 3.2443 | 3.2452 | 0.0009
GEN-2018-074 | 01 NORTH | 656243 | TCE8 | 69 | 2.5282 | 2.5287 | 0.0005
GEN-2018-074 | 01 NORTH | 656245 | TCE TAP8 | 69 | 3.0925 | 3.0933 | 0.0008
GEN-2018-074 | 01 NORTH | 656247 | TEMPLTON8 | 69 | 6.4029 | 6.4105 | 0.0076
GEN-2018-074 | 01 NORTH | 656249 | TOYNE8 | 69 | 7.0056 | 7.0133 | 0.0077
GEN-2018-074 | 01 NORTH | 656267 | MANNINGTAP 8 | 69 | 4.6901 | 4.7019 | 0.0118
GEN-2018-074 | 01 NORTH | 656527 | OSGOOD5 | 161 | 6.0078 | 6.0079 | 0.0001
GEN-2018-074 | 01 NORTH | 656555 | SPNCRSJCT8 | 69 | 9.1868 | 9.187 | 0.0002
GEN-2018-074 | 01 NORTH | 656570 | WISDOM5 | 161 | 10.7382 | 10.739 | 0.0008
GEN-2018-074 | 01 NORTH | 656573 | WISDOM G | 69 | 15.9262 | 15.9266 | 0.0004
GEN-2018-074 | 01 NORTH | 658030 | DENISONWEST8 | 69 | 6.9774 | 7.0539 | 0.0765
GEN-2018-074 | 01 NORTH | 658031 | DENSOUMAIN8 | 69 | 7.1484 | 7.2287 | 0.0803
GEN-2018-074 | 01 NORTH | 658122 | ROCKRPDMUNI8 | 69 | 2.8495 | 2.8496 | 0.0001
GEN-2018-074 | 01 NORTH | 658124 | LUVERNEMUNW8 | 69 | 1.8271 | 1.8272 | 0.0001
GEN-2018-074 | 01 NORTH | 658126 | LUVERNEMUNE8 | 69 | 1.7298 | 1.7298 | 0
GEN-2018-074 | 01 NORTH | 658128 | LUVERNEMUNS8 | 69 | 1.8328 | 1.8329 | 0.0001
GEN-2018-074 | 01 NORTH | 658130 | LAKEPARKMUN8 | 69 | 1.6745 | 1.6745 | 0
GEN-2018-074 | 01 NORTH | 659122 | STORLA__-BE4 | 230 | 5.6079 | 5.608 | 0.0001
GEN-2018-074 | 01 NORTH | 659188 | PHILIP_T-BE4 | 230 | 4.5024 | 4.5024 | 0
GEN-2018-074 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.3206 | 10.3206 | 0
GEN-2018-074 | 01 NORTH | 659295 | SD.PW1__-BE4 | 230 | 4.6237 | 4.6237 | 0
GEN-2018-074 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.7313 | 7.7332 | 0.0019
GEN-2018-074 | 01 NORTH | 659700 | LAKPRKTP-LO8 | 69 | 2.1311 | 2.1311 | 0
GEN-2018-074 | 01 NORTH | 659702 | ALLISNTP-LO8 | 69 | 1.6558 | 1.6558 | 0
GEN-2018-074 | 01 NORTH | 659703 | ALLISON -LO8 | 69 | 1.5607 | 1.5607 | 0
GEN-2018-074 | 01 NORTH | 659704 | MAYCITY -LO8 | 69 | 1.5964 | 1.5964 | 0
GEN-2018-074 | 01 NORTH | 659705 | ALLDRFTP-LO8 | 69 | 1.2718 | 1.2718 | 0
GEN-2018-074 | 01 NORTH | 659706 | ALLENDRF-LO8 | 69 | 1.2539 | 1.2539 | 0
GEN-2018-074 | 01 NORTH | 659707 | SIBLEY -LO8 | 69 | 1.0779 | 1.0779 | 0
GEN-2018-074 | 01 NORTH | 659708 | LITLRCKT-LO8 | 69 | 1.9743 | 1.9744 | 0.0001
GEN-2018-074 | 01 NORTH | 659709 | LITLRCK -LO8 | 69 | 1.9334 | 1.9334 | 0
GEN-2018-074 | 01 NORTH | 659710 | GEORGETP-LO8 | 69 | 2.3923 | 2.3924 | 0.0001
GEN-2018-074 | 01 NORTH | 659711 | GEORGE -LO8 | 69 | 2.3304 | 2.3305 | 0.0001
GEN-2018-074 | 01 NORTH | 659712 | RKRMUNTP-LO8 | 69 | 3.395 | 3.3951 | 0.0001
GEN-2018-074 | 01 NORTH | 659714 | RKRPDTAP-LO8 | 69 | 3.6102 | 3.6103 | 0.0001
GEN-2018-074 | 01 NORTH | 659715 | ROCKRPDS-LO8 | 69 | 3.4533 | 3.4534 | 0.0001
GEN-2018-074 | 01 NORTH | 659726 | STEEN -LO8 | 69 | 2.3501 | 2.3502 | 0.0001
GEN-2018-074 | 01 NORTH | 659727 | LUVERNE -LO8 | 69 | 1.8662 | 1.8662 | 0
GEN-2018-074 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 5.1402 | 5.1411 | 0.0009
GEN-2018-074 | 01 NORTH | 659736 | CLEVELND-LO8 | 69 | 4.4536 | 4.4538 | 0.0002
GEN-2018-074 | 01 NORTH | 659852 | K126MEC -NI8 | 69 | 3.951 | 3.9566 | 0.0056
GEN-2018-074 | 01 NORTH | 659853 | K125DUNL-NI8 | 69 | 4.0726 | 4.0792 | 0.0066
GEN-2018-074 | 01 NORTH | 659854 | K335AMAI-NI8 | 69 | 9.2691 | 9.3619 | 0.0928
GEN-2018-074 | 01 NORTH | 659855 | K318MEC -NI8 | 69 | 5.3939 | 5.4176 | 0.0237
GEN-2018-074 | 01 NORTH | 659862 | K307DENI-NI8 | 69 | 6.7482 | 6.7947 | 0.0465
GEN-2018-074 | 01 NORTH | 659863 | K313HALB-NI8 | 69 | 3.7351 | 3.7449 | 0.0098
GEN-2018-074 | 01 NORTH | 659867 | K319EWOL-NI8 | 69 | 2.7734 | 2.7775 | 0.0041
GEN-2018-074 | 01 NORTH | 659868 | L9 MANNI-NI8 | 69 | 2.6969 | 2.7008 | 0.0039
GEN-2018-074 | 01 NORTH | 659885 | K306SCHL-NI8 | 69 | 4.4536 | 4.4688 | 0.0152
GEN-2018-074 | 01 NORTH | 659886 | K326OTTE-NI8 | 69 | 4.2967 | 4.3102 | 0.0135
GEN-2018-074 | 01 NORTH | 659887 | K333SCHL-NI8 | 69 | 4.1592 | 4.1713 | 0.0121
GEN-2018-074 | 01 NORTH | 659895 | PERRY___-NI8 | 69 | 11.0108 | 11.0139 | 0.0031
GEN-2018-074 | 01 NORTH | 659897 | K338WTCT-NI8 | 69 | 8.8418 | 8.9252 | 0.0834
GEN-2018-074 | 01 NORTH | 659899 | K225ADAV-NI8 | 69 | 6.0324 | 6.0333 | 0.0009
GEN-2018-074 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.6034 | 7.6073 | 0.0039
GEN-2018-074 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.7404 | 14.7446 | 0.0042
GEN-2018-074 | 01 NORTH | 659906 | K317MANN-NI8 | 69 | 3.3778 | 3.3838 | 0.006
GEN-2018-074 | 01 NORTH | 659907 | J1CENTER-NI8 | 69 | 10.0355 | 10.0374 | 0.0019
GEN-2018-074 | 01 NORTH | 659912 | J6BOYER_-NI8 | 69 | 10.3454 | 10.4637 | 0.1183
GEN-2018-074 | 01 NORTH | 659918 | J12_____-NI8 | 69 | 5.4672 | 5.4835 | 0.0163
GEN-2018-074 | 01 NORTH | 659921 | J15_____-NI8 | 69 | 7.3765 | 7.3774 | 0.0009
GEN-2018-074 | 01 NORTH | 659942 | K217HWDN-NI8 | 69 | 8.6662 | 8.6676 | 0.0014
GEN-2018-074 | 01 NORTH | 659946 | K216LIBE-NI8 | 69 | 7.9248 | 7.9265 | 0.0017
GEN-2018-074 | 01 NORTH | 659953 | K412HTNM-NI8 | 69 | 12.4691 | 12.4736 | 0.0045
GEN-2018-074 | 01 NORTH | 659954 | K401UNIO-NI8 | 69 | 7.7715 | 7.7733 | 0.0018
GEN-2018-074 | 01 NORTH | 659971 | K301HINT-NI8 | 69 | 10.7082 | 10.7118 | 0.0036
GEN-2018-074 | 01 NORTH | 659972 | K334KING-NI8 | 69 | 2.9747 | 2.9753 | 0.0006
GEN-2018-074 | 01 NORTH | 659979 | K144LWTN-NI8 | 69 | 6.7859 | 6.7871 | 0.0012
GEN-2018-074 | 01 NORTH | 659980 | K135CONC-NI8 | 69 | 6.983 | 6.9843 | 0.0013
GEN-2018-074 | 01 NORTH | 659998 | K105UTE_-NI8 | 69 | 4.4827 | 4.4903 | 0.0076
GEN-2018-074 | 01 NORTH | 659999 | K106CHAR-NI8 | 69 | 5.1942 | 5.2081 | 0.0139
GEN-2018-074 | 01 NORTH | 660007 | MENNO JCT 7 | 115 | 6.7833 | 6.7837 | 0.0004
GEN-2018-074 | 01 NORTH | 660026 | NAPA JCT 7 | 115 | 8.1058 | 8.1062 | 0.0004
GEN-2018-074 | 01 NORTH | 660036 | YANKTONEAST7 | 115 | 4.1592 | 4.1593 | 0.0001
GEN-2018-074 | 01 NORTH | 660057 | AURORA CY T | 69 | 1.5185 | 1.5185 | 0
GEN-2018-074 | 01 NORTH | 660067 | BRULE CY T | 69 | 1.3028 | 1.3028 | 0
GEN-2018-074 | 01 NORTH | 660230 | STICKNEY JCT | 69 | 2.1781 | 2.1782 | 0.0001
GEN-2018-074 | 01 NORTH | 660231 | MT.VERNON T | 69 | 2.6755 | 2.6755 | 0
GEN-2018-074 | 01 NORTH | 660232 | MT.VERNON | 69 | 2.4362 | 2.4362 | 0
GEN-2018-074 | 01 NORTH | 660233 | WHITE LAKE | 69 | 1.5759 | 1.5759 | 0
GEN-2018-074 | 01 NORTH | 660234 | KIMBALL | 69 | 1.1997 | 1.1997 | 0
GEN-2018-074 | 01 NORTH | 660236 | CHB MO.VIEWT | 69 | 0.8107 | 0.8107 | 0
GEN-2018-074 | 01 NORTH | 660237 | CHB MO.VIEW | 69 | 0.8075 | 0.8075 | 0
GEN-2018-074 | 01 NORTH | 660238 | CHB CITY | 69 | 0.795 | 0.795 | 0
GEN-2018-074 | 01 NORTH | 660252 | MT VERNON 8 | 69 | 2.9503 | 2.9503 | 0
GEN-2018-074 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 3.7924 | 4.0402 | 0.2478
GEN-2018-074 | 01 NORTH | 760788 | GEN-2017-201 | 345 | 7.347 | 7.3478 | 0.0008
GEN-2018-074 | 01 NORTH | 762237 | G17-175TAP | 230 | 7.1324 | 7.1334 | 0.001
GEN-2018-074 | 01 NORTH | 762238 | GEN-2017-175 | 230 | 6.9255 | 6.9263 | 0.0008
GEN-2018-074 | 01 NORTH | 762350 | ASGI-2017-01 | 69 | 2.0957 | 2.0957 | 0
GEN-2018-074 | 01 NORTH | 762779 | G18-043-TAP | 345 | 15.1681 | 15.1699 | 0.0018
GEN-2018-074 | 01 NORTH | 762780 | GEN-2018-043 | 345 | 15.1273 | 15.1292 | 0.0019
GEN-2018-074 | 01 NORTH | 763098 | GEN-2018-074 | 230 | 3.5349 | 3.7838 | 0.2489
GEN-2018-074 | 01 NORTH | 763593 | GEN-2019-019 | 69 | 1.3957 | 1.3957 | 0
GEN-2019-019 | 01 NORTH | 602004 | SPLT RK4 | 230 | 13.5385 | 13.5564 | 0.0179
GEN-2019-019 | 01 NORTH | 635200 | RAUN 3 | 345 | 27.3808 | 27.3961 | 0.0153
GEN-2019-019 | 01 NORTH | 635371 | HOSPERS8 | 69 | 5.095 | 5.1524 | 0.0574
GEN-2019-019 | 01 NORTH | 635377 | DOONTAP8 | 69 | 5.8364 | 5.894 | 0.0576
GEN-2019-019 | 01 NORTH | 635380 | RCKVALY8 | 69 | 6.5146 | 6.5865 | 0.0719
GEN-2019-019 | 01 NORTH | 635381 | RKVALTT8 | 69 | 5.7606 | 5.8205 | 0.0599
GEN-2019-019 | 01 NORTH | 635382 | RCKVALT8 | 69 | 5.5829 | 5.6392 | 0.0563
GEN-2019-019 | 01 NORTH | 635383 | INWOODT8 | 69 | 5.8822 | 5.9365 | 0.0543
GEN-2019-019 | 01 NORTH | 635384 | INWOOD 8 | 69 | 2.3015 | 2.3093 | 0.0078
GEN-2019-019 | 01 NORTH | 635385 | HUDSON 8 | 69 | 6.2549 | 6.3157 | 0.0608
GEN-2019-019 | 01 NORTH | 635386 | SXRIVER8 | 69 | 3.4148 | 3.4314 | 0.0166
GEN-2019-019 | 01 NORTH | 635387 | ALCESTR8 | 69 | 1.6694 | 1.6731 | 0.0037
GEN-2019-019 | 01 NORTH | 635390 | IRETON 8 | 69 | 2.8991 | 2.9108 | 0.0117
GEN-2019-019 | 01 NORTH | 635391 | IRETONT8 | 69 | 6.0857 | 6.1426 | 0.0569
GEN-2019-019 | 01 NORTH | 635394 | MERRILN8 | 69 | 6.0471 | 6.0485 | 0.0014
GEN-2019-019 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.3561 | 8.3602 | 0.0041
GEN-2019-019 | 01 NORTH | 652235 | SIOUXFL8 | 69 | 4.0905 | 4.0908 | 0.0003
GEN-2019-019 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.2601 | 7.264 | 0.0039
GEN-2019-019 | 01 NORTH | 652509 | FTRANDL4 | 230 | 10.9789 | 10.9804 | 0.0015
GEN-2019-019 | 01 NORTH | 652513 | HANLON 4 | 230 | 5.8096 | 5.8119 | 0.0023
GEN-2019-019 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.9915 | 14.0115 | 0.02
GEN-2019-019 | 01 NORTH | 652524 | SIOUXFL7 | 115 | 28.0378 | 28.0564 | 0.0186
GEN-2019-019 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.5412 | 20.5851 | 0.0439
GEN-2019-019 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.7542 | 15.7704 | 0.0162
GEN-2019-019 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.5412 | 20.5851 | 0.0439
GEN-2019-019 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 21.5666 | 21.5984 | 0.0318
GEN-2019-019 | 01 NORTH | 652567 | DENISON4 | 230 | 5.4072 | 5.4081 | 0.0009
GEN-2019-019 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.9345 | 4.9353 | 0.0008
GEN-2019-019 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.5718 | 15.5875 | 0.0157
GEN-2019-019 | 01 NORTH | 655011 | SW101-ER8 | 69 | 2.5506 | 2.5507 | 0.0001
GEN-2019-019 | 01 NORTH | 655013 | MOS-EROS-ER8 | 69 | 2.4083 | 2.4084 | 0.0001
GEN-2019-019 | 01 NORTH | 655014 | MOS-NMAR-ER8 | 69 | 3.083 | 3.0831 | 0.0001
GEN-2019-019 | 01 NORTH | 655015 | MOS-SALM-ER8 | 69 | 2.3776 | 2.3777 | 0.0001
GEN-2019-019 | 01 NORTH | 655016 | MOS-SPNC-ER8 | 69 | 1.5463 | 1.5464 | 0.0001
GEN-2019-019 | 01 NORTH | 655018 | MOS-MDCY-ER8 | 69 | 1.7141 | 1.7142 | 0.0001
GEN-2019-019 | 01 NORTH | 655019 | SW124-ER8 | 69 | 2.7315 | 2.7317 | 0.0002
GEN-2019-019 | 01 NORTH | 655020 | SW130-ER8 | 69 | 4.129 | 4.1293 | 0.0003
GEN-2019-019 | 01 NORTH | 655022 | SW-SPENC-ER8 | 69 | 1.6416 | 1.6417 | 0.0001
GEN-2019-019 | 01 NORTH | 655023 | SW145-ER8 | 69 | 2.1954 | 2.1954 | 0
GEN-2019-019 | 01 NORTH | 655024 | SW-HOWAR-ER8 | 69 | 0.766 | 0.766 | 0
GEN-2019-019 | 01 NORTH | 655025 | SW156-ER8 | 69 | 1.7373 | 1.7373 | 0
GEN-2019-019 | 01 NORTH | 655026 | SW159-ER8 | 69 | 3.3125 | 3.3127 | 0.0002
GEN-2019-019 | 01 NORTH | 655027 | SW162-ER8 | 69 | 2.0223 | 2.0224 | 0.0001
GEN-2019-019 | 01 NORTH | 655028 | SW170-ER8 | 69 | 3.0974 | 3.0976 | 0.0002
GEN-2019-019 | 01 NORTH | 655029 | SW-FEDOR-ER8 | 69 | 1.0361 | 1.0361 | 0
GEN-2019-019 | 01 NORTH | 655030 | MOS-HMPA-ER8 | 69 | 1.7876 | 1.7877 | 0.0001
GEN-2019-019 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 2.0225 | 2.0226 | 0.0001
GEN-2019-019 | 01 NORTH | 655129 | SW806-ER8 | 69 | 0.8791 | 0.8791 | 0
GEN-2019-019 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.5421 | 2.5423 | 0.0002
GEN-2019-019 | 01 NORTH | 655133 | SW822-ER8 | 69 | 2.1967 | 2.1968 | 0.0001
GEN-2019-019 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.6246 | 2.6248 | 0.0002
GEN-2019-019 | 01 NORTH | 655137 | SW833-ER8 | 69 | 2.0954 | 2.0955 | 0.0001
GEN-2019-019 | 01 NORTH | 655143 | MOS-PARK-ER8 | 69 | 1.6931 | 1.6931 | 0
GEN-2019-019 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.8906 | 2.8908 | 0.0002
GEN-2019-019 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.8893 | 2.8895 | 0.0002
GEN-2019-019 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.5428 | 2.543 | 0.0002
GEN-2019-019 | 01 NORTH | 655151 | MOS-BGSP-ER8 | 69 | 1.3653 | 1.3653 | 0
GEN-2019-019 | 01 NORTH | 655152 | SW894-ER8 | 69 | 2.0683 | 2.0684 | 0.0001
GEN-2019-019 | 01 NORTH | 655165 | MOS-INDM-ER8 | 69 | 1.4782 | 1.4783 | 0.0001
GEN-2019-019 | 01 NORTH | 655166 | SW1142-ER8 | 69 | 4.8352 | 4.8357 | 0.0005
GEN-2019-019 | 01 NORTH | 655167 | MOS-CRTI-ER7 | 115 | 7.9573 | 7.9587 | 0.0014
GEN-2019-019 | 01 NORTH | 655180 | GARTSON-ER8 | 69 | 1.8525 | 1.8525 | 0
GEN-2019-019 | 01 NORTH | 655181 | EROS-ER8 | 69 | 2.1855 | 2.1856 | 0.0001
GEN-2019-019 | 01 NORTH | 655182 | SALEM-ER8 | 69 | 2.3087 | 2.3088 | 0.0001
GEN-2019-019 | 01 NORTH | 655185 | GRNDMEAD-ER8 | 69 | 2.6026 | 2.6028 | 0.0002
GEN-2019-019 | 01 NORTH | 655186 | COLTON-ER8 | 69 | 2.1061 | 2.1061 | 0
GEN-2019-019 | 01 NORTH | 655187 | MARION-ER8 | 69 | 1.3835 | 1.3836 | 0.0001
GEN-2019-019 | 01 NORTH | 655188 | PARKERCI-ER8 | 69 | 1.6158 | 1.6159 | 0.0001
GEN-2019-019 | 01 NORTH | 655190 | MONTROSE-ER8 | 69 | 3.9431 | 3.9434 | 0.0003
GEN-2019-019 | 01 NORTH | 655191 | TRENT-ER8 | 69 | 1.0482 | 1.0482 | 0
GEN-2019-019 | 01 NORTH | 655192 | PARKER-ER8 | 69 | 1.7256 | 1.7257 | 0.0001
GEN-2019-019 | 01 NORTH | 655194 | SPENCER-ER8 | 69 | 1.6168 | 1.6169 | 0.0001
GEN-2019-019 | 01 NORTH | 655195 | CHESTER-ER8 | 69 | 1.4798 | 1.4798 | 0
GEN-2019-019 | 01 NORTH | 655196 | HOWARD-ER8 | 69 | 0.7477 | 0.7477 | 0
GEN-2019-019 | 01 NORTH | 655197 | HOWARDCI-ER8 | 69 | 0.8263 | 0.8263 | 0
GEN-2019-019 | 01 NORTH | 655198 | DOLTON-ER8 | 69 | 1.2742 | 1.2742 | 0
GEN-2019-019 | 01 NORTH | 655199 | ORLAND-ER8 | 69 | 1.8338 | 1.8339 | 0.0001
GEN-2019-019 | 01 NORTH | 655200 | WBRANDON-ER7 | 115 | 14.1468 | 14.1514 | 0.0046
GEN-2019-019 | 01 NORTH | 655201 | HUMBOLT-ER8 | 69 | 2.7626 | 2.7628 | 0.0002
GEN-2019-019 | 01 NORTH | 655202 | FEDORA-ER8 | 69 | 0.8761 | 0.8761 | 0
GEN-2019-019 | 01 NORTH | 655203 | LYONS-ER8 | 69 | 1.9629 | 1.963 | 0.0001
GEN-2019-019 | 01 NORTH | 655204 | SPLITRCK-ER7 | 115 | 4.5062 | 4.5067 | 0.0005
GEN-2019-019 | 01 NORTH | 655308 | ALCESTER-ER8 | 69 | 1.0267 | 1.0267 | 0
GEN-2019-019 | 01 NORTH | 655311 | AKRON-ER8 | 69 | 1.5318 | 1.5318 | 0
GEN-2019-019 | 01 NORTH | 655313 | RICHLAND-ER8 | 69 | 2.5338 | 2.534 | 0.0002
GEN-2019-019 | 01 NORTH | 655314 | ELKPNTCY-ER8 | 69 | 1.9394 | 1.9395 | 0.0001
GEN-2019-019 | 01 NORTH | 655315 | ELKPOINT-ER8 | 69 | 1.9387 | 1.9388 | 0.0001
GEN-2019-019 | 01 NORTH | 655316 | BURBANK-ER8 | 69 | 1.8813 | 1.8814 | 0.0001
GEN-2019-019 | 01 NORTH | 655326 | BGSPRING-ER8 | 69 | 1.1813 | 1.1813 | 0
GEN-2019-019 | 01 NORTH | 655327 | UNIONCRK-ER8 | 69 | 2.0025 | 2.0026 | 0.0001
GEN-2019-019 | 01 NORTH | 655346 | INDMARIN-ER8 | 69 | 1.4001 | 1.4002 | 0.0001
GEN-2019-019 | 01 NORTH | 655348 | CORSON-ER7 | 115 | 10.0028 | 10.0051 | 0.0023
GEN-2019-019 | 01 NORTH | 655349 | MOS-FMC-ER7 | 115 | 5.9903 | 5.9911 | 0.0008
GEN-2019-019 | 01 NORTH | 655359 | JEFERSON-ER8 | 69 | 1.6887 | 1.6888 | 0.0001
GEN-2019-019 | 01 NORTH | 655360 | MCOOKLK-ER8 | 69 | 1.3614 | 1.3615 | 0.0001
GEN-2019-019 | 01 NORTH | 655362 | LINCOLN-ER7 | 115 | 3.3356 | 3.336 | 0.0004
GEN-2019-019 | 01 NORTH | 655368 | VLLYSPRG-ER7 | 115 | 5.0339 | 5.0345 | 0.0006
GEN-2019-019 | 01 NORTH | 655377 | SW1145-ER7 | 115 | 26.6284 | 26.6451 | 0.0167
GEN-2019-019 | 01 NORTH | 655390 | MOS-CLTN-ER8 | 69 | 2.1085 | 2.1086 | 0.0001
GEN-2019-019 | 01 NORTH | 655391 | MOS-CHST-ER8 | 69 | 1.4816 | 1.4816 | 0
GEN-2019-019 | 01 NORTH | 655393 | SWR5123-ER8 | 69 | 0.9792 | 0.9792 | 0
GEN-2019-019 | 01 NORTH | 655396 | SW144-ER8 | 69 | 1.8567 | 1.8568 | 0.0001
GEN-2019-019 | 01 NORTH | 655397 | XLSW4X1-ER8 | 69 | 2.3632 | 2.3633 | 0.0001
GEN-2019-019 | 01 NORTH | 655400 | BRANDON-ER7 | 115 | 11.3001 | 11.3031 | 0.003
GEN-2019-019 | 01 NORTH | 655401 | ROWENA-ER7 | 115 | 6.5215 | 6.5224 | 0.0009
GEN-2019-019 | 01 NORTH | 655404 | HRRISBRG-ER7 | 115 | 3.3595 | 3.3599 | 0.0004
GEN-2019-019 | 01 NORTH | 655405 | SHINDLER-ER7 | 115 | 2.8572 | 2.8575 | 0.0003
GEN-2019-019 | 01 NORTH | 655406 | 6MILE RD-ER7 | 115 | 2.6748 | 2.6751 | 0.0003
GEN-2019-019 | 01 NORTH | 655407 | MOS-SPRK-ER7 | 115 | 4.6562 | 4.6566 | 0.0004
GEN-2019-019 | 01 NORTH | 655408 | SXFCHCLR-ER7 | 115 | 3.4418 | 3.4423 | 0.0005
GEN-2019-019 | 01 NORTH | 655409 | MAPLE ST-ER7 | 115 | 13.2994 | 13.3035 | 0.0041
GEN-2019-019 | 01 NORTH | 655410 | SYCAMORE-ER7 | 115 | 3.0721 | 3.0724 | 0.0003
GEN-2019-019 | 01 NORTH | 655413 | SW167 -ER7 | 115 | 14.5975 | 14.6024 | 0.0049
GEN-2019-019 | 01 NORTH | 655414 | SW1116 -ER7 | 115 | 12.0362 | 12.0395 | 0.0033
GEN-2019-019 | 01 NORTH | 655427 | MOS-ALC2-ER8 | 69 | 1.0267 | 1.0267 | 0
GEN-2019-019 | 01 NORTH | 655428 | BIGSPRGS-ER8 | 69 | 1.1813 | 1.1813 | 0
GEN-2019-019 | 01 NORTH | 655437 | LAMESA-ER7 | 115 | 2.056 | 2.0562 | 0.0002
GEN-2019-019 | 01 NORTH | 655438 | HARTFORD-ER7 | 115 | 2.4247 | 2.4249 | 0.0002
GEN-2019-019 | 01 NORTH | 655439 | SXFALLS-ER7 | 115 | 3.3636 | 3.364 | 0.0004
GEN-2019-019 | 01 NORTH | 655440 | MARIONRD-ER7 | 115 | 2.5609 | 2.5612 | 0.0003
GEN-2019-019 | 01 NORTH | 655441 | BUCKSNRT-ER7 | 115 | 3.9589 | 3.9595 | 0.0006
GEN-2019-019 | 01 NORTH | 655444 | DELAPRE-ER7 | 115 | 3.655 | 3.6555 | 0.0005
GEN-2019-019 | 01 NORTH | 655445 | SUNDOWN-ER7 | 115 | 3.7672 | 3.7677 | 0.0005
GEN-2019-019 | 01 NORTH | 655446 | SW1109-ER7 | 115 | 3.8253 | 3.8258 | 0.0005
GEN-2019-019 | 01 NORTH | 655447 | WALLLK-ER7 | 115 | 1.9755 | 1.9757 | 0.0002
GEN-2019-019 | 01 NORTH | 655448 | WILOWCRK-ER7 | 115 | 3.4723 | 3.4728 | 0.0005
GEN-2019-019 | 01 NORTH | 655449 | HARTSE-ER7 | 115 | 2.3248 | 2.3249 | 0.0001
GEN-2019-019 | 01 NORTH | 655450 | MOS-ELIS-ER7 | 115 | 3.0913 | 3.0917 | 0.0004
GEN-2019-019 | 01 NORTH | 655451 | SW102-ER7 | 115 | 2.9913 | 2.9916 | 0.0003
GEN-2019-019 | 01 NORTH | 655452 | MOS-MRRD-ER7 | 115 | 2.9076 | 2.9079 | 0.0003
GEN-2019-019 | 01 NORTH | 655453 | MOS-LAME-ER7 | 115 | 2.2 | 2.2001 | 0.0001
GEN-2019-019 | 01 NORTH | 655468 | VFODNES-ER7 | 115 | 5.1865 | 5.1875 | 0.001
GEN-2019-019 | 01 NORTH | 655469 | VFODNES-ER8 | 69 | 4.3996 | 4.4001 | 0.0005
GEN-2019-019 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.9605 | 6.9641 | 0.0036
GEN-2019-019 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.3209 | 3.3212 | 0.0003
GEN-2019-019 | 01 NORTH | 655493 | HANLON-ER7 | 115 | 4.0301 | 4.0306 | 0.0005
GEN-2019-019 | 01 NORTH | 655494 | HANLON1-ER8 | 69 | 5.388 | 5.3886 | 0.0006
GEN-2019-019 | 01 NORTH | 655495 | HANLON2-ER8 | 69 | 5.388 | 5.3886 | 0.0006
GEN-2019-019 | 01 NORTH | 655506 | SXFALLS2-ER7 | 115 | 3.5123 | 3.5128 | 0.0005
GEN-2019-019 | 01 NORTH | 655518 | DAYTON__-ER7 | 115 | 3.6176 | 3.6181 | 0.0005
GEN-2019-019 | 01 NORTH | 658122 | ROCKRPDMUNI8 | 69 | 2.8484 | 2.8496 | 0.0012
GEN-2019-019 | 01 NORTH | 658124 | LUVERNEMUNW8 | 69 | 1.8267 | 1.8272 | 0.0005
GEN-2019-019 | 01 NORTH | 658126 | LUVERNEMUNE8 | 69 | 1.7294 | 1.7298 | 0.0004
GEN-2019-019 | 01 NORTH | 658128 | LUVERNEMUNS8 | 69 | 1.8324 | 1.8329 | 0.0005
GEN-2019-019 | 01 NORTH | 658900 | L4SXCTNMUNI8 | 69 | 6.5741 | 6.9305 | 0.3564
GEN-2019-019 | 01 NORTH | 658902 | L5SXCTWMUNI8 | 69 | 6.3626 | 6.6614 | 0.2988
GEN-2019-019 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.7035 | 7.7332 | 0.0297
GEN-2019-019 | 01 NORTH | 659708 | LITLRCKT-LO8 | 69 | 1.9738 | 1.9744 | 0.0006
GEN-2019-019 | 01 NORTH | 659709 | LITLRCK -LO8 | 69 | 1.9328 | 1.9334 | 0.0006
GEN-2019-019 | 01 NORTH | 659710 | GEORGETP-LO8 | 69 | 2.3915 | 2.3924 | 0.0009
GEN-2019-019 | 01 NORTH | 659711 | GEORGE -LO8 | 69 | 2.3297 | 2.3305 | 0.0008
GEN-2019-019 | 01 NORTH | 659712 | RKRMUNTP-LO8 | 69 | 3.3933 | 3.3951 | 0.0018
GEN-2019-019 | 01 NORTH | 659714 | RKRPDTAP-LO8 | 69 | 3.6083 | 3.6103 | 0.002
GEN-2019-019 | 01 NORTH | 659715 | ROCKRPDS-LO8 | 69 | 3.4517 | 3.4534 | 0.0017
GEN-2019-019 | 01 NORTH | 659716 | MAPLETAP-LO7 | 115 | 13.3456 | 13.3497 | 0.0041
GEN-2019-019 | 01 NORTH | 659717 | STATELIN-LO7 | 115 | 4.0066 | 4.0069 | 0.0003
GEN-2019-019 | 01 NORTH | 659718 | LRCHWDTP-LO7 | 115 | 3.1745 | 3.1747 | 0.0002
GEN-2019-019 | 01 NORTH | 659719 | LARCHW0D-LO7 | 115 | 3.1055 | 3.1057 | 0.0002
GEN-2019-019 | 01 NORTH | 659720 | WESTLYON-LO7 | 115 | 2.5793 | 2.5795 | 0.0002
GEN-2019-019 | 01 NORTH | 659721 | LESTERSS-LO7 | 115 | 2.1883 | 2.1884 | 0.0001
GEN-2019-019 | 01 NORTH | 659722 | LESTERSS-LO8 | 69 | 2.2137 | 2.2137 | 0
GEN-2019-019 | 01 NORTH | 659724 | LESTER -LO8 | 69 | 2.1603 | 2.1604 | 0.0001
GEN-2019-019 | 01 NORTH | 659726 | STEEN -LO8 | 69 | 2.3493 | 2.3502 | 0.0009
GEN-2019-019 | 01 NORTH | 659727 | LUVERNE -LO8 | 69 | 1.8657 | 1.8662 | 0.0005
GEN-2019-019 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 5.128 | 5.1411 | 0.0131
GEN-2019-019 | 01 NORTH | 659736 | CLEVELND-LO8 | 69 | 4.4508 | 4.4538 | 0.003
GEN-2019-019 | 01 NORTH | 659894 | NORTHWST-NI8 | 69 | 4.2541 | 4.2817 | 0.0276
GEN-2019-019 | 01 NORTH | 659896 | K228WSTB-NI8 | 69 | 5.9117 | 6.0023 | 0.0906
GEN-2019-019 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.5317 | 7.6073 | 0.0756
GEN-2019-019 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.4295 | 14.7446 | 0.3151
GEN-2019-019 | 01 NORTH | 659902 | L1______-NI8 | 69 | 6.5258 | 6.7082 | 0.1824
GEN-2019-019 | 01 NORTH | 659904 | L3______-NI8 | 69 | 9.0638 | 9.2156 | 0.1518
GEN-2019-019 | 01 NORTH | 659905 | L8______-NI8 | 69 | 6.2628 | 6.3868 | 0.124
GEN-2019-019 | 01 NORTH | 659907 | J1CENTER-NI8 | 69 | 9.8136 | 10.0374 | 0.2238
GEN-2019-019 | 01 NORTH | 659920 | J14PRKNS-NI8 | 69 | 4.9804 | 5.0222 | 0.0418
GEN-2019-019 | 01 NORTH | 659921 | J15_____-NI8 | 69 | 6.9303 | 7.3774 | 0.4471
GEN-2019-019 | 01 NORTH | 659940 | K223SIOU-NI8 | 69 | 6.5113 | 6.7162 | 0.2049
GEN-2019-019 | 01 NORTH | 659941 | K222HULL-NI8 | 69 | 6.2468 | 6.4827 | 0.2359
GEN-2019-019 | 01 NORTH | 659942 | K217HWDN-NI8 | 69 | 8.5419 | 8.6676 | 0.1257
GEN-2019-019 | 01 NORTH | 659943 | K207OC N-NI8 | 69 | 6.2431 | 6.3819 | 0.1388
GEN-2019-019 | 01 NORTH | 659944 | K202PRES-NI8 | 69 | 5.7038 | 5.7331 | 0.0293
GEN-2019-019 | 01 NORTH | 659945 | K226MERR-NI8 | 69 | 5.9552 | 5.9747 | 0.0195
GEN-2019-019 | 01 NORTH | 659955 | K213HOSP-NI8 | 69 | 5.2652 | 5.3524 | 0.0872
GEN-2019-019 | 01 NORTH | 659977 | K218ROCK-NI8 | 69 | 5.6845 | 5.7452 | 0.0607
GEN-2019-019 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 4.0397 | 4.0402 | 0.0005
GEN-2019-019 | 01 NORTH | 763098 | GEN-2018-074 | 230 | 3.7834 | 3.7838 | 0.0004
GEN-2019-019 | 01 NORTH | 763593 | GEN-2019-019 | 69 | 1.091 | 1.3957 | 0.3047
GEN-2019-023 | 01 NORTH | 588550 | GEN-2017-010 | 230 | 4.4607 | 4.4944 | 0.0337
GEN-2019-023 | 01 NORTH | 652200 | GLENDIVE7 | 115 | 7.0638 | 7.2403 | 0.1765
GEN-2019-023 | 01 NORTH | 652212 | GLENDIVEP2T7 | 115 | 4.3101 | 4.3802 | 0.0701
GEN-2019-023 | 01 NORTH | 652213 | FALLON 8 | 69 | 1.0835 | 1.086 | 0.0025
GEN-2019-023 | 01 NORTH | 652394 | TERRY TAP | 115 | 2.8927 | 2.9213 | 0.0286
GEN-2019-023 | 01 NORTH | 652395 | SHIRLEY TAP | 115 | 3.0332 | 3.0625 | 0.0293
GEN-2019-023 | 01 NORTH | 652401 | CIRCLE 7 | 115 | 2.1931 | 2.2055 | 0.0124
GEN-2019-023 | 01 NORTH | 652403 | DAWSONC4 | 230 | 4.2606 | 4.4878 | 0.2272
GEN-2019-023 | 01 NORTH | 652404 | DAWSONC7 | 115 | 7.7963 | 8.0373 | 0.241
GEN-2019-023 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.1604 | 2.1847 | 0.0243
GEN-2019-023 | 01 NORTH | 652406 | FTPECK 7 | 115 | 2.9877 | 3.0059 | 0.0182
GEN-2019-023 | 01 NORTH | 652407 | FALLON 7 | 115 | 3.1886 | 3.225 | 0.0364
GEN-2019-023 | 01 NORTH | 652409 | WOLFPT 7 | 115 | 2.9793 | 2.994 | 0.0147
GEN-2019-023 | 01 NORTH | 652411 | MI CTYE4 | 230 | 2.8219 | 2.8745 | 0.0526
GEN-2019-023 | 01 NORTH | 652412 | MI CTYE7 | 115 | 3.8599 | 3.9048 | 0.0449
GEN-2019-023 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.7237 | 6.7953 | 0.0716
GEN-2019-023 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.4796 | 9.6412 | 0.1616
GEN-2019-023 | 01 NORTH | 652468 | HEBRON 4 | 230 | 5.7832 | 5.7996 | 0.0164
GEN-2019-023 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 4.0842 | 4.5412 | 0.457
GEN-2019-023 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.044 | 5.0501 | 0.0061
GEN-2019-023 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7332 | 5.7451 | 0.0119
GEN-2019-023 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9863 | 1.9873 | 0.001
GEN-2019-023 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5741 | 3.5772 | 0.0031
GEN-2019-023 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.153 | 4.1546 | 0.0016
GEN-2019-023 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 13.812 | 13.8395 | 0.0275
GEN-2019-023 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.8701 | 6.8769 | 0.0068
GEN-2019-023 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1072 | 3.1081 | 0.0009
GEN-2019-023 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.4896 | 5.4925 | 0.0029
GEN-2019-023 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.0493 | 4.0503 | 0.001
GEN-2019-023 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2576 | 3.2583 | 0.0007
GEN-2019-023 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.215 | 5.2168 | 0.0018
GEN-2019-023 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.1506 | 4.1518 | 0.0012
GEN-2019-023 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.458 | 3.4588 | 0.0008
GEN-2019-023 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9003 | 2.9011 | 0.0008
GEN-2019-023 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5449 | 3.546 | 0.0011
GEN-2019-023 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.2466 | 8.2529 | 0.0063
GEN-2019-023 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.4574 | 6.4602 | 0.0028
GEN-2019-023 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.314 | 2.3144 | 0.0004
GEN-2019-023 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1204 | 3.121 | 0.0006
GEN-2019-023 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.9805 | 2.9811 | 0.0006
GEN-2019-023 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7485 | 2.749 | 0.0005
GEN-2019-023 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6487 | 2.6492 | 0.0005
GEN-2019-023 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9038 | 3.9048 | 0.001
GEN-2019-023 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4361 | 3.4369 | 0.0008
GEN-2019-023 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.1997 | 6.2023 | 0.0026
GEN-2019-023 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9963 | 3.9974 | 0.0011
GEN-2019-023 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.1904 | 6.1939 | 0.0035
GEN-2019-023 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.526 | 3.5272 | 0.0012
GEN-2019-023 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 16.2246 | 16.2445 | 0.0199
GEN-2019-023 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.1564 | 7.2166 | 0.0602
GEN-2019-023 | 01 NORTH | 659125 | DICKINSN-BE7 | 115 | 9.4294 | 9.475 | 0.0456
GEN-2019-023 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.7739 | 5.786 | 0.0121
GEN-2019-023 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.9295 | 13.9575 | 0.028
GEN-2019-023 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.4144 | 10.4624 | 0.048
GEN-2019-023 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7202 | 3.7222 | 0.002
GEN-2019-023 | 01 NORTH | 659186 | E.SIDNEY-LY7 | 115 | 4.2882 | 4.2943 | 0.0061
GEN-2019-023 | 01 NORTH | 659195 | DICKINS2-BE7 | 115 | 9.3938 | 9.4389 | 0.0451
GEN-2019-023 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.5065 | 15.5246 | 0.0181
GEN-2019-023 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 16.2246 | 16.2445 | 0.0199
GEN-2019-023 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.6369 | 9.6383 | 0.0014
GEN-2019-023 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.2314 | 7.2341 | 0.0027
GEN-2019-023 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2699 | 7.2707 | 0.0008
GEN-2019-023 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.2686 | 5.4613 | 0.1927
GEN-2019-023 | 01 NORTH | 659259 | HEADRESS-CM7 | 115 | 2.9731 | 2.9876 | 0.0145
GEN-2019-023 | 01 NORTH | 659263 | LITTL_MS-BE7 | 115 | 3.0186 | 3.0301 | 0.0115
GEN-2019-023 | 01 NORTH | 659265 | LITTL_MS-BE4 | 230 | 3.5472 | 3.579 | 0.0318
GEN-2019-023 | 01 NORTH | 659266 | RHAME___-BE4 | 230 | 4.5381 | 4.5731 | 0.035
GEN-2019-023 | 01 NORTH | 659267 | RHAME___-BE7 | 115 | 2.0354 | 2.0388 | 0.0034
GEN-2019-023 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3769 | 11.4121 | 0.0352
GEN-2019-023 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3037 | 2.3084 | 0.0047
GEN-2019-023 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.4796 | 9.6412 | 0.1616
GEN-2019-023 | 01 NORTH | 659339 | BOWMAN__-BE4 | 230 | 3.8359 | 3.8564 | 0.0205
GEN-2019-023 | 01 NORTH | 659340 | BOWMAN__-BE7 | 115 | 3.5107 | 3.5192 | 0.0085
GEN-2019-023 | 01 NORTH | 659341 | NBURR___-GE7 | 115 | 1.8199 | 1.8222 | 0.0023
GEN-2019-023 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.1691 | 12.1759 | 0.0068
GEN-2019-023 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.1692 | 12.176 | 0.0068
GEN-2019-023 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.3848 | 9.4095 | 0.0247
GEN-2019-023 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.7566 | 11.7695 | 0.0129
GEN-2019-023 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.7233 | 8.7413 | 0.018
GEN-2019-023 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 17.7902 | 17.8114 | 0.0212
GEN-2019-023 | 01 NORTH | 659400 | ND.SUN._-PP4 | 230 | 5.2393 | 5.2524 | 0.0131
GEN-2019-023 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9315 | 1.9348 | 0.0033
GEN-2019-023 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7384 | 1.741 | 0.0026
GEN-2019-023 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.5501 | 6.6188 | 0.0687
GEN-2019-023 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6117 | 3.6271 | 0.0154
GEN-2019-023 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 17.694 | 17.7151 | 0.0211
GEN-2019-023 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 17.7055 | 17.7266 | 0.0211
GEN-2019-023 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 4.0842 | 4.5412 | 0.457
GEN-2019-023 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.5156 | 3.6741 | 0.1585
GEN-2019-023 | 01 NORTH | 659542 | REDWATER-MC7 | 115 | 2.1931 | 2.2055 | 0.0124
GEN-2019-023 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9315 | 1.9348 | 0.0033
GEN-2019-023 | 01 NORTH | 659550 | LNGBUTTE-RR4 | 230 | 5.643 | 5.6586 | 0.0156
GEN-2019-023 | 01 NORTH | 659551 | LNGBUTTE-RR7 | 115 | 3.5355 | 3.5385 | 0.003
GEN-2019-023 | 01 NORTH | 659553 | RAIDER__-RR7 | 115 | 2.3899 | 2.3913 | 0.0014
GEN-2019-023 | 01 NORTH | 659554 | REDTRAIL-RR7 | 115 | 2.3664 | 2.3678 | 0.0014
GEN-2019-023 | 01 NORTH | 659555 | RICHRDTN-RR7 | 115 | 2.1899 | 2.1911 | 0.0012
GEN-2019-023 | 01 NORTH | 661004 | BAKER 4 | 230 | 3.3112 | 3.3447 | 0.0335
GEN-2019-023 | 01 NORTH | 661005 | BAKER 7 | 115 | 3.5443 | 3.566 | 0.0217
GEN-2019-023 | 01 NORTH | 661010 | MILESCITYSW7 | 115 | 1.0259 | 1.0277 | 0.0018
GEN-2019-023 | 01 NORTH | 661019 | MATHSON7 | 115 | 8.3632 | 8.3978 | 0.0346
GEN-2019-023 | 01 NORTH | 661024 | WDICKSN7 | 115 | 6.6775 | 6.6996 | 0.0221
GEN-2019-023 | 01 NORTH | 661032 | GLENDCT7 | 115 | 6.4335 | 6.5561 | 0.1226
GEN-2019-023 | 01 NORTH | 661033 | CABINCR7 | 115 | 3.1795 | 3.2007 | 0.0212
GEN-2019-023 | 01 NORTH | 661034 | KEYXLPS14 7 | 115 | 3.254 | 3.2742 | 0.0202
GEN-2019-023 | 01 NORTH | 661053 | MANDAN 4 | 230 | 16.3954 | 16.4017 | 0.0063
GEN-2019-023 | 01 NORTH | 661056 | LEWIS 7 | 115 | 5.8371 | 5.8509 | 0.0138
GEN-2019-023 | 01 NORTH | 661070 | N ENGLN7 | 115 | 3.8225 | 3.8296 | 0.0071
GEN-2019-023 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 4.009 | 4.4691 | 0.4601
GEN-2019-037 | 01 NORTH | 67030 | MPC04000MPT | 230 | 11.1676 | 11.1686 | 0.001
GEN-2019-037 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.5193 | 7.5395 | 0.0202
GEN-2019-037 | 01 NORTH | 587720 | GEN-2016-087 | 230 | 4.0406 | 4.0409 | 0.0003
GEN-2019-037 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 12.0071 | 12.1416 | 0.1345
GEN-2019-037 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 9.3441 | 9.3508 | 0.0067
GEN-2019-037 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.5617 | 11.5622 | 0.0005
GEN-2019-037 | 01 NORTH | 602052 | MAGIC CITY 4 | 230 | 4.4713 | 4.4718 | 0.0005
GEN-2019-037 | 01 NORTH | 603022 | SOURIS 7 | 115 | 9.0344 | 9.0365 | 0.0021
GEN-2019-037 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.2594 | 11.2636 | 0.0042
GEN-2019-037 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.8766 | 23.8817 | 0.0051
GEN-2019-037 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.8766 | 23.8817 | 0.0051
GEN-2019-037 | 01 NORTH | 608600 | BISONMP4 | 230 | 8.1608 | 8.1612 | 0.0004
GEN-2019-037 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.8766 | 23.8817 | 0.0051
GEN-2019-037 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.8987 | 5.8989 | 0.0002
GEN-2019-037 | 01 NORTH | 615145 | NEW FRONT W | 115 | 4.6102 | 4.6104 | 0.0002
GEN-2019-037 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 6.5314 | 6.5323 | 0.0009
GEN-2019-037 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.6376 | 8.6387 | 0.0011
GEN-2019-037 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.2341 | 19.2385 | 0.0044
GEN-2019-037 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0447 | 9.0449 | 0.0002
GEN-2019-037 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.2341 | 19.2385 | 0.0044
GEN-2019-037 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.2341 | 19.2385 | 0.0044
GEN-2019-037 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.2341 | 19.2385 | 0.0044
GEN-2019-037 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.1786 | 16.1826 | 0.004
GEN-2019-037 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.1052 | 18.1128 | 0.0076
GEN-2019-037 | 01 NORTH | 615903 | GRE-BALTA 4 | 230 | 6.7137 | 6.7143 | 0.0006
GEN-2019-037 | 01 NORTH | 615904 | GRE-BALTACB4 | 230 | 6.7137 | 6.7143 | 0.0006
GEN-2019-037 | 01 NORTH | 620276 | NHARVEY7 | 115 | 3.2698 | 3.2699 | 0.0001
GEN-2019-037 | 01 NORTH | 620290 | HARVEY 4 | 230 | 5.0725 | 5.0728 | 0.0003
GEN-2019-037 | 01 NORTH | 620369 | JAMESTN3 | 345 | 5.848 | 5.8481 | 0.0001
GEN-2019-037 | 01 NORTH | 620381 | UNDERWD4 | 230 | 15.1305 | 15.1333 | 0.0028
GEN-2019-037 | 01 NORTH | 652204 | VALLEYC8 | 69 | 2.2674 | 2.2674 | 0
GEN-2019-037 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.7495 | 6.7532 | 0.0037
GEN-2019-037 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1032 | 1.1033 | 0.0001
GEN-2019-037 | 01 NORTH | 652296 | WARD 4 | 230 | 14.6606 | 14.6677 | 0.0071
GEN-2019-037 | 01 NORTH | 652400 | WILISTN4 | 230 | 11.2215 | 11.2308 | 0.0093
GEN-2019-037 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.6312 | 8.6335 | 0.0023
GEN-2019-037 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0441 | 5.0452 | 0.0011
GEN-2019-037 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.7895 | 6.7953 | 0.0058
GEN-2019-037 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.6357 | 9.6412 | 0.0055
GEN-2019-037 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.8612 | 14.8712 | 0.01
GEN-2019-037 | 01 NORTH | 652427 | BISMARK7 | 115 | 16.3348 | 16.3394 | 0.0046
GEN-2019-037 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.7074 | 2.7074 | 0
GEN-2019-037 | 01 NORTH | 652432 | EDGELEY7 | 115 | 3.4668 | 3.4668 | 0
GEN-2019-037 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.5792 | 10.5797 | 0.0005
GEN-2019-037 | 01 NORTH | 652436 | FARGO 7 | 115 | 11.4465 | 11.4468 | 0.0003
GEN-2019-037 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.3339 | 7.3342 | 0.0003
GEN-2019-037 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.439 | 7.4406 | 0.0016
GEN-2019-037 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.0544 | 12.0679 | 0.0135
GEN-2019-037 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.6587 | 15.6661 | 0.0074
GEN-2019-037 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.4519 | 8.4532 | 0.0013
GEN-2019-037 | 01 NORTH | 652445 | JAMESTN7 | 115 | 9.734 | 9.7348 | 0.0008
GEN-2019-037 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.2845 | 8.2851 | 0.0006
GEN-2019-037 | 01 NORTH | 652454 | VALLEYC7 | 115 | 3.0515 | 3.0515 | 0
GEN-2019-037 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.5509 | 10.581 | 0.0301
GEN-2019-037 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.6207 | 4.621 | 0.0003
GEN-2019-037 | 01 NORTH | 652466 | HILKEN 4 | 230 | 8.2405 | 8.2441 | 0.0036
GEN-2019-037 | 01 NORTH | 652496 | WINCHESTER4 | 230 | 4.5664 | 4.567 | 0.0006
GEN-2019-037 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 4.0406 | 4.0409 | 0.0003
GEN-2019-037 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.0355 | 9.0374 | 0.0019
GEN-2019-037 | 01 NORTH | 652529 | WATERTN3 | 345 | 10.7754 | 10.7764 | 0.001
GEN-2019-037 | 01 NORTH | 652568 | GROTONSOUTH7 | 115 | 17.783 | 17.7857 | 0.0027
GEN-2019-037 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.8123 | 5.8135 | 0.0012
GEN-2019-037 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 8.9713 | 8.9732 | 0.0019
GEN-2019-037 | 01 NORTH | 655411 | CRANDALL-ER7 | 115 | 5.6371 | 5.6373 | 0.0002
GEN-2019-037 | 01 NORTH | 655419 | SW561-ER7 | 115 | 5.8463 | 5.8466 | 0.0003
GEN-2019-037 | 01 NORTH | 655612 | HARVEY -CP7 | 115 | 3.8437 | 3.8438 | 0.0001
GEN-2019-037 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.248 | 6.2499 | 0.0019
GEN-2019-037 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.5749 | 8.5759 | 0.001
GEN-2019-037 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.3891 | 8.3903 | 0.0012
GEN-2019-037 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.8628 | 15.8672 | 0.0044
GEN-2019-037 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.7779 | 6.7794 | 0.0015
GEN-2019-037 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.0568 | 8.0595 | 0.0027
GEN-2019-037 | 01 NORTH | 655658 | RUTHVILL-CP7 | 115 | 6.2954 | 6.2968 | 0.0014
GEN-2019-037 | 01 NORTH | 655661 | DOUGLS.C-CP7 | 115 | 4.0801 | 4.0808 | 0.0007
GEN-2019-037 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 6.1526 | 6.1537 | 0.0011
GEN-2019-037 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 3.1392 | 3.1394 | 0.0002
GEN-2019-037 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.975 | 0.9751 | 0.0001
GEN-2019-037 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9022 | 0.9023 | 0.0001
GEN-2019-037 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.909 | 0.9091 | 0.0001
GEN-2019-037 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6891 | 0.6891 | 0
GEN-2019-037 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6174 | 0.6175 | 0.0001
GEN-2019-037 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1094 | 1.1096 | 0.0002
GEN-2019-037 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1153 | 1.1154 | 0.0001
GEN-2019-037 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1058 | 1.106 | 0.0002
GEN-2019-037 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5109 | 1.5113 | 0.0004
GEN-2019-037 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0219 | 1.0221 | 0.0002
GEN-2019-037 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9894 | 0.9896 | 0.0002
GEN-2019-037 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9898 | 0.99 | 0.0002
GEN-2019-037 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5484 | 1.5489 | 0.0005
GEN-2019-037 | 01 NORTH | 655780 | NORMANLK-BD7 | 115 | 3.1573 | 3.1576 | 0.0003
GEN-2019-037 | 01 NORTH | 655781 | LARSON -BD7 | 115 | 2.1864 | 2.1865 | 0.0001
GEN-2019-037 | 01 NORTH | 655782 | LIGNIBRD-BD7 | 115 | 1.5357 | 1.5358 | 0.0001
GEN-2019-037 | 01 NORTH | 655783 | HAWKEYE -BD7 | 115 | 1.4664 | 1.4665 | 0.0001
GEN-2019-037 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.242 | 1.242 | 0
GEN-2019-037 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1533 | 4.1546 | 0.0013
GEN-2019-037 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0327 | 4.0337 | 0.001
GEN-2019-037 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 7.8704 | 7.8745 | 0.0041
GEN-2019-037 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 13.8286 | 13.8395 | 0.0109
GEN-2019-037 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.8742 | 6.8769 | 0.0027
GEN-2019-037 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1073 | 3.1081 | 0.0008
GEN-2019-037 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.4901 | 5.4925 | 0.0024
GEN-2019-037 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6375 | 3.6384 | 0.0009
GEN-2019-037 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.0496 | 4.0503 | 0.0007
GEN-2019-037 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.6312 | 8.6335 | 0.0023
GEN-2019-037 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.7045 | 6.7054 | 0.0009
GEN-2019-037 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2578 | 3.2583 | 0.0005
GEN-2019-037 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.2156 | 5.2168 | 0.0012
GEN-2019-037 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6346 | 4.6353 | 0.0007
GEN-2019-037 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.151 | 4.1518 | 0.0008
GEN-2019-037 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.2879 | 4.2891 | 0.0012
GEN-2019-037 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.6804 | 5.6825 | 0.0021
GEN-2019-037 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.6551 | 9.6612 | 0.0061
GEN-2019-037 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4582 | 3.4588 | 0.0006
GEN-2019-037 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9004 | 2.9011 | 0.0007
GEN-2019-037 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5451 | 3.546 | 0.0009
GEN-2019-037 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.2476 | 8.2529 | 0.0053
GEN-2019-037 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5061 | 3.5069 | 0.0008
GEN-2019-037 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.7748 | 4.7755 | 0.0007
GEN-2019-037 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.4583 | 6.4602 | 0.0019
GEN-2019-037 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.5788 | 2.5792 | 0.0004
GEN-2019-037 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3193 | 4.3205 | 0.0012
GEN-2019-037 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7143 | 3.7152 | 0.0009
GEN-2019-037 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3141 | 2.3144 | 0.0003
GEN-2019-037 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1206 | 3.121 | 0.0004
GEN-2019-037 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.6938 | 5.6959 | 0.0021
GEN-2019-037 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.838 | 5.8402 | 0.0022
GEN-2019-037 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.0405 | 4.0415 | 0.001
GEN-2019-037 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.9807 | 2.9811 | 0.0004
GEN-2019-037 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7487 | 2.749 | 0.0003
GEN-2019-037 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6489 | 2.6492 | 0.0003
GEN-2019-037 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9041 | 3.9048 | 0.0007
GEN-2019-037 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.513 | 4.5139 | 0.0009
GEN-2019-037 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 6.8752 | 6.8782 | 0.003
GEN-2019-037 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.2854 | 6.288 | 0.0026
GEN-2019-037 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.5613 | 7.5631 | 0.0018
GEN-2019-037 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.3027 | 8.3048 | 0.0021
GEN-2019-037 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.2315 | 5.2323 | 0.0008
GEN-2019-037 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9043 | 3.9048 | 0.0005
GEN-2019-037 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.67 | 4.6707 | 0.0007
GEN-2019-037 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.7125 | 5.7146 | 0.0021
GEN-2019-037 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 12.7862 | 12.7969 | 0.0107
GEN-2019-037 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 9.7028 | 9.709 | 0.0062
GEN-2019-037 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.6743 | 7.6782 | 0.0039
GEN-2019-037 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.3846 | 5.3865 | 0.0019
GEN-2019-037 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2117 | 4.2128 | 0.0011
GEN-2019-037 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.0098 | 5.0114 | 0.0016
GEN-2019-037 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4364 | 3.4369 | 0.0005
GEN-2019-037 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.2006 | 6.2023 | 0.0017
GEN-2019-037 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.8737 | 4.8746 | 0.0009
GEN-2019-037 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9967 | 3.9974 | 0.0007
GEN-2019-037 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.1909 | 6.1939 | 0.003
GEN-2019-037 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5262 | 3.5272 | 0.001
GEN-2019-037 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.2763 | 4.2768 | 0.0005
GEN-2019-037 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4342 | 3.435 | 0.0008
GEN-2019-037 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.2523 | 5.2541 | 0.0018
GEN-2019-037 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1012 | 3.1015 | 0.0003
GEN-2019-037 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.3259 | 6.3285 | 0.0026
GEN-2019-037 | 01 NORTH | 655901 | BROOKBNK-MW7 | 115 | 8.1124 | 8.1165 | 0.0041
GEN-2019-037 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 8.5872 | 8.5921 | 0.0049
GEN-2019-037 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 9.5005 | 9.5075 | 0.007
GEN-2019-037 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 18.3947 | 18.4244 | 0.0297
GEN-2019-037 | 01 NORTH | 655907 | E.NEWTWN-MW7 | 115 | 10.9948 | 11.0044 | 0.0096
GEN-2019-037 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 8.0171 | 8.0218 | 0.0047
GEN-2019-037 | 01 NORTH | 655910 | LINDAHLS-MW7 | 115 | 5.7267 | 5.7278 | 0.0011
GEN-2019-037 | 01 NORTH | 655911 | SIMPSON -MW7 | 115 | 3.9027 | 3.9032 | 0.0005
GEN-2019-037 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 6.0147 | 6.0171 | 0.0024
GEN-2019-037 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.1263 | 4.1273 | 0.001
GEN-2019-037 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 6.9776 | 6.9805 | 0.0029
GEN-2019-037 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 6.6533 | 6.656 | 0.0027
GEN-2019-037 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 5.9234 | 5.9255 | 0.0021
GEN-2019-037 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 10.9499 | 10.9596 | 0.0097
GEN-2019-037 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 12.4095 | 12.4221 | 0.0126
GEN-2019-037 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.4157 | 3.4164 | 0.0007
GEN-2019-037 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.7534 | 6.7564 | 0.003
GEN-2019-037 | 01 NORTH | 655946 | POWERSLK-MW7 | 115 | 4.7903 | 4.7911 | 0.0008
GEN-2019-037 | 01 NORTH | 655947 | PWRSLKTP-MW7 | 115 | 7.4284 | 7.4303 | 0.0019
GEN-2019-037 | 01 NORTH | 655948 | LIBERTY -MW7 | 115 | 6.7396 | 6.7411 | 0.0015
GEN-2019-037 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 8.6128 | 8.617 | 0.0042
GEN-2019-037 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.5055 | 5.5074 | 0.0019
GEN-2019-037 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.6118 | 4.6131 | 0.0013
GEN-2019-037 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 16.6804 | 16.6894 | 0.009
GEN-2019-037 | 01 NORTH | 655960 | BIGBEND -MW7 | 115 | 5.2478 | 5.25 | 0.0022
GEN-2019-037 | 01 NORTH | 655963 | HOWIE -MW7 | 115 | 4.2791 | 4.2806 | 0.0015
GEN-2019-037 | 01 NORTH | 655967 | SATTER -MW7 | 115 | 8.0654 | 8.0701 | 0.0047
GEN-2019-037 | 01 NORTH | 655968 | MUSKRAT -MW7 | 115 | 4.4149 | 4.4165 | 0.0016
GEN-2019-037 | 01 NORTH | 657741 | ROUGHRIDER 4 | 230 | 16.1229 | 16.1263 | 0.0034
GEN-2019-037 | 01 NORTH | 657742 | OLIVERWND3 4 | 230 | 11.2774 | 11.279 | 0.0016
GEN-2019-037 | 01 NORTH | 657751 | CENTER 4 | 230 | 21.0466 | 21.0509 | 0.0043
GEN-2019-037 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.8766 | 23.8817 | 0.0051
GEN-2019-037 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.4276 | 4.4278 | 0.0002
GEN-2019-037 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.6432 | 12.6451 | 0.0019
GEN-2019-037 | 01 NORTH | 657804 | MPC-VCY8 | 69 | 2.2674 | 2.2674 | 0
GEN-2019-037 | 01 NORTH | 657848 | YNG2 4 | 230 | 19.3593 | 19.3624 | 0.0031
GEN-2019-037 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.272 | 3.272 | 0
GEN-2019-037 | 01 NORTH | 657951 | CNTSHNT3 | 345 | 12.6432 | 12.6451 | 0.0019
GEN-2019-037 | 01 NORTH | 658209 | MOORHDW4 | 230 | 7.2375 | 7.2377 | 0.0002
GEN-2019-037 | 01 NORTH | 659060 | FINSTAD345 | 345 | 6.6255 | 6.6373 | 0.0118
GEN-2019-037 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 16.1299 | 16.2445 | 0.1146
GEN-2019-037 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.76 | 18.0623 | 0.3023
GEN-2019-037 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 24.0349 | 24.2688 | 0.2339
GEN-2019-037 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.4146 | 6.4202 | 0.0056
GEN-2019-037 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3872 | 5.393 | 0.0058
GEN-2019-037 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.1961 | 4.1972 | 0.0011
GEN-2019-037 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.2141 | 7.2166 | 0.0025
GEN-2019-037 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 5.0719 | 5.0728 | 0.0009
GEN-2019-037 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.3904 | 6.3924 | 0.002
GEN-2019-037 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.0157 | 12.0275 | 0.0118
GEN-2019-037 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 12.5841 | 12.5902 | 0.0061
GEN-2019-037 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 5.2683 | 5.2709 | 0.0026
GEN-2019-037 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.011 | 6.0148 | 0.0038
GEN-2019-037 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 8.8937 | 8.8982 | 0.0045
GEN-2019-037 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.5088 | 6.5093 | 0.0005
GEN-2019-037 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.039 | 11.044 | 0.005
GEN-2019-037 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.2978 | 6.2998 | 0.002
GEN-2019-037 | 01 NORTH | 659165 | CROCKER_-BE3 | 345 | 6.5 | 6.5013 | 0.0013
GEN-2019-037 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.4243 | 3.4247 | 0.0004
GEN-2019-037 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.9464 | 13.9575 | 0.0111
GEN-2019-037 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.4412 | 10.4624 | 0.0212
GEN-2019-037 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.3948 | 4.3957 | 0.0009
GEN-2019-037 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7214 | 3.7222 | 0.0008
GEN-2019-037 | 01 NORTH | 659187 | GROTON__-BE7 | 115 | 17.7545 | 17.7573 | 0.0028
GEN-2019-037 | 01 NORTH | 659190 | ND.PW1__-BE7 | 115 | 7.439 | 7.4406 | 0.0016
GEN-2019-037 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.9097 | 22.103 | 0.1933
GEN-2019-037 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.3187 | 10.3206 | 0.0019
GEN-2019-037 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.42 | 15.5246 | 0.1046
GEN-2019-037 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 16.1299 | 16.2445 | 0.1146
GEN-2019-037 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.6302 | 9.6383 | 0.0081
GEN-2019-037 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.2189 | 7.2341 | 0.0152
GEN-2019-037 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.266 | 7.2707 | 0.0047
GEN-2019-037 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.4599 | 5.4613 | 0.0014
GEN-2019-037 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.1489 | 4.1494 | 0.0005
GEN-2019-037 | 01 NORTH | 659275 | GROTON_G-BE7 | 115 | 17.3733 | 17.3759 | 0.0026
GEN-2019-037 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 2.5899 | 2.59 | 0.0001
GEN-2019-037 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 7.0563 | 7.0589 | 0.0026
GEN-2019-037 | 01 NORTH | 659288 | DAY_CNTY-PP7 | 115 | 3.9893 | 3.9894 | 0.0001
GEN-2019-037 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 7.8754 | 7.8768 | 0.0014
GEN-2019-037 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3962 | 11.4121 | 0.0159
GEN-2019-037 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3082 | 2.3084 | 0.0002
GEN-2019-037 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.6357 | 9.6412 | 0.0055
GEN-2019-037 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 8.4085 | 8.4176 | 0.0091
GEN-2019-037 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.1504 | 11.16 | 0.0096
GEN-2019-037 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.2607 | 8.2708 | 0.0101
GEN-2019-037 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 11.8765 | 11.8883 | 0.0118
GEN-2019-037 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.5037 | 6.5042 | 0.0005
GEN-2019-037 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.1714 | 12.1759 | 0.0045
GEN-2019-037 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.1715 | 12.176 | 0.0045
GEN-2019-037 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.621 | 7.6254 | 0.0044
GEN-2019-037 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 7.0563 | 7.0589 | 0.0026
GEN-2019-037 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.3886 | 9.4095 | 0.0209
GEN-2019-037 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.7586 | 11.7695 | 0.0109
GEN-2019-037 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.2583 | 7.2686 | 0.0103
GEN-2019-037 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.1469 | 14.16 | 0.0131
GEN-2019-037 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.7294 | 8.7413 | 0.0119
GEN-2019-037 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 17.7974 | 17.8114 | 0.014
GEN-2019-037 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.6772 | 4.6802 | 0.003
GEN-2019-037 | 01 NORTH | 659408 | CAMPBL._-PP4 | 230 | 3.7376 | 3.7378 | 0.0002
GEN-2019-037 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 16.1299 | 16.2445 | 0.1146
GEN-2019-037 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1961 | 4.1972 | 0.0011
GEN-2019-037 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.76 | 18.0623 | 0.3023
GEN-2019-037 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2978 | 6.2998 | 0.002
GEN-2019-037 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.76 | 18.0623 | 0.3023
GEN-2019-037 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.2607 | 8.2708 | 0.0101
GEN-2019-037 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.3602 | 6.3622 | 0.002
GEN-2019-037 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.3294 | 6.3314 | 0.002
GEN-2019-037 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9347 | 1.9348 | 0.0001
GEN-2019-037 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.741 | 1.741 | 0
GEN-2019-037 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.6168 | 6.6188 | 0.002
GEN-2019-037 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6267 | 3.6271 | 0.0004
GEN-2019-037 | 01 NORTH | 659454 | LINDAHLWND 7 | 115 | 5.2868 | 5.2876 | 0.0008
GEN-2019-037 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 17.7012 | 17.7151 | 0.0139
GEN-2019-037 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 17.7126 | 17.7266 | 0.014
GEN-2019-037 | 01 NORTH | 659472 | CROCKER_-UA3 | 345 | 5.6015 | 5.6025 | 0.001
GEN-2019-037 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.0604 | 6.0655 | 0.0051
GEN-2019-037 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 10.1308 | 10.1335 | 0.0027
GEN-2019-037 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9347 | 1.9348 | 0.0001
GEN-2019-037 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 7.7241 | 7.7315 | 0.0074
GEN-2019-037 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.6797 | 6.6834 | 0.0037
GEN-2019-037 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.4751 | 9.4765 | 0.0014
GEN-2019-037 | 01 NORTH | 661016 | COYOTE 3 | 345 | 8.5873 | 8.588 | 0.0007
GEN-2019-037 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 16.3069 | 16.3115 | 0.0046
GEN-2019-037 | 01 NORTH | 661053 | MANDAN 4 | 230 | 16.395 | 16.4017 | 0.0067
GEN-2019-037 | 01 NORTH | 661060 | LINTON 7 | 115 | 1.3999 | 1.3999 | 0
GEN-2019-037 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.0157 | 12.0275 | 0.0118
GEN-2019-037 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 12.543 | 12.5491 | 0.0061
GEN-2019-037 | 01 NORTH | 672603 | BDV 4 | 230 | 4.9813 | 4.9819 | 0.0006
GEN-2019-037 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.2133 | 3.2145 | 0.0012
GEN-2019-037 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 11.0999 | 11.4023 | 0.3024
GEN-2018-065 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9087 | 14.9095 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8762 | 13.8769 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7367 | 15.7375 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1786 | 28.1843 | 0.0057
GEN-2018-065 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3169 | 28.3192 | 0.0023
GEN-2018-065 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3731 | 23.3747 | 0.0016
GEN-2018-065 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7703 | 26.7724 | 0.0021
GEN-2018-065 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7491 | 9.7493 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.2037 | 15.2043 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0603 | 26.0623 | 0.002
GEN-2018-065 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1191 | 10.1194 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1418 | 15.1426 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6243 | 16.6252 | 0.0009
GEN-2018-065 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3396 | 16.3405 | 0.0009
GEN-2018-065 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6426 | 7.6461 | 0.0035
GEN-2018-065 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0797 | 4.0803 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2697 | 6.2704 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.884 | 3.8842 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.3903 | 5.3908 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.912 | 3.9122 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.36 | 5.3617 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5383 | 7.5428 | 0.0045
GEN-2018-065 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6911 | 10.6963 | 0.0052
GEN-2018-065 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.9334 | 4.9346 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.5695 | 4.5701 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4485 | 5.4489 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6753 | 3.6754 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.5789 | 13.6105 | 0.0316
GEN-2018-065 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5593 | 10.5682 | 0.0089
GEN-2018-065 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.9303 | 18.9459 | 0.0156
GEN-2018-065 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4691 | 6.4703 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 10.3057 | 10.3141 | 0.0084
GEN-2018-065 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.1641 | 6.1659 | 0.0018
GEN-2018-065 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.7893 | 13.7979 | 0.0086
GEN-2018-065 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9665 | 12.9735 | 0.007
GEN-2018-065 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 4.0482 | 4.0485 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.3944 | 4.3947 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.6805 | 5.6816 | 0.0011
GEN-2018-065 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.0248 | 11.0321 | 0.0073
GEN-2018-065 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3835 | 11.3866 | 0.0031
GEN-2018-065 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3665 | 5.3673 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3165 | 7.3184 | 0.0019
GEN-2018-065 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3263 | 9.3275 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2927 | 11.2937 | 0.001
GEN-2018-065 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1644 | 8.1647 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7258 | 7.7262 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7188 | 4.7189 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.6854 | 5.6866 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9582 | 6.9835 | 0.0253
GEN-2018-065 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5139 | 14.5347 | 0.0208
GEN-2018-065 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.351 | 5.3527 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3449 | 8.3466 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4537 | 7.455 | 0.0013
GEN-2018-065 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.6599 | 11.6818 | 0.0219
GEN-2018-065 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.4403 | 9.4542 | 0.0139
GEN-2018-065 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.08 | 9.0923 | 0.0123
GEN-2018-065 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.775 | 13.7935 | 0.0185
GEN-2018-065 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.3982 | 11.4191 | 0.0209
GEN-2018-065 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3678 | 22.3684 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9306 | 8.9312 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9785 | 20.9804 | 0.0019
GEN-2018-065 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 16.0033 | 16.0048 | 0.0015
GEN-2018-065 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.8132 | 15.8147 | 0.0015
GEN-2018-065 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.6115 | 8.6229 | 0.0114
GEN-2018-065 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7596 | 8.7598 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7596 | 8.7598 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.0252 | 9.0618 | 0.0366
GEN-2018-065 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.4049 | 21.4054 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.3914 | 16.3919 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3494 | 16.3499 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2601 | 8.2993 | 0.0392
GEN-2018-065 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.7952 | 6.8359 | 0.0407
GEN-2018-065 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2719 | 2.2723 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.0252 | 9.0618 | 0.0366
GEN-2018-065 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.035 | 9.0717 | 0.0367
GEN-2018-065 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5321 | 8.5648 | 0.0327
GEN-2018-065 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.762 | 11.7785 | 0.0165
GEN-2018-065 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.7986 | 11.8153 | 0.0167
GEN-2018-068 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.8968 | 14.9095 | 0.0127
GEN-2018-068 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8666 | 13.8769 | 0.0103
GEN-2018-068 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7242 | 15.7375 | 0.0133
GEN-2018-068 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.0949 | 28.1843 | 0.0894
GEN-2018-068 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.2827 | 28.3192 | 0.0365
GEN-2018-068 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3505 | 23.3747 | 0.0242
GEN-2018-068 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7398 | 26.7724 | 0.0326
GEN-2018-068 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7452 | 9.7493 | 0.0041
GEN-2018-068 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1941 | 15.2043 | 0.0102
GEN-2018-068 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0314 | 26.0623 | 0.0309
GEN-2018-068 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1143 | 10.1194 | 0.0051
GEN-2018-068 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1295 | 15.1426 | 0.0131
GEN-2018-068 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6112 | 16.6252 | 0.014
GEN-2018-068 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3269 | 16.3405 | 0.0136
GEN-2018-068 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.5906 | 7.6461 | 0.0555
GEN-2018-068 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0709 | 4.0803 | 0.0094
GEN-2018-068 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2594 | 6.2704 | 0.011
GEN-2018-068 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8816 | 3.8842 | 0.0026
GEN-2018-068 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.3819 | 5.3908 | 0.0089
GEN-2018-068 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.9093 | 3.9122 | 0.0029
GEN-2018-068 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.3348 | 5.3617 | 0.0269
GEN-2018-068 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.4729 | 7.5428 | 0.0699
GEN-2018-068 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6139 | 10.6963 | 0.0824
GEN-2018-068 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.9153 | 4.9346 | 0.0193
GEN-2018-068 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.5602 | 4.5701 | 0.0099
GEN-2018-068 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4425 | 5.4489 | 0.0064
GEN-2018-068 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6737 | 3.6754 | 0.0017
GEN-2018-068 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.1252 | 13.6105 | 0.4853
GEN-2018-068 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.4283 | 10.5682 | 0.1399
GEN-2018-068 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.7025 | 18.9459 | 0.2434
GEN-2018-068 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4512 | 6.4703 | 0.0191
GEN-2018-068 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 10.182 | 10.3141 | 0.1321
GEN-2018-068 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.1377 | 6.1659 | 0.0282
GEN-2018-068 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.6622 | 13.7979 | 0.1357
GEN-2018-068 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.8618 | 12.9735 | 0.1117
GEN-2018-068 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 4.0438 | 4.0485 | 0.0047
GEN-2018-068 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.3913 | 4.3947 | 0.0034
GEN-2018-068 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.6632 | 5.6816 | 0.0184
GEN-2018-068 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9176 | 11.0321 | 0.1145
GEN-2018-068 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3371 | 11.3866 | 0.0495
GEN-2018-068 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3547 | 5.3673 | 0.0126
GEN-2018-068 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.289 | 7.3184 | 0.0294
GEN-2018-068 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3079 | 9.3275 | 0.0196
GEN-2018-068 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2779 | 11.2937 | 0.0158
GEN-2018-068 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1598 | 8.1647 | 0.0049
GEN-2018-068 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7188 | 7.7262 | 0.0074
GEN-2018-068 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7173 | 4.7189 | 0.0016
GEN-2018-068 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.6681 | 5.6866 | 0.0185
GEN-2018-068 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.6023 | 6.9835 | 0.3812
GEN-2018-068 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.2109 | 14.5347 | 0.3238
GEN-2018-068 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3262 | 5.3527 | 0.0265
GEN-2018-068 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.319 | 8.3466 | 0.0276
GEN-2018-068 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.435 | 7.455 | 0.02
GEN-2018-068 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.3437 | 11.6818 | 0.3381
GEN-2018-068 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.239 | 9.4542 | 0.2152
GEN-2018-068 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.9001 | 9.0923 | 0.1922
GEN-2018-068 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.5046 | 13.7935 | 0.2889
GEN-2018-068 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.0958 | 11.4191 | 0.3233
GEN-2018-068 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.359 | 22.3684 | 0.0094
GEN-2018-068 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9215 | 8.9312 | 0.0097
GEN-2018-068 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9494 | 20.9804 | 0.031
GEN-2018-068 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.9812 | 16.0048 | 0.0236
GEN-2018-068 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.7917 | 15.8147 | 0.023
GEN-2018-068 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.4454 | 8.6229 | 0.1775
GEN-2018-068 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7568 | 8.7598 | 0.003
GEN-2018-068 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7568 | 8.7598 | 0.003
GEN-2018-068 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 8.513 | 9.0618 | 0.5488
GEN-2018-068 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.3968 | 21.4054 | 0.0086
GEN-2018-068 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.3837 | 16.3919 | 0.0082
GEN-2018-068 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3418 | 16.3499 | 0.0081
GEN-2018-068 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 7.7176 | 8.2993 | 0.5817
GEN-2018-068 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.2423 | 6.8359 | 0.5936
GEN-2018-068 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.266 | 2.2723 | 0.0063
GEN-2018-068 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 8.513 | 9.0618 | 0.5488
GEN-2018-068 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 8.5217 | 9.0717 | 0.55
GEN-2018-068 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.0729 | 8.5648 | 0.4919
GEN-2018-068 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.5213 | 11.7785 | 0.2572
GEN-2018-068 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.5564 | 11.8153 | 0.2589
GEN-2018-083 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9018 | 14.9095 | 0.0077
GEN-2018-083 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8707 | 13.8769 | 0.0062
GEN-2018-083 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7295 | 15.7375 | 0.008
GEN-2018-083 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2305 | 12.2349 | 0.0044
GEN-2018-083 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5859 | 15.5878 | 0.0019
GEN-2018-083 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1302 | 28.1843 | 0.0541
GEN-2018-083 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.2971 | 28.3192 | 0.0221
GEN-2018-083 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3601 | 23.3747 | 0.0146
GEN-2018-083 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7527 | 26.7724 | 0.0197
GEN-2018-083 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.248 | 10.2492 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7468 | 9.7493 | 0.0025
GEN-2018-083 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3866 | 9.3886 | 0.002
GEN-2018-083 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1982 | 15.2043 | 0.0061
GEN-2018-083 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8955 | 17.9039 | 0.0084
GEN-2018-083 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7634 | 17.7719 | 0.0085
GEN-2018-083 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0436 | 26.0623 | 0.0187
GEN-2018-083 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2891 | 15.2952 | 0.0061
GEN-2018-083 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1163 | 10.1194 | 0.0031
GEN-2018-083 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7275 | 5.7279 | 0.0004
GEN-2018-083 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1347 | 15.1426 | 0.0079
GEN-2018-083 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6167 | 16.6252 | 0.0085
GEN-2018-083 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1116 | 15.1157 | 0.0041
GEN-2018-083 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3323 | 16.3405 | 0.0082
GEN-2018-083 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3178 | 9.3198 | 0.002
GEN-2018-083 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6268 | 7.6461 | 0.0193
GEN-2018-083 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0771 | 4.0803 | 0.0032
GEN-2018-083 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6111 | 4.6139 | 0.0028
GEN-2018-083 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.265 | 6.2704 | 0.0054
GEN-2018-083 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8829 | 3.8842 | 0.0013
GEN-2018-083 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5255 | 7.5428 | 0.0173
GEN-2018-083 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.381 | 20.4621 | 0.0811
GEN-2018-083 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.2267 | 17.2846 | 0.0579
GEN-2018-083 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.3706 | 17.4268 | 0.0562
GEN-2018-083 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.5724 | 10.6963 | 0.1239
GEN-2018-083 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.4947 | 10.5434 | 0.0487
GEN-2018-083 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.0693 | 23.1799 | 0.1106
GEN-2018-083 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.2538 | 10.2965 | 0.0427
GEN-2018-083 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.9604 | 12.0245 | 0.0641
GEN-2018-083 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.4874 | 18.5516 | 0.0642
GEN-2018-083 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.9874 | 20.0618 | 0.0744
GEN-2018-083 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2772 | 6.2875 | 0.0103
GEN-2018-083 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.931 | 5.9354 | 0.0044
GEN-2018-083 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7135 | 5.7156 | 0.0021
GEN-2018-083 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9399 | 3.9405 | 0.0006
GEN-2018-083 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.1056 | 5.1094 | 0.0038
GEN-2018-083 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1448 | 17.1539 | 0.0091
GEN-2018-083 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4461 | 5.4489 | 0.0028
GEN-2018-083 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6747 | 3.6754 | 0.0007
GEN-2018-083 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.318 | 13.6105 | 0.2925
GEN-2018-083 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.4869 | 10.5682 | 0.0813
GEN-2018-083 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.8146 | 18.9459 | 0.1313
GEN-2018-083 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4582 | 6.4703 | 0.0121
GEN-2018-083 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3825 | 11.387 | 0.0045
GEN-2018-083 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.4952 | 23.518 | 0.0228
GEN-2018-083 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.2102 | 44.2293 | 0.0191
GEN-2018-083 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.7304 | 13.7979 | 0.0675
GEN-2018-083 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9146 | 12.9735 | 0.0589
GEN-2018-083 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7273 | 11.7308 | 0.0035
GEN-2018-083 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.0829 | 6.0876 | 0.0047
GEN-2018-083 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.8566 | 11.0321 | 0.1755
GEN-2018-083 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3167 | 11.3866 | 0.0699
GEN-2018-083 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7798 | 4.7822 | 0.0024
GEN-2018-083 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2495 | 4.2507 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3604 | 5.3673 | 0.0069
GEN-2018-083 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3025 | 7.3184 | 0.0159
GEN-2018-083 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3266 | 9.3288 | 0.0022
GEN-2018-083 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3163 | 9.3275 | 0.0112
GEN-2018-083 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2848 | 11.2937 | 0.0089
GEN-2018-083 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.162 | 8.1647 | 0.0027
GEN-2018-083 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.9936 | 4.9949 | 0.0013
GEN-2018-083 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7221 | 7.7262 | 0.0041
GEN-2018-083 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.718 | 4.7189 | 0.0009
GEN-2018-083 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9244 | 6.9835 | 0.0591
GEN-2018-083 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.4766 | 14.5347 | 0.0581
GEN-2018-083 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.348 | 5.3527 | 0.0047
GEN-2018-083 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2305 | 12.2349 | 0.0044
GEN-2018-083 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.2953 | 5.3006 | 0.0053
GEN-2018-083 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3307 | 8.3466 | 0.0159
GEN-2018-083 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4435 | 7.455 | 0.0115
GEN-2018-083 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.4786 | 11.6818 | 0.2032
GEN-2018-083 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.3252 | 9.4542 | 0.129
GEN-2018-083 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 22.9896 | 23.011 | 0.0214
GEN-2018-083 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.9772 | 9.0923 | 0.1151
GEN-2018-083 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7417 | 13.7935 | 0.0518
GEN-2018-083 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.2249 | 11.4191 | 0.1942
GEN-2018-083 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6839 | 29.6902 | 0.0063
GEN-2018-083 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3608 | 22.3684 | 0.0076
GEN-2018-083 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.735 | 28.7456 | 0.0106
GEN-2018-083 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.1157 | 25.1221 | 0.0064
GEN-2018-083 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2503 | 32.2577 | 0.0074
GEN-2018-083 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.6645 | 3.6665 | 0.002
GEN-2018-083 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.5802 | 17.6119 | 0.0317
GEN-2018-083 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.031 | 21.0502 | 0.0192
GEN-2018-083 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9159 | 20.9321 | 0.0162
GEN-2018-083 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3769 | 21.3861 | 0.0092
GEN-2018-083 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5821 | 25.5957 | 0.0136
GEN-2018-083 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1009 | 22.1094 | 0.0085
GEN-2018-083 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.1324 | 32.1471 | 0.0147
GEN-2018-083 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.6164 | 25.6258 | 0.0094
GEN-2018-083 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 10.8645 | 10.8675 | 0.003
GEN-2018-083 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.928 | 8.9312 | 0.0032
GEN-2018-083 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9623 | 20.9804 | 0.0181
GEN-2018-083 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.9908 | 16.0048 | 0.014
GEN-2018-083 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9623 | 20.9804 | 0.0181
GEN-2018-083 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.801 | 15.8147 | 0.0137
GEN-2018-083 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5362 | 7.5375 | 0.0013
GEN-2018-083 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.5166 | 8.6229 | 0.1063
GEN-2018-083 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9766 | 9.9799 | 0.0033
GEN-2018-083 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9711 | 6.9723 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8256 | 5.8264 | 0.0008
GEN-2018-083 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7578 | 8.7598 | 0.002
GEN-2018-083 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7578 | 8.7598 | 0.002
GEN-2018-083 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 8.9497 | 9.0618 | 0.1121
GEN-2018-083 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.3984 | 21.4054 | 0.007
GEN-2018-083 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.386 | 16.3919 | 0.0059
GEN-2018-083 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.344 | 16.3499 | 0.0059
GEN-2018-083 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2102 | 8.2993 | 0.0891
GEN-2018-083 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.7776 | 6.8359 | 0.0583
GEN-2018-083 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 1.7531 | 2.2723 | 0.5192
GEN-2018-083 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 8.9497 | 9.0618 | 0.1121
GEN-2018-083 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 8.9594 | 9.0717 | 0.1123
GEN-2018-083 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.4646 | 8.5648 | 0.1002
GEN-2018-083 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.3651 | 11.7785 | 0.4134
GEN-2018-083 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.3992 | 11.8153 | 0.4161
GEN-2018-125 | 02 NEBRASKA | 530555 | COLBY 3 | 115 | 6.0758 | 6.077 | 0.0012
GEN-2018-125 | 02 NEBRASKA | 530559 | PH RUN 3 | 115 | 4.6675 | 4.6681 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 7.612 | 7.6164 | 0.0044
GEN-2018-125 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 10.5516 | 10.5554 | 0.0038
GEN-2018-125 | 02 NEBRASKA | 530644 | COLBY 2 | 69 | 3.6312 | 3.6314 | 0.0002
GEN-2018-125 | 02 NEBRASKA | 530702 | BUCKEYE_230 | 230 | 7.8518 | 7.8538 | 0.002
GEN-2018-125 | 02 NEBRASKA | 531351 | BREWSTR3 | 115 | 3.2159 | 3.2162 | 0.0003
GEN-2018-125 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.5697 | 12.5764 | 0.0067
GEN-2018-125 | 02 NEBRASKA | 531449 | HOLCOMB7 | 345 | 9.0393 | 9.0416 | 0.0023
GEN-2018-125 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.1228 | 6.1282 | 0.0054
GEN-2018-125 | 02 NEBRASKA | 531464 | SETAB 3 | 115 | 10.3871 | 10.3887 | 0.0016
GEN-2018-125 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.7417 | 6.7444 | 0.0027
GEN-2018-125 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 11.4371 | 11.4396 | 0.0025
GEN-2018-125 | 02 NEBRASKA | 531623 | EASTFORK3 | 115 | 10.0075 | 10.0117 | 0.0042
GEN-2018-125 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.4373 | 5.4415 | 0.0042
GEN-2018-125 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.1893 | 7.2095 | 0.0202
GEN-2018-125 | 02 NEBRASKA | 579450 | GEN-2016-075 | 345 | 6.6525 | 6.6559 | 0.0034
GEN-2018-125 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 8.0647 | 8.0752 | 0.0105
GEN-2018-125 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2264 | 12.2349 | 0.0085
GEN-2018-125 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.072 | 6.0859 | 0.0139
GEN-2018-125 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.1182 | 6.177 | 0.0588
GEN-2018-125 | 02 NEBRASKA | 588220 | GEN-2016-147 | 115 | 4.4271 | 4.4293 | 0.0022
GEN-2018-125 | 02 NEBRASKA | 640050 | AINSWND7 | 115 | 3.7403 | 3.7407 | 0.0004
GEN-2018-125 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.2553 | 7.258 | 0.0027
GEN-2018-125 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.5334 | 9.5864 | 0.053
GEN-2018-125 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.659 | 14.6896 | 0.0306
GEN-2018-125 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.8773 | 4.8806 | 0.0033
GEN-2018-125 | 02 NEBRASKA | 640083 | BEVERLY8 | 69 | 4.4603 | 4.4619 | 0.0016
GEN-2018-125 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.1878 | 7.1976 | 0.0098
GEN-2018-125 | 02 NEBRASKA | 640094 | C.CREEK7 | 115 | 7.3578 | 7.3625 | 0.0047
GEN-2018-125 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.485 | 3.4857 | 0.0007
GEN-2018-125 | 02 NEBRASKA | 640100 | CAMBRIG7 | 115 | 4.2795 | 4.2813 | 0.0018
GEN-2018-125 | 02 NEBRASKA | 640101 | CAMBRIG8 | 69 | 2.312 | 2.3124 | 0.0004
GEN-2018-125 | 02 NEBRASKA | 640102 | CANADAY4 | 230 | 6.2835 | 6.2904 | 0.0069
GEN-2018-125 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2853 | 5.2865 | 0.0012
GEN-2018-125 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.294 | 10.2965 | 0.0025
GEN-2018-125 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.0219 | 12.0245 | 0.0026
GEN-2018-125 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.1473 | 6.1507 | 0.0034
GEN-2018-125 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8567 | 3.8575 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 640167 | ENDERS 7 | 115 | 3.8682 | 3.8705 | 0.0023
GEN-2018-125 | 02 NEBRASKA | 640168 | ENDERS 8 | 69 | 3.1485 | 3.1494 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9056 | 9.9083 | 0.0027
GEN-2018-125 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.308 | 4.3083 | 0.0003
GEN-2018-125 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 15.3897 | 15.6269 | 0.2372
GEN-2018-125 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 18.9606 | 19.087 | 0.1264
GEN-2018-125 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1064 | 17.1539 | 0.0475
GEN-2018-125 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.5055 | 23.5409 | 0.0354
GEN-2018-125 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.5355 | 7.543 | 0.0075
GEN-2018-125 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.4086 | 19.4267 | 0.0181
GEN-2018-125 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.3802 | 4.3819 | 0.0017
GEN-2018-125 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5472 | 3.5478 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.2728 | 6.2769 | 0.0041
GEN-2018-125 | 02 NEBRASKA | 640238 | JEFFREY7 | 115 | 6.1947 | 6.1987 | 0.004
GEN-2018-125 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 12.5569 | 12.5694 | 0.0125
GEN-2018-125 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.7053 | 9.7149 | 0.0096
GEN-2018-125 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.2904 | 12.3066 | 0.0162
GEN-2018-125 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.6293 | 8.6829 | 0.0536
GEN-2018-125 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.7112 | 14.7516 | 0.0404
GEN-2018-125 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 9.2325 | 9.2473 | 0.0148
GEN-2018-125 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.3945 | 8.4017 | 0.0072
GEN-2018-125 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2083 | 4.2093 | 0.001
GEN-2018-125 | 02 NEBRASKA | 640265 | MALONEY7 | 115 | 11.4965 | 11.5158 | 0.0193
GEN-2018-125 | 02 NEBRASKA | 640267 | MAXWELS7 | 115 | 6.8144 | 6.8203 | 0.0059
GEN-2018-125 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.626 | 8.6347 | 0.0087
GEN-2018-125 | 02 NEBRASKA | 640270 | MCCOOK 8 | 69 | 4.5726 | 4.5741 | 0.0015
GEN-2018-125 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3705 | 11.387 | 0.0165
GEN-2018-125 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.6775 | 14.6852 | 0.0077
GEN-2018-125 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7268 | 5.7276 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4163 | 7.4229 | 0.0066
GEN-2018-125 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.503 | 23.518 | 0.015
GEN-2018-125 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.2181 | 44.2293 | 0.0112
GEN-2018-125 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 13.1296 | 13.184 | 0.0544
GEN-2018-125 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 18.6295 | 18.6799 | 0.0504
GEN-2018-125 | 02 NEBRASKA | 640288 | N.PLATT8 | 69 | 5.118 | 5.1203 | 0.0023
GEN-2018-125 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.8271 | 7.8471 | 0.02
GEN-2018-125 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.736 | 14.7732 | 0.0372
GEN-2018-125 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.4601 | 2.4607 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4653 | 2.4656 | 0.0003
GEN-2018-125 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.2301 | 8.2477 | 0.0176
GEN-2018-125 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.6842 | 16.7023 | 0.0181
GEN-2018-125 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9299 | 4.9308 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.3378 | 6.3555 | 0.0177
GEN-2018-125 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 11.3032 | 11.3199 | 0.0167
GEN-2018-125 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.4767 | 7.4869 | 0.0102
GEN-2018-125 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.2078 | 13.224 | 0.0162
GEN-2018-125 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.6879 | 6.6904 | 0.0025
GEN-2018-125 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.8888 | 9.8943 | 0.0055
GEN-2018-125 | 02 NEBRASKA | 640355 | ST.PAUL7 | 115 | 3.9748 | 3.9757 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.2269 | 4.2293 | 0.0024
GEN-2018-125 | 02 NEBRASKA | 640360 | STAPLETON 8 | 69 | 3.4556 | 3.4565 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.6543 | 4.6572 | 0.0029
GEN-2018-125 | 02 NEBRASKA | 640366 | STOCKVL8 | 69 | 3.4007 | 3.4016 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.4026 | 10.5829 | 0.1803
GEN-2018-125 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.0119 | 9.0234 | 0.0115
GEN-2018-125 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.3318 | 9.3407 | 0.0089
GEN-2018-125 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.3869 | 8.3893 | 0.0024
GEN-2018-125 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0817 | 4.0822 | 0.0005
GEN-2018-125 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5277 | 2.5278 | 0.0001
GEN-2018-125 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.826 | 3.8269 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.2299 | 5.2432 | 0.0133
GEN-2018-125 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 8.1291 | 8.1399 | 0.0108
GEN-2018-125 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2264 | 12.2349 | 0.0085
GEN-2018-125 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7455 | 6.7478 | 0.0023
GEN-2018-125 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4552 | 5.4566 | 0.0014
GEN-2018-125 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 22.997 | 23.011 | 0.014
GEN-2018-125 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.4086 | 19.4267 | 0.0181
GEN-2018-125 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 17.3813 | 17.3976 | 0.0163
GEN-2018-125 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 17.0678 | 17.0846 | 0.0168
GEN-2018-125 | 02 NEBRASKA | 648513 | GRPR1 3 | 345 | 7.0176 | 7.0215 | 0.0039
GEN-2018-125 | 02 NEBRASKA | 648520 | GRPR2 3 | 345 | 6.6525 | 6.6559 | 0.0034
GEN-2018-125 | 02 NEBRASKA | 648527 | GRPR3 3 | 345 | 7.0176 | 7.0215 | 0.0039
GEN-2018-125 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6061 | 17.6119 | 0.0058
GEN-2018-125 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9256 | 20.9321 | 0.0065
GEN-2018-125 | 02 NEBRASKA | 652532 | GR PRAIRIE 3 | 345 | 7.4077 | 7.4123 | 0.0046
GEN-2018-125 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 7.4077 | 7.4123 | 0.0046
GEN-2018-125 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.76 | 12.8103 | 0.0503
GEN-2018-125 | 02 NEBRASKA | 653572 | SIDNEY 7 | 115 | 4.5293 | 4.5316 | 0.0023
GEN-2018-125 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.6359 | 12.6851 | 0.0492
GEN-2018-125 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 5.973 | 5.9843 | 0.0113
GEN-2018-125 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.3165 | 6.3256 | 0.0091
GEN-2018-125 | 02 NEBRASKA | 659135 | STEGALL_-MB3 | 345 | 4.8769 | 4.8804 | 0.0035
GEN-2018-125 | 02 NEBRASKA | 659210 | SIDNEY__-MB4 | 230 | 6.7281 | 6.7383 | 0.0102
GEN-2018-125 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 5.973 | 5.9843 | 0.0113
GEN-2018-125 | 02 NEBRASKA | 659426 | SD.LS-LR-MB3 | 345 | 5.973 | 5.9843 | 0.0113
GEN-2018-125 | 02 NEBRASKA | 659800 | GRANTNB_-TS7 | 115 | 6.4475 | 6.4543 | 0.0068
GEN-2018-125 | 02 NEBRASKA | 659801 | OGALALA_-TS7 | 115 | 14.736 | 14.7732 | 0.0372
GEN-2018-125 | 02 NEBRASKA | 659824 | MCONGHY_-TS7 | 115 | 5.5251 | 5.5303 | 0.0052
GEN-2018-125 | 02 NEBRASKA | 659825 | ARTHUR__-TS7 | 115 | 2.1649 | 2.1657 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 659826 | HYANNIS_-TS7 | 115 | 1.22 | 1.2203 | 0.0003
GEN-2018-125 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.7968 | 7.8067 | 0.0099
GEN-2018-125 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9675 | 9.9799 | 0.0124
GEN-2018-125 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9699 | 6.9723 | 0.0024
GEN-2018-125 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8247 | 5.8264 | 0.0017
GEN-2018-125 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 6.6196 | 7.052 | 0.4324
GEN-2018-125 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 6.9341 | 7.3653 | 0.4312
GEN-2018-131 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9095 | 14.9188 | 0.0093
GEN-2018-131 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8769 | 13.8844 | 0.0075
GEN-2018-131 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7375 | 15.7472 | 0.0097
GEN-2018-131 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5878 | 15.5903 | 0.0025
GEN-2018-131 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1843 | 28.25 | 0.0657
GEN-2018-131 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3192 | 28.3459 | 0.0267
GEN-2018-131 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3747 | 23.3923 | 0.0176
GEN-2018-131 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7724 | 26.7962 | 0.0238
GEN-2018-131 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2492 | 10.2507 | 0.0015
GEN-2018-131 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7493 | 9.7523 | 0.003
GEN-2018-131 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3886 | 9.391 | 0.0024
GEN-2018-131 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.2043 | 15.2117 | 0.0074
GEN-2018-131 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.9039 | 17.914 | 0.0101
GEN-2018-131 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7719 | 17.7822 | 0.0103
GEN-2018-131 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0623 | 26.0848 | 0.0225
GEN-2018-131 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2952 | 15.3025 | 0.0073
GEN-2018-131 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1194 | 10.1232 | 0.0038
GEN-2018-131 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7279 | 5.7285 | 0.0006
GEN-2018-131 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1426 | 15.1523 | 0.0097
GEN-2018-131 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6252 | 16.6355 | 0.0103
GEN-2018-131 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1157 | 15.1206 | 0.0049
GEN-2018-131 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3405 | 16.3503 | 0.0098
GEN-2018-131 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3198 | 9.3222 | 0.0024
GEN-2018-131 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6461 | 7.6819 | 0.0358
GEN-2018-131 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0803 | 4.0864 | 0.0061
GEN-2018-131 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6139 | 4.6175 | 0.0036
GEN-2018-131 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2704 | 6.278 | 0.0076
GEN-2018-131 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8842 | 3.8859 | 0.0017
GEN-2018-131 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.3908 | 5.3961 | 0.0053
GEN-2018-131 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.9122 | 3.9138 | 0.0016
GEN-2018-131 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.3617 | 5.377 | 0.0153
GEN-2018-131 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5428 | 7.585 | 0.0422
GEN-2018-131 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6963 | 10.7573 | 0.061
GEN-2018-131 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1799 | 23.2427 | 0.0628
GEN-2018-131 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.0245 | 12.0588 | 0.0343
GEN-2018-131 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.9346 | 4.9456 | 0.011
GEN-2018-131 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.5701 | 4.5758 | 0.0057
GEN-2018-131 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2875 | 6.2976 | 0.0101
GEN-2018-131 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7156 | 5.7183 | 0.0027
GEN-2018-131 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9405 | 3.9412 | 0.0007
GEN-2018-131 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4489 | 5.4532 | 0.0043
GEN-2018-131 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6754 | 3.6766 | 0.0012
GEN-2018-131 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.6105 | 13.9921 | 0.3816
GEN-2018-131 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5682 | 10.6728 | 0.1046
GEN-2018-131 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.9458 | 19.1226 | 0.1768
GEN-2018-131 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4703 | 6.4838 | 0.0135
GEN-2018-131 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 10.3141 | 10.3901 | 0.076
GEN-2018-131 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.1659 | 6.1819 | 0.016
GEN-2018-131 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.7979 | 13.8937 | 0.0958
GEN-2018-131 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9735 | 13.0531 | 0.0796
GEN-2018-131 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.0321 | 11.1173 | 0.0852
GEN-2018-131 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3866 | 11.4228 | 0.0362
GEN-2018-131 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3673 | 5.3763 | 0.009
GEN-2018-131 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3184 | 7.3394 | 0.021
GEN-2018-131 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3288 | 9.3312 | 0.0024
GEN-2018-131 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3275 | 9.3417 | 0.0142
GEN-2018-131 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2937 | 11.305 | 0.0113
GEN-2018-131 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1647 | 8.1683 | 0.0036
GEN-2018-131 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7262 | 7.7315 | 0.0053
GEN-2018-131 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7189 | 4.7201 | 0.0012
GEN-2018-131 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.6866 | 5.6973 | 0.0107
GEN-2018-131 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9835 | 7.2114 | 0.2279
GEN-2018-131 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5347 | 14.7231 | 0.1884
GEN-2018-131 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3527 | 5.3677 | 0.015
GEN-2018-131 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3466 | 8.3667 | 0.0201
GEN-2018-131 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.455 | 7.4695 | 0.0145
GEN-2018-131 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.6818 | 11.9443 | 0.2625
GEN-2018-131 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.4541 | 9.6194 | 0.1653
GEN-2018-131 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.0923 | 9.2394 | 0.1471
GEN-2018-131 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7935 | 13.9613 | 0.1678
GEN-2018-131 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.4191 | 11.6699 | 0.2508
GEN-2018-131 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6902 | 29.6958 | 0.0056
GEN-2018-131 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3684 | 22.3752 | 0.0068
GEN-2018-131 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7456 | 28.7531 | 0.0075
GEN-2018-131 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.1221 | 25.1272 | 0.0051
GEN-2018-131 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2577 | 32.2643 | 0.0066
GEN-2018-131 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6119 | 17.6285 | 0.0166
GEN-2018-131 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9312 | 8.9373 | 0.0061
GEN-2018-131 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9804 | 21.0028 | 0.0224
GEN-2018-131 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 16.0048 | 16.022 | 0.0172
GEN-2018-131 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9804 | 21.0028 | 0.0224
GEN-2018-131 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.8147 | 15.8313 | 0.0166
GEN-2018-131 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5375 | 7.5391 | 0.0016
GEN-2018-131 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.6229 | 8.7586 | 0.1357
GEN-2018-131 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7598 | 8.7619 | 0.0021
GEN-2018-131 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7598 | 8.7619 | 0.0021
GEN-2018-131 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.0618 | 9.5193 | 0.4575
GEN-2018-131 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.4054 | 21.4116 | 0.0062
GEN-2018-131 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.3919 | 16.3979 | 0.006
GEN-2018-131 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3499 | 16.3559 | 0.006
GEN-2018-131 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2993 | 8.6551 | 0.3558
GEN-2018-131 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.8359 | 7.0661 | 0.2302
GEN-2018-131 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2723 | 2.2769 | 0.0046
GEN-2018-131 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.0618 | 9.5193 | 0.4575
GEN-2018-131 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.0716 | 9.5291 | 0.4575
GEN-2018-131 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5647 | 8.9723 | 0.4076
GEN-2018-131 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.7785 | 11.9753 | 0.1968
GEN-2018-131 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.8152 | 12.0133 | 0.1981
GEN-2018-132 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9095 | 14.918 | 0.0085
GEN-2018-132 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8769 | 13.8838 | 0.0069
GEN-2018-132 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7375 | 15.7464 | 0.0089
GEN-2018-132 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5878 | 15.5901 | 0.0023
GEN-2018-132 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1843 | 28.2447 | 0.0604
GEN-2018-132 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3192 | 28.3438 | 0.0246
GEN-2018-132 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3747 | 23.3908 | 0.0161
GEN-2018-132 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7724 | 26.7942 | 0.0218
GEN-2018-132 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2492 | 10.2506 | 0.0014
GEN-2018-132 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7493 | 9.7521 | 0.0028
GEN-2018-132 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3886 | 9.3908 | 0.0022
GEN-2018-132 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.2043 | 15.2111 | 0.0068
GEN-2018-132 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.9039 | 17.9132 | 0.0093
GEN-2018-132 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7719 | 17.7813 | 0.0094
GEN-2018-132 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0623 | 26.083 | 0.0207
GEN-2018-132 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2952 | 15.3019 | 0.0067
GEN-2018-132 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1194 | 10.1229 | 0.0035
GEN-2018-132 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7279 | 5.7284 | 0.0005
GEN-2018-132 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1426 | 15.1515 | 0.0089
GEN-2018-132 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6252 | 16.6346 | 0.0094
GEN-2018-132 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1157 | 15.1202 | 0.0045
GEN-2018-132 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3405 | 16.3495 | 0.009
GEN-2018-132 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3198 | 9.322 | 0.0022
GEN-2018-132 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6461 | 7.679 | 0.0329
GEN-2018-132 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0803 | 4.0859 | 0.0056
GEN-2018-132 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6139 | 4.6172 | 0.0033
GEN-2018-132 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2704 | 6.2774 | 0.007
GEN-2018-132 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8842 | 3.8858 | 0.0016
GEN-2018-132 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.3908 | 5.3957 | 0.0049
GEN-2018-132 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.9122 | 3.9137 | 0.0015
GEN-2018-132 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.3617 | 5.3758 | 0.0141
GEN-2018-132 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5428 | 7.5815 | 0.0387
GEN-2018-132 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6963 | 10.7523 | 0.056
GEN-2018-132 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1799 | 23.2375 | 0.0576
GEN-2018-132 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.0245 | 12.056 | 0.0315
GEN-2018-132 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.9346 | 4.9447 | 0.0101
GEN-2018-132 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.5701 | 4.5753 | 0.0052
GEN-2018-132 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2875 | 6.2968 | 0.0093
GEN-2018-132 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7156 | 5.718 | 0.0024
GEN-2018-132 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9405 | 3.9412 | 0.0007
GEN-2018-132 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4489 | 5.4529 | 0.004
GEN-2018-132 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6754 | 3.6765 | 0.0011
GEN-2018-132 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.6105 | 13.96 | 0.3495
GEN-2018-132 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5682 | 10.6641 | 0.0959
GEN-2018-132 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.9458 | 19.1079 | 0.1621
GEN-2018-132 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4703 | 6.4827 | 0.0124
GEN-2018-132 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 10.3141 | 10.3838 | 0.0697
GEN-2018-132 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 6.1659 | 6.1806 | 0.0147
GEN-2018-132 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.7979 | 13.8858 | 0.0879
GEN-2018-132 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9735 | 13.0465 | 0.073
GEN-2018-132 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.0321 | 11.1103 | 0.0782
GEN-2018-132 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3866 | 11.4198 | 0.0332
GEN-2018-132 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3673 | 5.3756 | 0.0083
GEN-2018-132 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3184 | 7.3377 | 0.0193
GEN-2018-132 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3288 | 9.3311 | 0.0023
GEN-2018-132 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3275 | 9.3405 | 0.013
GEN-2018-132 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2937 | 11.3041 | 0.0104
GEN-2018-132 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1647 | 8.168 | 0.0033
GEN-2018-132 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7262 | 7.7311 | 0.0049
GEN-2018-132 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7189 | 4.72 | 0.0011
GEN-2018-132 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.6866 | 5.6964 | 0.0098
GEN-2018-132 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9835 | 7.1922 | 0.2087
GEN-2018-132 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5347 | 14.7074 | 0.1727
GEN-2018-132 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3527 | 5.3665 | 0.0138
GEN-2018-132 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3466 | 8.3651 | 0.0185
GEN-2018-132 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.455 | 7.4683 | 0.0133
GEN-2018-132 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.6818 | 11.9224 | 0.2406
GEN-2018-132 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.4542 | 9.6057 | 0.1515
GEN-2018-132 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.0923 | 9.2272 | 0.1349
GEN-2018-132 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7935 | 13.9473 | 0.1538
GEN-2018-132 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.4191 | 11.649 | 0.2299
GEN-2018-132 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6902 | 29.6954 | 0.0052
GEN-2018-132 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3684 | 22.3747 | 0.0063
GEN-2018-132 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7456 | 28.7525 | 0.0069
GEN-2018-132 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.1221 | 25.1268 | 0.0047
GEN-2018-132 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2577 | 32.2638 | 0.0061
GEN-2018-132 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6119 | 17.6271 | 0.0152
GEN-2018-132 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9312 | 8.9369 | 0.0057
GEN-2018-132 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9804 | 21.001 | 0.0206
GEN-2018-132 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 16.0048 | 16.0206 | 0.0158
GEN-2018-132 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9804 | 21.001 | 0.0206
GEN-2018-132 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.8147 | 15.83 | 0.0153
GEN-2018-132 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5375 | 7.539 | 0.0015
GEN-2018-132 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.6229 | 8.7474 | 0.1245
GEN-2018-132 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7598 | 8.7617 | 0.0019
GEN-2018-132 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7598 | 8.7617 | 0.0019
GEN-2018-132 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.0618 | 9.4801 | 0.4183
GEN-2018-132 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.4054 | 21.4111 | 0.0057
GEN-2018-132 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.3919 | 16.3974 | 0.0055
GEN-2018-132 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3499 | 16.3554 | 0.0055
GEN-2018-132 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2993 | 8.6248 | 0.3255
GEN-2018-132 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.8359 | 7.0467 | 0.2108
GEN-2018-132 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2723 | 2.2765 | 0.0042
GEN-2018-132 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.0618 | 9.4801 | 0.4183
GEN-2018-132 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.0717 | 9.49 | 0.4183
GEN-2018-132 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5647 | 8.9842 | 0.4195
GEN-2018-132 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.7785 | 11.959 | 0.1805
GEN-2018-132 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.8152 | 11.9969 | 0.1817
GEN-2019-009 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.6233 | 12.627 | 0.0037
GEN-2019-009 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.6872 | 16.6889 | 0.0017
GEN-2019-009 | 02 NEBRASKA | 532913 | KELLY 5 | 161 | 6.4905 | 6.5127 | 0.0222
GEN-2019-009 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.0188 | 18.0208 | 0.002
GEN-2019-009 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 19.8595 | 19.8656 | 0.0061
GEN-2019-009 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.1148 | 20.1173 | 0.0025
GEN-2019-009 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.4451 | 18.4492 | 0.0041
GEN-2019-009 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 9.3529 | 9.3538 | 0.0009
GEN-2019-009 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 7.1884 | 7.1889 | 0.0005
GEN-2019-009 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 9.3031 | 9.3041 | 0.001
GEN-2019-009 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.908 | 5.9084 | 0.0004
GEN-2019-009 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.1563 | 43.174 | 0.0177
GEN-2019-009 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.1362 | 19.1395 | 0.0033
GEN-2019-009 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.1813 | 39.1958 | 0.0145
GEN-2019-009 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.3372 | 17.3566 | 0.0194
GEN-2019-009 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.5447 | 16.5615 | 0.0168
GEN-2019-009 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.4619 | 16.4786 | 0.0167
GEN-2019-009 | 02 NEBRASKA | 640062 | AUBURN 8 | 69 | 4.162 | 4.1884 | 0.0264
GEN-2019-009 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.3757 | 5.3766 | 0.0009
GEN-2019-009 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.1393 | 13.1448 | 0.0055
GEN-2019-009 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.775 | 26.8363 | 0.0613
GEN-2019-009 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 17.9623 | 18.1034 | 0.1411
GEN-2019-009 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6775 | 4.6816 | 0.0041
GEN-2019-009 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 2.0071 | 2.0143 | 0.0072
GEN-2019-009 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.7132 | 7.8286 | 0.1154
GEN-2019-009 | 02 NEBRASKA | 640235 | HUMBOLT7 | 115 | 6.6509 | 6.6997 | 0.0488
GEN-2019-009 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.5059 | 23.518 | 0.0121
GEN-2019-009 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.5643 | 4.5754 | 0.0111
GEN-2019-009 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7749 | 4.7792 | 0.0043
GEN-2019-009 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 22.9991 | 23.011 | 0.0119
GEN-2019-009 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.1563 | 43.174 | 0.0177
GEN-2019-009 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.0805 | 34.1042 | 0.0237
GEN-2019-009 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.5627 | 29.585 | 0.0223
GEN-2019-009 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8547 | 22.8645 | 0.0098
GEN-2019-009 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.3985 | 31.4133 | 0.0148
GEN-2019-009 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 43.5879 | 43.6362 | 0.0483
GEN-2019-009 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.2287 | 30.2459 | 0.0172
GEN-2019-009 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.3632 | 26.3773 | 0.0141
GEN-2019-009 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 21.9369 | 21.9731 | 0.0362
GEN-2019-009 | 02 NEBRASKA | 646258 | S1258 5 | 161 | 5.8943 | 6.0275 | 0.1332
GEN-2019-009 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.0022 | 8.4507 | 0.4485
GEN-2019-009 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.1111 | 10.4355 | 0.3244
GEN-2019-009 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.23 | 16.268 | 0.038
GEN-2019-009 | 02 NEBRASKA | 646398 | S1398 5 | 161 | 6.6869 | 6.7514 | 0.0645
GEN-2019-009 | 02 NEBRASKA | 646399 | S1399 5 | 161 | 6.4495 | 6.5001 | 0.0506
GEN-2019-009 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.005 | 32.0168 | 0.0118
GEN-2019-009 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.4671 | 17.4759 | 0.0088
GEN-2019-009 | 02 NEBRASKA | 647101 | AUBRNT 8 | 69 | 5.8142 | 5.8657 | 0.0515
GEN-2019-009 | 02 NEBRASKA | 647107 | SAC623 8 | 69 | 18.1693 | 18.1807 | 0.0114
GEN-2019-009 | 02 NEBRASKA | 647108 | SAC629 8 | 69 | 11.9122 | 11.9154 | 0.0032
GEN-2019-009 | 02 NEBRASKA | 647109 | SAC SO 8 | 69 | 9.7661 | 9.7694 | 0.0033
GEN-2019-009 | 02 NEBRASKA | 647110 | SAC NO 8 | 69 | 10.0318 | 10.0341 | 0.0023
GEN-2019-009 | 02 NEBRASKA | 647111 | W BROCK8 | 69 | 10.2139 | 10.4116 | 0.1977
GEN-2019-009 | 02 NEBRASKA | 647112 | MGLN TP8 | 69 | 1.9748 | 1.9789 | 0.0041
GEN-2019-009 | 02 NEBRASKA | 647113 | MAGELLN8 | 69 | 1.7517 | 1.755 | 0.0033
GEN-2019-009 | 02 NEBRASKA | 647400 | TECUMSH8 | 69 | 2.9271 | 2.9344 | 0.0073
GEN-2019-009 | 02 NEBRASKA | 647401 | NCU903 8 | 69 | 4.7623 | 4.7816 | 0.0193
GEN-2019-009 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.401 | 11.4048 | 0.0038
GEN-2019-009 | 02 NEBRASKA | 647866 | S6866 8 | 69 | 20.5314 | 20.5478 | 0.0164
GEN-2019-009 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.5966 | 8.5976 | 0.001
GEN-2019-009 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.4376 | 32.4556 | 0.018
GEN-2019-009 | 02 NEBRASKA | 647962 | S962 8 | 69 | 5.0124 | 5.0248 | 0.0124
GEN-2019-009 | 02 NEBRASKA | 647963 | S963 8 | 69 | 9.397 | 9.554 | 0.157
GEN-2019-009 | 02 NEBRASKA | 647964 | S964 8 | 69 | 2.3742 | 2.3802 | 0.006
GEN-2019-009 | 02 NEBRASKA | 647965 | S965 8 | 69 | 4.9478 | 4.9738 | 0.026
GEN-2019-009 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4924 | 0.4925 | 0.0001
GEN-2019-009 | 02 NEBRASKA | 647967 | S967 8 | 69 | 4.8589 | 4.8875 | 0.0286
GEN-2019-009 | 02 NEBRASKA | 647968 | S968 8 | 69 | 4.3072 | 4.3235 | 0.0163
GEN-2019-009 | 02 NEBRASKA | 647969 | S969 8 | 69 | 4.3557 | 4.3652 | 0.0095
GEN-2019-009 | 02 NEBRASKA | 647973 | S973 8 | 69 | 3.635 | 3.6585 | 0.0235
GEN-2019-009 | 02 NEBRASKA | 647974 | S974 8 | 69 | 5.7779 | 5.7863 | 0.0084
GEN-2019-009 | 02 NEBRASKA | 647975 | S975 8 | 69 | 6.2632 | 6.3049 | 0.0417
GEN-2019-009 | 02 NEBRASKA | 647977 | S977 8 | 69 | 5.403 | 5.4382 | 0.0352
GEN-2019-009 | 02 NEBRASKA | 647993 | S993 8 | 69 | 1.6001 | 1.6028 | 0.0027
GEN-2019-009 | 02 NEBRASKA | 647994 | S994 8 | 69 | 12.4911 | 12.4957 | 0.0046
GEN-2019-009 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.4697 | 9.4709 | 0.0012
GEN-2019-009 | 02 NEBRASKA | 648600 | NC1HS 5 | 161 | 5.7745 | 5.9023 | 0.1278
GEN-2019-009 | 02 NEBRASKA | 648610 | NC2HS 5 | 161 | 5.7835 | 5.9117 | 0.1282
GEN-2019-009 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9229 | 20.9321 | 0.0092
GEN-2019-009 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.4774 | 8.4781 | 0.0007
GEN-2019-009 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 7.5965 | 7.5969 | 0.0004
GEN-2019-009 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 16.5677 | 16.5698 | 0.0021
GEN-2019-009 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 21.884 | 21.893 | 0.009
GEN-2019-009 | 02 NEBRASKA | 763505 | GEN-2019-009 | 161 | 7.6967 | 8.145 | 0.4483
GEN-2019-009 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 43.0504 | 43.0681 | 0.0177
GEN-2019-039 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.4266 | 5.4336 | 0.007
GEN-2019-039 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.258 | 7.2629 | 0.0049
GEN-2019-039 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2865 | 5.2927 | 0.0062
GEN-2019-039 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.462 | 21.0918 | 0.6298
GEN-2019-039 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.2845 | 17.732 | 0.4475
GEN-2019-039 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.4267 | 18.2174 | 0.7907
GEN-2019-039 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6963 | 10.7898 | 0.0935
GEN-2019-039 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.5434 | 10.6743 | 0.1309
GEN-2019-039 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1798 | 23.8038 | 0.624
GEN-2019-039 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.2965 | 10.3908 | 0.0943
GEN-2019-039 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.0245 | 12.166 | 0.1415
GEN-2019-039 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.5516 | 18.9754 | 0.4238
GEN-2019-039 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.0617 | 20.5749 | 0.5132
GEN-2019-039 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2875 | 6.3095 | 0.022
GEN-2019-039 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9354 | 5.9583 | 0.0229
GEN-2019-039 | 02 NEBRASKA | 640173 | FREMONT7 | 115 | 6.2792 | 6.2844 | 0.0052
GEN-2019-039 | 02 NEBRASKA | 640176 | FULERTN7 | 115 | 2.6685 | 2.6702 | 0.0017
GEN-2019-039 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.1094 | 5.1251 | 0.0157
GEN-2019-039 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.5409 | 23.5694 | 0.0285
GEN-2019-039 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4703 | 6.486 | 0.0157
GEN-2019-039 | 02 NEBRASKA | 640281 | N.BEND 7 | 115 | 4.9515 | 4.9608 | 0.0093
GEN-2019-039 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9735 | 12.9941 | 0.0206
GEN-2019-039 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7308 | 11.7707 | 0.0399
GEN-2019-039 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.6816 | 5.6862 | 0.0046
GEN-2019-039 | 02 NEBRASKA | 640328 | RISNGCY7 | 115 | 6.2681 | 6.6803 | 0.4122
GEN-2019-039 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.0876 | 6.1155 | 0.0279
GEN-2019-039 | 02 NEBRASKA | 640340 | SEWARD 7 | 115 | 7.7061 | 7.7709 | 0.0648
GEN-2019-039 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.0321 | 11.1206 | 0.0885
GEN-2019-039 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3866 | 11.4978 | 0.1112
GEN-2019-039 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7822 | 4.797 | 0.0148
GEN-2019-039 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2507 | 4.2578 | 0.0071
GEN-2019-039 | 02 NEBRASKA | 640347 | SPALDNG7 | 115 | 3.9345 | 3.9365 | 0.002
GEN-2019-039 | 02 NEBRASKA | 640375 | TAMORA 7 | 115 | 6.1294 | 6.1578 | 0.0284
GEN-2019-039 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.9949 | 5.0009 | 0.006
GEN-2019-039 | 02 NEBRASKA | 640411 | YORK 7 | 115 | 7.8529 | 7.8653 | 0.0124
GEN-2019-039 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.3893 | 8.3987 | 0.0094
GEN-2019-039 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0822 | 4.0832 | 0.001
GEN-2019-039 | 02 NEBRASKA | 640417 | RISNGCY8 | 69 | 3.8766 | 3.9652 | 0.0886
GEN-2019-039 | 02 NEBRASKA | 640443 | YORK 8 | 69 | 2.6703 | 2.6712 | 0.0009
GEN-2019-039 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5278 | 2.5283 | 0.0005
GEN-2019-039 | 02 NEBRASKA | 640468 | TAMORA 8 | 69 | 4.1309 | 4.1385 | 0.0076
GEN-2019-039 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.3006 | 5.3114 | 0.0108
GEN-2019-039 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.6665 | 3.6706 | 0.0041
GEN-2019-039 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6119 | 17.6555 | 0.0436
GEN-2019-039 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3861 | 21.4238 | 0.0377
GEN-2019-039 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5957 | 25.6527 | 0.057
GEN-2019-039 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1094 | 22.1404 | 0.031
GEN-2019-039 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.6258 | 25.6555 | 0.0297
GEN-2019-039 | 02 NEBRASKA | 763714 | GEN-2019-039 | 115 | 8.5187 | 9.5701 | 1.0514
GEN-2019-039 | 02 NEBRASKA | 763718 | G19-039-TAP | 115 | 8.5466 | 9.5976 | 1.051
GEN-2019-041 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.6264 | 12.627 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 300076 | 5FAIRPTB2 | 161 | 16.6706 | 16.6709 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 301347 | 5WINSLOW | 161 | 8.8828 | 8.8829 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.6886 | 16.6889 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.0205 | 18.0208 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 8.0594 | 8.0597 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 19.8647 | 19.8656 | 0.0009
GEN-2019-041 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.1169 | 20.1173 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 541257 | COOK 5 | 161 | 14.2577 | 14.2579 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541258 | WOODBIN5 | 161 | 17.076 | 17.0763 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541394 | AVENUECTY 5 | 161 | 8.809 | 8.809 | 0
GEN-2019-041 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.4486 | 18.4492 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 541401 | EASTOWN5 | 161 | 17.5976 | 17.5978 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 7.7066 | 7.7068 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 7.7066 | 7.7068 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 7.7066 | 7.7068 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 9.3534 | 9.3538 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 7.1887 | 7.1889 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 9.3036 | 9.3041 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.9082 | 5.9084 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 542980 | NASHUA 7 | 345 | 23.1453 | 23.1456 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 542982 | IATAN 7 | 345 | 29.8836 | 29.884 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 42.7478 | 43.174 | 0.4262
GEN-2019-041 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.0587 | 19.1395 | 0.0808
GEN-2019-041 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2204 | 12.2349 | 0.0145
GEN-2019-041 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.1766 | 6.177 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.4348 | 31.4394 | 0.0046
GEN-2019-041 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.3534 | 17.3566 | 0.0032
GEN-2019-041 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.5588 | 16.5615 | 0.0027
GEN-2019-041 | 02 NEBRASKA | 635570 | ORIENT 3 | 345 | 17.3634 | 17.3641 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.4758 | 16.4786 | 0.0028
GEN-2019-041 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.5848 | 9.5864 | 0.0016
GEN-2019-041 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.3751 | 5.3766 | 0.0015
GEN-2019-041 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.1362 | 13.1448 | 0.0086
GEN-2019-041 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 15.9005 | 15.9146 | 0.0141
GEN-2019-041 | 02 NEBRASKA | 640105 | CARLJCT7 | 115 | 5.6346 | 5.6353 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 10.8847 | 10.8969 | 0.0122
GEN-2019-041 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.693 | 10.6963 | 0.0033
GEN-2019-041 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1761 | 23.1799 | 0.0038
GEN-2019-041 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.8263 | 26.8363 | 0.01
GEN-2019-041 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1011 | 18.1034 | 0.0023
GEN-2019-041 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6815 | 4.6816 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 2.0143 | 2.0143 | 0
GEN-2019-041 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4141 | 8.424 | 0.0099
GEN-2019-041 | 02 NEBRASKA | 640169 | FAIRBRY7 | 115 | 5.1199 | 5.1205 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7 | 7.0088 | 0.0088
GEN-2019-041 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.7017 | 5.7041 | 0.0024
GEN-2019-041 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9054 | 9.9083 | 0.0029
GEN-2019-041 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.308 | 4.3083 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1493 | 17.1539 | 0.0046
GEN-2019-041 | 02 NEBRASKA | 640208 | HARBINE7 | 115 | 6.8848 | 6.8861 | 0.0013
GEN-2019-041 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.8281 | 7.8286 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 640235 | HUMBOLT7 | 115 | 6.6993 | 6.6997 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3785 | 11.387 | 0.0085
GEN-2019-041 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.6801 | 14.6852 | 0.0051
GEN-2019-041 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7271 | 5.7276 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.435 | 23.518 | 0.083
GEN-2019-041 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 43.859 | 44.2293 | 0.3703
GEN-2019-041 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.2451 | 8.2477 | 0.0026
GEN-2019-041 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.6997 | 16.7023 | 0.0026
GEN-2019-041 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9307 | 4.9308 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7252 | 11.7308 | 0.0056
GEN-2019-041 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.0294 | 11.0321 | 0.0027
GEN-2019-041 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.575 | 4.5754 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640362 | STERLNG7 | 115 | 4.7129 | 4.7161 | 0.0032
GEN-2019-041 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.509 | 6.5097 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 640373 | SUTTON 8 | 69 | 3.9222 | 3.9224 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.5815 | 10.5829 | 0.0014
GEN-2019-041 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.3878 | 8.3893 | 0.0015
GEN-2019-041 | 02 NEBRASKA | 640415 | CARLJCT8 | 69 | 3.7202 | 3.7204 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 640426 | STEELEC7 | 115 | 5.1056 | 5.1061 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7791 | 4.7792 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5277 | 2.5278 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2204 | 12.2349 | 0.0145
GEN-2019-041 | 02 NEBRASKA | 640558 | S.FLATS.PLT7 | 115 | 4.5098 | 4.5102 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 22.9285 | 23.011 | 0.0825
GEN-2019-041 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 42.7478 | 43.174 | 0.4262
GEN-2019-041 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7338 | 28.7456 | 0.0118
GEN-2019-041 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 31.6732 | 31.6838 | 0.0106
GEN-2019-041 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 34.095 | 34.1042 | 0.0092
GEN-2019-041 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.5729 | 29.585 | 0.0121
GEN-2019-041 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.1174 | 25.1221 | 0.0047
GEN-2019-041 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 22.8586 | 22.8645 | 0.0059
GEN-2019-041 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 43.6305 | 43.6362 | 0.0057
GEN-2019-041 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.4501 | 8.4507 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.4346 | 10.4355 | 0.0009
GEN-2019-041 | 02 NEBRASKA | 647102 | HYDCAP 8 | 69 | 4.4755 | 4.4762 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 647103 | ENRON 8 | 69 | 4.3219 | 4.3226 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 647400 | TECUMSH8 | 69 | 2.9342 | 2.9344 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4925 | 0.4925 | 0
GEN-2019-041 | 02 NEBRASKA | 647968 | S968 8 | 69 | 4.3231 | 4.3235 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 647969 | S969 8 | 69 | 4.3645 | 4.3652 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 647970 | S970 8 | 69 | 4.2125 | 4.213 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 647974 | S974 8 | 69 | 5.7846 | 5.7863 | 0.0017
GEN-2019-041 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.58 | 17.6119 | 0.0319
GEN-2019-041 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.0154 | 21.0502 | 0.0348
GEN-2019-041 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.8938 | 20.9321 | 0.0383
GEN-2019-041 | 02 NEBRASKA | 650208 | W LINCOLN 7 | 115 | 22.3185 | 22.3428 | 0.0243
GEN-2019-041 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3647 | 21.3861 | 0.0214
GEN-2019-041 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5648 | 25.5957 | 0.0309
GEN-2019-041 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.0852 | 22.1094 | 0.0242
GEN-2019-041 | 02 NEBRASKA | 650217 | 8&N 7 | 115 | 24.1885 | 24.2179 | 0.0294
GEN-2019-041 | 02 NEBRASKA | 650218 | 3&VANDORN 7 | 115 | 21.8531 | 21.8792 | 0.0261
GEN-2019-041 | 02 NEBRASKA | 650229 | 27&PLR 7 | 115 | 20.6158 | 20.6461 | 0.0303
GEN-2019-041 | 02 NEBRASKA | 650230 | 2&N 7 | 115 | 25.8817 | 25.9158 | 0.0341
GEN-2019-041 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.2738 | 27.3176 | 0.0438
GEN-2019-041 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 27.6813 | 27.7384 | 0.0571
GEN-2019-041 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.3143 | 23.3645 | 0.0502
GEN-2019-041 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 21.4058 | 21.4412 | 0.0354
GEN-2019-041 | 02 NEBRASKA | 650250 | 40&ROKEBY 7 | 115 | 21.2424 | 21.2751 | 0.0327
GEN-2019-041 | 02 NEBRASKA | 650255 | 56&PLR 7 | 115 | 19.1972 | 19.2217 | 0.0245
GEN-2019-041 | 02 NEBRASKA | 650257 | 56&ELK TAP7 | 115 | 25.1478 | 25.1809 | 0.0331
GEN-2019-041 | 02 NEBRASKA | 650258 | 40&GERTIE 7 | 115 | 23.3216 | 23.3517 | 0.0301
GEN-2019-041 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.388 | 27.4269 | 0.0389
GEN-2019-041 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.0928 | 25.1269 | 0.0341
GEN-2019-041 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 21.8645 | 21.8872 | 0.0227
GEN-2019-041 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.6155 | 22.6388 | 0.0233
GEN-2019-041 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 21.7446 | 21.774 | 0.0294
GEN-2019-041 | 02 NEBRASKA | 650276 | 76&ROKEBY 7 | 115 | 17.8219 | 17.844 | 0.0221
GEN-2019-041 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.1084 | 32.1471 | 0.0387
GEN-2019-041 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.5797 | 25.6258 | 0.0461
GEN-2019-041 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.806 | 12.8103 | 0.0043
GEN-2019-041 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.6809 | 12.6851 | 0.0042
GEN-2019-041 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.4778 | 8.4781 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9735 | 9.9799 | 0.0064
GEN-2019-041 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9681 | 6.9723 | 0.0042
GEN-2019-041 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8235 | 5.8264 | 0.0029
GEN-2019-041 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 7.5969 | 7.5969 | 0
GEN-2019-041 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 16.5695 | 16.5698 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 21.8877 | 21.893 | 0.0053
GEN-2019-041 | 02 NEBRASKA | 763505 | GEN-2019-009 | 161 | 8.1445 | 8.145 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 42.6418 | 43.0681 | 0.4263
GEN-2019-069 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9057 | 14.9095 | 0.0038
GEN-2019-069 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8739 | 13.8769 | 0.003
GEN-2019-069 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7336 | 15.7375 | 0.0039
GEN-2019-069 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2328 | 12.2349 | 0.0021
GEN-2019-069 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5869 | 15.5878 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.158 | 28.1843 | 0.0263
GEN-2019-069 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3085 | 28.3192 | 0.0107
GEN-2019-069 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3676 | 23.3747 | 0.0071
GEN-2019-069 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7628 | 26.7724 | 0.0096
GEN-2019-069 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2486 | 10.2492 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7481 | 9.7493 | 0.0012
GEN-2019-069 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3876 | 9.3886 | 0.001
GEN-2019-069 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.2013 | 15.2043 | 0.003
GEN-2019-069 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8998 | 17.9039 | 0.0041
GEN-2019-069 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7678 | 17.7719 | 0.0041
GEN-2019-069 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0532 | 26.0623 | 0.0091
GEN-2019-069 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2922 | 15.2952 | 0.003
GEN-2019-069 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1179 | 10.1194 | 0.0015
GEN-2019-069 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7277 | 5.7279 | 0.0002
GEN-2019-069 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1388 | 15.1426 | 0.0038
GEN-2019-069 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6211 | 16.6252 | 0.0041
GEN-2019-069 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1137 | 15.1157 | 0.002
GEN-2019-069 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3365 | 16.3405 | 0.004
GEN-2019-069 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3189 | 9.3198 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6367 | 7.6461 | 0.0094
GEN-2019-069 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0787 | 4.0803 | 0.0016
GEN-2019-069 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6126 | 4.6139 | 0.0013
GEN-2019-069 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2678 | 6.2704 | 0.0026
GEN-2019-069 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8835 | 3.8842 | 0.0007
GEN-2019-069 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5344 | 7.5428 | 0.0084
GEN-2019-069 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.4227 | 20.4621 | 0.0394
GEN-2019-069 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.2564 | 17.2846 | 0.0282
GEN-2019-069 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.3995 | 17.4268 | 0.0273
GEN-2019-069 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6357 | 10.6963 | 0.0606
GEN-2019-069 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.5197 | 10.5434 | 0.0237
GEN-2019-069 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1261 | 23.1799 | 0.0538
GEN-2019-069 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.2757 | 10.2965 | 0.0208
GEN-2019-069 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.9933 | 12.0245 | 0.0312
GEN-2019-069 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.5204 | 18.5516 | 0.0312
GEN-2019-069 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.0256 | 20.0618 | 0.0362
GEN-2019-069 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2825 | 6.2875 | 0.005
GEN-2019-069 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9332 | 5.9354 | 0.0022
GEN-2019-069 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7146 | 5.7156 | 0.001
GEN-2019-069 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9402 | 3.9405 | 0.0003
GEN-2019-069 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.1075 | 5.1094 | 0.0019
GEN-2019-069 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1495 | 17.1539 | 0.0044
GEN-2019-069 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4475 | 5.4489 | 0.0014
GEN-2019-069 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6751 | 3.6754 | 0.0003
GEN-2019-069 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.4668 | 13.6105 | 0.1437
GEN-2019-069 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5286 | 10.5682 | 0.0396
GEN-2019-069 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.882 | 18.9459 | 0.0639
GEN-2019-069 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4644 | 6.4703 | 0.0059
GEN-2019-069 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3848 | 11.387 | 0.0022
GEN-2019-069 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.5069 | 23.518 | 0.0111
GEN-2019-069 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.22 | 44.2293 | 0.0093
GEN-2019-069 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.765 | 13.7979 | 0.0329
GEN-2019-069 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9448 | 12.9735 | 0.0287
GEN-2019-069 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7291 | 11.7308 | 0.0017
GEN-2019-069 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.0853 | 6.0876 | 0.0023
GEN-2019-069 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9461 | 11.0321 | 0.086
GEN-2019-069 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3526 | 11.3866 | 0.034
GEN-2019-069 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.781 | 4.7822 | 0.0012
GEN-2019-069 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2501 | 4.2507 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.364 | 5.3673 | 0.0033
GEN-2019-069 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3106 | 7.3184 | 0.0078
GEN-2019-069 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3277 | 9.3288 | 0.0011
GEN-2019-069 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3221 | 9.3275 | 0.0054
GEN-2019-069 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2894 | 11.2937 | 0.0043
GEN-2019-069 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1634 | 8.1647 | 0.0013
GEN-2019-069 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.9943 | 4.9949 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7242 | 7.7262 | 0.002
GEN-2019-069 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7185 | 4.7189 | 0.0004
GEN-2019-069 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9547 | 6.9835 | 0.0288
GEN-2019-069 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5064 | 14.5347 | 0.0283
GEN-2019-069 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3504 | 5.3527 | 0.0023
GEN-2019-069 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2328 | 12.2349 | 0.0021
GEN-2019-069 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.298 | 5.3006 | 0.0026
GEN-2019-069 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3389 | 8.3466 | 0.0077
GEN-2019-069 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4494 | 7.455 | 0.0056
GEN-2019-069 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.5822 | 11.6818 | 0.0996
GEN-2019-069 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.3911 | 9.4542 | 0.0631
GEN-2019-069 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.0006 | 23.011 | 0.0104
GEN-2019-069 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.036 | 9.0923 | 0.0563
GEN-2019-069 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7683 | 13.7935 | 0.0252
GEN-2019-069 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.3239 | 11.4191 | 0.0952
GEN-2019-069 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6871 | 29.6902 | 0.0031
GEN-2019-069 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3647 | 22.3684 | 0.0037
GEN-2019-069 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7404 | 28.7456 | 0.0052
GEN-2019-069 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.119 | 25.1221 | 0.0031
GEN-2019-069 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2541 | 32.2577 | 0.0036
GEN-2019-069 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.6655 | 3.6665 | 0.001
GEN-2019-069 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.5965 | 17.6119 | 0.0154
GEN-2019-069 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.0408 | 21.0502 | 0.0094
GEN-2019-069 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9242 | 20.9321 | 0.0079
GEN-2019-069 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3816 | 21.3861 | 0.0045
GEN-2019-069 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5891 | 25.5957 | 0.0066
GEN-2019-069 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1052 | 22.1094 | 0.0042
GEN-2019-069 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.14 | 32.1471 | 0.0071
GEN-2019-069 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.6212 | 25.6258 | 0.0046
GEN-2019-069 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 10.8661 | 10.8675 | 0.0014
GEN-2019-069 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9297 | 8.9312 | 0.0015
GEN-2019-069 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9716 | 20.9804 | 0.0088
GEN-2019-069 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.998 | 16.0048 | 0.0068
GEN-2019-069 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9716 | 20.9804 | 0.0088
GEN-2019-069 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.808 | 15.8147 | 0.0067
GEN-2019-069 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5369 | 7.5375 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.5709 | 8.6229 | 0.052
GEN-2019-069 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9783 | 9.9799 | 0.0016
GEN-2019-069 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9717 | 6.9723 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.826 | 5.8264 | 0.0004
GEN-2019-069 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7588 | 8.7598 | 0.001
GEN-2019-069 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7588 | 8.7598 | 0.001
GEN-2019-069 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.007 | 9.0618 | 0.0548
GEN-2019-069 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.402 | 21.4054 | 0.0034
GEN-2019-069 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.389 | 16.3919 | 0.0029
GEN-2019-069 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3471 | 16.3499 | 0.0028
GEN-2019-069 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2558 | 8.2993 | 0.0435
GEN-2019-069 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.8074 | 6.8359 | 0.0285
GEN-2019-069 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2673 | 2.2723 | 0.005
GEN-2019-069 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.007 | 9.0618 | 0.0548
GEN-2019-069 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.0168 | 9.0717 | 0.0549
GEN-2019-069 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5158 | 8.5648 | 0.049
GEN-2019-069 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.5726 | 11.7785 | 0.2059
GEN-2019-069 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.6094 | 11.8153 | 0.2059
GEN-2019-070 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9078 | 14.9095 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8756 | 13.8769 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7358 | 15.7375 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.234 | 12.2349 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5874 | 15.5878 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.1728 | 28.1843 | 0.0115
GEN-2019-070 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3145 | 28.3192 | 0.0047
GEN-2019-070 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3716 | 23.3747 | 0.0031
GEN-2019-070 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7682 | 26.7724 | 0.0042
GEN-2019-070 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.249 | 10.2492 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7488 | 9.7493 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3882 | 9.3886 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.203 | 15.2043 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.9021 | 17.9039 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7701 | 17.7719 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0583 | 26.0623 | 0.004
GEN-2019-070 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2939 | 15.2952 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1188 | 10.1194 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7279 | 5.7279 | 0
GEN-2019-070 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1409 | 15.1426 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6234 | 16.6252 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1148 | 15.1157 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3387 | 16.3405 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3194 | 9.3198 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.642 | 7.6461 | 0.0041
GEN-2019-070 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0796 | 4.0803 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6133 | 4.6139 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2693 | 6.2704 | 0.0011
GEN-2019-070 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8839 | 3.8842 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5391 | 7.5428 | 0.0037
GEN-2019-070 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.4448 | 20.4621 | 0.0173
GEN-2019-070 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.2722 | 17.2846 | 0.0124
GEN-2019-070 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.4148 | 17.4268 | 0.012
GEN-2019-070 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6697 | 10.6963 | 0.0266
GEN-2019-070 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.533 | 10.5434 | 0.0104
GEN-2019-070 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1563 | 23.1799 | 0.0236
GEN-2019-070 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.2874 | 10.2965 | 0.0091
GEN-2019-070 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.0109 | 12.0245 | 0.0136
GEN-2019-070 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.5379 | 18.5516 | 0.0137
GEN-2019-070 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.0459 | 20.0618 | 0.0159
GEN-2019-070 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2853 | 6.2875 | 0.0022
GEN-2019-070 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9344 | 5.9354 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7152 | 5.7156 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9404 | 3.9405 | 0.0001
GEN-2019-070 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.1086 | 5.1094 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.152 | 17.1539 | 0.0019
GEN-2019-070 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4483 | 5.4489 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6753 | 3.6754 | 0.0001
GEN-2019-070 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.5473 | 13.6105 | 0.0632
GEN-2019-070 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5509 | 10.5682 | 0.0173
GEN-2019-070 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.9178 | 18.9459 | 0.0281
GEN-2019-070 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4677 | 6.4703 | 0.0026
GEN-2019-070 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.386 | 11.387 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.5132 | 23.518 | 0.0048
GEN-2019-070 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.2252 | 44.2293 | 0.0041
GEN-2019-070 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.7835 | 13.7979 | 0.0144
GEN-2019-070 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.961 | 12.9735 | 0.0125
GEN-2019-070 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7301 | 11.7308 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.0866 | 6.0876 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9943 | 11.0321 | 0.0378
GEN-2019-070 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3717 | 11.3866 | 0.0149
GEN-2019-070 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.7817 | 4.7822 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2504 | 4.2507 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.3659 | 5.3673 | 0.0014
GEN-2019-070 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.315 | 7.3184 | 0.0034
GEN-2019-070 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3283 | 9.3288 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3251 | 9.3275 | 0.0024
GEN-2019-070 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2918 | 11.2937 | 0.0019
GEN-2019-070 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1641 | 8.1647 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.9947 | 4.9949 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7254 | 7.7262 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7187 | 4.7189 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9709 | 6.9835 | 0.0126
GEN-2019-070 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5223 | 14.5347 | 0.0124
GEN-2019-070 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3517 | 5.3527 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.234 | 12.2349 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.2995 | 5.3006 | 0.0011
GEN-2019-070 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3432 | 8.3466 | 0.0034
GEN-2019-070 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4525 | 7.455 | 0.0025
GEN-2019-070 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.638 | 11.6818 | 0.0438
GEN-2019-070 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.4264 | 9.4542 | 0.0278
GEN-2019-070 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.0065 | 23.011 | 0.0045
GEN-2019-070 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.0676 | 9.0923 | 0.0247
GEN-2019-070 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7825 | 13.7935 | 0.011
GEN-2019-070 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.3773 | 11.4191 | 0.0418
GEN-2019-070 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6889 | 29.6902 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3668 | 22.3684 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7433 | 28.7456 | 0.0023
GEN-2019-070 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.1207 | 25.1221 | 0.0014
GEN-2019-070 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2561 | 32.2577 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.6661 | 3.6665 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.6052 | 17.6119 | 0.0067
GEN-2019-070 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.0461 | 21.0502 | 0.0041
GEN-2019-070 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9287 | 20.9321 | 0.0034
GEN-2019-070 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3841 | 21.3861 | 0.002
GEN-2019-070 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5928 | 25.5957 | 0.0029
GEN-2019-070 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1076 | 22.1094 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.144 | 32.1471 | 0.0031
GEN-2019-070 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.6238 | 25.6258 | 0.002
GEN-2019-070 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 10.8669 | 10.8675 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9305 | 8.9312 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9766 | 20.9804 | 0.0038
GEN-2019-070 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 16.0018 | 16.0048 | 0.003
GEN-2019-070 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9766 | 20.9804 | 0.0038
GEN-2019-070 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.8118 | 15.8147 | 0.0029
GEN-2019-070 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5372 | 7.5375 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.6001 | 8.6229 | 0.0228
GEN-2019-070 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9792 | 9.9799 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9721 | 6.9723 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8263 | 5.8264 | 0.0001
GEN-2019-070 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7593 | 8.7598 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7593 | 8.7598 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.0378 | 9.0618 | 0.024
GEN-2019-070 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.4039 | 21.4054 | 0.0015
GEN-2019-070 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.3907 | 16.3919 | 0.0012
GEN-2019-070 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3487 | 16.3499 | 0.0012
GEN-2019-070 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2802 | 8.2993 | 0.0191
GEN-2019-070 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.8234 | 6.8359 | 0.0125
GEN-2019-070 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2701 | 2.2723 | 0.0022
GEN-2019-070 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.0378 | 9.0618 | 0.024
GEN-2019-070 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.0476 | 9.0717 | 0.0241
GEN-2019-070 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5433 | 8.5648 | 0.0215
GEN-2019-070 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.6875 | 11.7785 | 0.091
GEN-2019-070 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.7243 | 11.8153 | 0.091
GEN-2019-073 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.9057 | 14.9095 | 0.0038
GEN-2019-073 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.8739 | 13.8769 | 0.003
GEN-2019-073 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.7336 | 15.7375 | 0.0039
GEN-2019-073 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.2328 | 12.2349 | 0.0021
GEN-2019-073 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.5869 | 15.5878 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 28.158 | 28.1843 | 0.0263
GEN-2019-073 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.3085 | 28.3192 | 0.0107
GEN-2019-073 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.3676 | 23.3747 | 0.0071
GEN-2019-073 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.7628 | 26.7724 | 0.0096
GEN-2019-073 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2486 | 10.2492 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7481 | 9.7493 | 0.0012
GEN-2019-073 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3876 | 9.3886 | 0.001
GEN-2019-073 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.2013 | 15.2043 | 0.003
GEN-2019-073 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8998 | 17.9039 | 0.0041
GEN-2019-073 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.7678 | 17.7719 | 0.0041
GEN-2019-073 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 26.0532 | 26.0623 | 0.0091
GEN-2019-073 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2922 | 15.2952 | 0.003
GEN-2019-073 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.1179 | 10.1194 | 0.0015
GEN-2019-073 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7277 | 5.7279 | 0.0002
GEN-2019-073 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 15.1388 | 15.1426 | 0.0038
GEN-2019-073 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 16.6211 | 16.6252 | 0.0041
GEN-2019-073 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 15.1137 | 15.1157 | 0.002
GEN-2019-073 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 16.3365 | 16.3405 | 0.004
GEN-2019-073 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3189 | 9.3198 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.6367 | 7.6461 | 0.0094
GEN-2019-073 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.0787 | 4.0803 | 0.0016
GEN-2019-073 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.6126 | 4.6139 | 0.0013
GEN-2019-073 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.2678 | 6.2704 | 0.0026
GEN-2019-073 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8835 | 3.8842 | 0.0007
GEN-2019-073 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.5344 | 7.5428 | 0.0084
GEN-2019-073 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 20.4227 | 20.4621 | 0.0394
GEN-2019-073 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 17.2564 | 17.2846 | 0.0282
GEN-2019-073 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 17.3995 | 17.4268 | 0.0273
GEN-2019-073 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.6357 | 10.6963 | 0.0606
GEN-2019-073 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.5197 | 10.5434 | 0.0237
GEN-2019-073 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.1261 | 23.1799 | 0.0538
GEN-2019-073 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.2757 | 10.2965 | 0.0208
GEN-2019-073 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.9933 | 12.0245 | 0.0312
GEN-2019-073 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 18.5204 | 18.5516 | 0.0312
GEN-2019-073 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 20.0256 | 20.0618 | 0.0362
GEN-2019-073 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 6.2825 | 6.2875 | 0.005
GEN-2019-073 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.9332 | 5.9354 | 0.0022
GEN-2019-073 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.7146 | 5.7156 | 0.001
GEN-2019-073 | 02 NEBRASKA | 640164 | EMERSONG | 69 | 3.9402 | 3.9405 | 0.0003
GEN-2019-073 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 5.1075 | 5.1094 | 0.0019
GEN-2019-073 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.1495 | 17.1539 | 0.0044
GEN-2019-073 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4475 | 5.4489 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6751 | 3.6754 | 0.0003
GEN-2019-073 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.4668 | 13.6105 | 0.1437
GEN-2019-073 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.5286 | 10.5682 | 0.0396
GEN-2019-073 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.882 | 18.9459 | 0.0639
GEN-2019-073 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.4644 | 6.4703 | 0.0059
GEN-2019-073 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.3848 | 11.387 | 0.0022
GEN-2019-073 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.5069 | 23.518 | 0.0111
GEN-2019-073 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.22 | 44.2293 | 0.0093
GEN-2019-073 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.765 | 13.7979 | 0.0329
GEN-2019-073 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.9448 | 12.9735 | 0.0287
GEN-2019-073 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7291 | 11.7308 | 0.0017
GEN-2019-073 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 6.0853 | 6.0876 | 0.0023
GEN-2019-073 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.9461 | 11.0321 | 0.086
GEN-2019-073 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.3526 | 11.3866 | 0.034
GEN-2019-073 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.781 | 4.7822 | 0.0012
GEN-2019-073 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.2501 | 4.2507 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.364 | 5.3673 | 0.0033
GEN-2019-073 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.3106 | 7.3184 | 0.0078
GEN-2019-073 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3277 | 9.3288 | 0.0011
GEN-2019-073 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.3221 | 9.3275 | 0.0054
GEN-2019-073 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.2894 | 11.2937 | 0.0043
GEN-2019-073 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.1634 | 8.1647 | 0.0013
GEN-2019-073 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.9943 | 4.9949 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7242 | 7.7262 | 0.002
GEN-2019-073 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7185 | 4.7189 | 0.0004
GEN-2019-073 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9547 | 6.9835 | 0.0288
GEN-2019-073 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.5064 | 14.5347 | 0.0283
GEN-2019-073 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.3504 | 5.3527 | 0.0023
GEN-2019-073 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.2328 | 12.2349 | 0.0021
GEN-2019-073 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.298 | 5.3006 | 0.0026
GEN-2019-073 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.3389 | 8.3466 | 0.0077
GEN-2019-073 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.4494 | 7.455 | 0.0056
GEN-2019-073 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.5822 | 11.6818 | 0.0996
GEN-2019-073 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.3911 | 9.4542 | 0.0631
GEN-2019-073 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.0006 | 23.011 | 0.0104
GEN-2019-073 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 9.036 | 9.0923 | 0.0563
GEN-2019-073 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.7683 | 13.7935 | 0.0252
GEN-2019-073 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 11.3239 | 11.4191 | 0.0952
GEN-2019-073 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 29.6871 | 29.6902 | 0.0031
GEN-2019-073 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.3647 | 22.3684 | 0.0037
GEN-2019-073 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 28.7404 | 28.7456 | 0.0052
GEN-2019-073 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.119 | 25.1221 | 0.0031
GEN-2019-073 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.2541 | 32.2577 | 0.0036
GEN-2019-073 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.6655 | 3.6665 | 0.001
GEN-2019-073 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.5965 | 17.6119 | 0.0154
GEN-2019-073 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.0408 | 21.0502 | 0.0094
GEN-2019-073 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 20.9242 | 20.9321 | 0.0079
GEN-2019-073 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.3816 | 21.3861 | 0.0045
GEN-2019-073 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.5891 | 25.5957 | 0.0066
GEN-2019-073 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1052 | 22.1094 | 0.0042
GEN-2019-073 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.14 | 32.1471 | 0.0071
GEN-2019-073 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.6212 | 25.6258 | 0.0046
GEN-2019-073 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 10.8661 | 10.8675 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.9297 | 8.9312 | 0.0015
GEN-2019-073 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.9716 | 20.9804 | 0.0088
GEN-2019-073 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.998 | 16.0048 | 0.0068
GEN-2019-073 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.9716 | 20.9804 | 0.0088
GEN-2019-073 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.808 | 15.8147 | 0.0067
GEN-2019-073 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5369 | 7.5375 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.5709 | 8.6229 | 0.052
GEN-2019-073 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.9783 | 9.9799 | 0.0016
GEN-2019-073 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9717 | 6.9723 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.826 | 5.8264 | 0.0004
GEN-2019-073 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7588 | 8.7598 | 0.001
GEN-2019-073 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7588 | 8.7598 | 0.001
GEN-2019-073 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 9.007 | 9.0618 | 0.0548
GEN-2019-073 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.402 | 21.4054 | 0.0034
GEN-2019-073 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.389 | 16.3919 | 0.0029
GEN-2019-073 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.3471 | 16.3499 | 0.0028
GEN-2019-073 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 8.2558 | 8.2993 | 0.0435
GEN-2019-073 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 6.8074 | 6.8359 | 0.0285
GEN-2019-073 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.2673 | 2.2723 | 0.005
GEN-2019-073 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 9.007 | 9.0618 | 0.0548
GEN-2019-073 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 9.0168 | 9.0717 | 0.0549
GEN-2019-073 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 8.5158 | 8.5648 | 0.049
GEN-2019-073 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.5726 | 11.7785 | 0.2059
GEN-2019-073 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.6094 | 11.8153 | 0.2059
GEN-2018-063 | 03 CENTRAL | 99911 | GI91POI | 69 | 2.9476 | 2.9476 | 0
GEN-2018-063 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 13.773 | 13.7737 | 0.0007
GEN-2018-063 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.3575 | 8.3575 | 0
GEN-2018-063 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.7482 | 6.7482 | 0
GEN-2018-063 | 03 CENTRAL | 300117 | 5SEDALA | 161 | 9.0119 | 9.012 | 0.0001
GEN-2018-063 | 03 CENTRAL | 300528 | 2DRESDN | 69 | 5.9412 | 5.9412 | 0
GEN-2018-063 | 03 CENTRAL | 300529 | 2GEOGT1 | 69 | 7.4029 | 7.403 | 0.0001
GEN-2018-063 | 03 CENTRAL | 300530 | 2GEOGT2 | 69 | 7.9883 | 7.9883 | 0
GEN-2018-063 | 03 CENTRAL | 300531 | 2GEORGE | 69 | 8.0789 | 8.0789 | 0
GEN-2018-063 | 03 CENTRAL | 300534 | 2LINCLN | 69 | 4.9615 | 4.9615 | 0
GEN-2018-063 | 03 CENTRAL | 300541 | 2SEDALI | 69 | 10.3146 | 10.3146 | 0
GEN-2018-063 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.2588 | 6.2588 | 0
GEN-2018-063 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 10.9469 | 10.947 | 0.0001
GEN-2018-063 | 03 CENTRAL | 345071 | 5MCBAIN T | 161 | 15.0382 | 15.0383 | 0.0001
GEN-2018-063 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.501 | 22.5012 | 0.0002
GEN-2018-063 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 22.501 | 22.5012 | 0.0002
GEN-2018-063 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.701 | 3.701 | 0
GEN-2018-063 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 9.254 | 9.254 | 0
GEN-2018-063 | 03 CENTRAL | 541148 | WBURGE_CAP5 | 161 | 6.3658 | 6.3658 | 0
GEN-2018-063 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.7768 | 9.7768 | 0
GEN-2018-063 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.728 | 7.7281 | 0.0001
GEN-2018-063 | 03 CENTRAL | 541228 | WBURGE 5 | 161 | 6.609 | 6.6091 | 0.0001
GEN-2018-063 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.7392 | 7.7393 | 0.0001
GEN-2018-063 | 03 CENTRAL | 541269 | WBURGE 2 | 69 | 6.8579 | 6.8579 | 0
GEN-2018-063 | 03 CENTRAL | 541270 | KNOSTER2 | 69 | 4.897 | 4.897 | 0
GEN-2018-063 | 03 CENTRAL | 541271 | SEDN 2 | 69 | 7.4361 | 7.4361 | 0
GEN-2018-063 | 03 CENTRAL | 541272 | SEDS 2 | 69 | 6.6241 | 6.6242 | 0.0001
GEN-2018-063 | 03 CENTRAL | 541273 | KELHYS 2 | 69 | 7.0569 | 7.0569 | 0
GEN-2018-063 | 03 CENTRAL | 541274 | PITTCRN2 | 69 | 6.5659 | 6.5659 | 0
GEN-2018-063 | 03 CENTRAL | 541275 | SEDPLT 2 | 69 | 6.7408 | 6.7408 | 0
GEN-2018-063 | 03 CENTRAL | 541276 | COLECMP2 | 69 | 3.0969 | 3.0969 | 0
GEN-2018-063 | 03 CENTRAL | 541277 | WARSAW 2 | 69 | 3.4041 | 3.4041 | 0
GEN-2018-063 | 03 CENTRAL | 541281 | WARSAWTP | 69 | 3.1025 | 3.1025 | 0
GEN-2018-063 | 03 CENTRAL | 541335 | WAFBW_SW5 | 161 | 6.6928 | 6.6928 | 0
GEN-2018-063 | 03 CENTRAL | 541336 | WAFBW5 | 161 | 6.0897 | 6.0897 | 0
GEN-2018-063 | 03 CENTRAL | 541337 | WAFBE_SW5 | 161 | 6.7208 | 6.7208 | 0
GEN-2018-063 | 03 CENTRAL | 541338 | WAFBE5 | 161 | 6.1165 | 6.1165 | 0
GEN-2018-063 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.2575 | 7.2576 | 0.0001
GEN-2018-063 | 03 CENTRAL | 541524 | MONSERTP | 69 | 5.7919 | 5.7919 | 0
GEN-2018-063 | 03 CENTRAL | 541534 | KNOSTERTP | 69 | 4.9511 | 4.9511 | 0
GEN-2018-063 | 03 CENTRAL | 541535 | LAMONTETP | 69 | 5.0793 | 5.0793 | 0
GEN-2018-063 | 03 CENTRAL | 541536 | LAMONTE | 69 | 4.9249 | 4.9249 | 0
GEN-2018-063 | 03 CENTRAL | 762988 | GEN-2018-063 | 69 | 16.7328 | 17.3208 | 0.588
GEN-2018-063 | 03 CENTRAL | 762992 | G18-063-TAP | 69 | 17.2577 | 17.8448 | 0.5871
GEN-2018-108 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0358 | 16.0361 | 0.0003
GEN-2018-108 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.2738 | 10.2755 | 0.0017
GEN-2018-108 | 03 CENTRAL | 511557 | CHISHOLM6 | 230 | 11.3442 | 11.3451 | 0.0009
GEN-2018-108 | 03 CENTRAL | 514771 | TANGIER2 | 69 | 3.8409 | 3.841 | 0.0001
GEN-2018-108 | 03 CENTRAL | 514773 | NEWMAN 2 | 69 | 1.6206 | 1.6206 | 0
GEN-2018-108 | 03 CENTRAL | 514775 | TANGRTP2 | 69 | 4.9882 | 4.9884 | 0.0002
GEN-2018-108 | 03 CENTRAL | 514776 | NEWGRTP2 | 69 | 5.6913 | 5.6915 | 0.0002
GEN-2018-108 | 03 CENTRAL | 514778 | CLEOCOR4 | 138 | 5.7512 | 5.7514 | 0.0002
GEN-2018-108 | 03 CENTRAL | 514779 | WDNITRO2 | 69 | 4.9757 | 4.9758 | 0.0001
GEN-2018-108 | 03 CENTRAL | 514781 | CEDARAV2 | 69 | 5.9414 | 5.9416 | 0.0002
GEN-2018-108 | 03 CENTRAL | 514782 | WODWRD 2 | 69 | 11.3123 | 11.313 | 0.0007
GEN-2018-108 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.3418 | 13.3441 | 0.0023
GEN-2018-108 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1492 | 5.1493 | 0.0001
GEN-2018-108 | 03 CENTRAL | 514792 | ALVAOGE2 | 69 | 7.7184 | 7.7194 | 0.001
GEN-2018-108 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.0808 | 9.0823 | 0.0015
GEN-2018-108 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.0357 | 10.0409 | 0.0052
GEN-2018-108 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.5439 | 7.5447 | 0.0008
GEN-2018-108 | 03 CENTRAL | 514880 | NORTWST7 | 345 | 31.2896 | 31.2934 | 0.0038
GEN-2018-108 | 03 CENTRAL | 514901 | CIMARON7 | 345 | 32.1231 | 32.1275 | 0.0044
GEN-2018-108 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2241 | 3.2242 | 0.0001
GEN-2018-108 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 18.5114 | 18.5361 | 0.0247
GEN-2018-108 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 23.9995 | 24.0118 | 0.0123
GEN-2018-108 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.1319 | 9.1334 | 0.0015
GEN-2018-108 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.6986 | 9.7005 | 0.0019
GEN-2018-108 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 16.7031 | 16.7115 | 0.0084
GEN-2018-108 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.6938 | 17.6997 | 0.0059
GEN-2018-108 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 11.9181 | 11.9223 | 0.0042
GEN-2018-108 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.4731 | 7.4739 | 0.0008
GEN-2018-108 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 30.2867 | 30.2927 | 0.006
GEN-2018-108 | 03 CENTRAL | 515533 | REDCLFT4 | 138 | 6.8459 | 6.8465 | 0.0006
GEN-2018-108 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.2297 | 12.2333 | 0.0036
GEN-2018-108 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 10.9979 | 11.0013 | 0.0034
GEN-2018-108 | 03 CENTRAL | 515560 | CZYCRVT2 | 69 | 3.3784 | 3.3785 | 0.0001
GEN-2018-108 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.5022 | 8.5042 | 0.002
GEN-2018-108 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.197 | 13.2022 | 0.0052
GEN-2018-108 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 9.7616 | 9.7642 | 0.0026
GEN-2018-108 | 03 CENTRAL | 515600 | KNGFSHR7 | 345 | 11.3345 | 11.335 | 0.0005
GEN-2018-108 | 03 CENTRAL | 515605 | CANADN7 | 345 | 11.9729 | 11.9734 | 0.0005
GEN-2018-108 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 9.6177 | 9.6202 | 0.0025
GEN-2018-108 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 8.6902 | 8.6923 | 0.0021
GEN-2018-108 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.7747 | 10.7774 | 0.0027
GEN-2018-108 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 10.9472 | 10.9515 | 0.0043
GEN-2018-108 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 10.0304 | 10.034 | 0.0036
GEN-2018-108 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5721 | 19.5746 | 0.0025
GEN-2018-108 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 6.4051 | 6.4053 | 0.0002
GEN-2018-108 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.5753 | 8.5806 | 0.0053
GEN-2018-108 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.459 | 14.5121 | 0.0531
GEN-2018-108 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 15.5265 | 15.5414 | 0.0149
GEN-2018-108 | 03 CENTRAL | 515863 | REDCLF 4 | 138 | 6.8315 | 6.8321 | 0.0006
GEN-2018-108 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 16.1124 | 16.1144 | 0.002
GEN-2018-108 | 03 CENTRAL | 515877 | REDDIRT7 | 345 | 16.1086 | 16.1106 | 0.002
GEN-2018-108 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.361 | 10.3687 | 0.0077
GEN-2018-108 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.6894 | 11.6993 | 0.0099
GEN-2018-108 | 03 CENTRAL | 516025 | SUNDANC4 | 138 | 3.7708 | 3.7709 | 0.0001
GEN-2018-108 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.5315 | 9.5367 | 0.0052
GEN-2018-108 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.5209 | 9.5261 | 0.0052
GEN-2018-108 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.2005 | 8.2008 | 0.0003
GEN-2018-108 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.1025 | 10.1077 | 0.0052
GEN-2018-108 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.7335 | 11.7416 | 0.0081
GEN-2018-108 | 03 CENTRAL | 520437 | SALTPLN4 | 138 | 6.4234 | 6.425 | 0.0016
GEN-2018-108 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3423 | 19.3447 | 0.0024
GEN-2018-108 | 03 CENTRAL | 520480 | CURTIS 2 | 69 | 4.1023 | 4.1023 | 0
GEN-2018-108 | 03 CENTRAL | 520500 | BEARCAT4 | 138 | 14.4539 | 14.4552 | 0.0013
GEN-2018-108 | 03 CENTRAL | 520507 | CEDRDAL4 | 138 | 4.7452 | 4.7453 | 0.0001
GEN-2018-108 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.8534 | 6.8537 | 0.0003
GEN-2018-108 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.8039 | 6.8067 | 0.0028
GEN-2018-108 | 03 CENTRAL | 520848 | CDRDLTP4 | 138 | 5.8818 | 5.882 | 0.0002
GEN-2018-108 | 03 CENTRAL | 520920 | FTSUPLY4 | 138 | 5.5329 | 5.5331 | 0.0002
GEN-2018-108 | 03 CENTRAL | 520922 | SLEEPBR4 | 138 | 4.3851 | 4.3852 | 0.0001
GEN-2018-108 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.9803 | 7.9807 | 0.0004
GEN-2018-108 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.8699 | 8.8702 | 0.0003
GEN-2018-108 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.009 | 20.0115 | 0.0025
GEN-2018-108 | 03 CENTRAL | 521065 | TALOGA 4 | 138 | 7.4304 | 7.4308 | 0.0004
GEN-2018-108 | 03 CENTRAL | 521197 | CRTSJCT2 | 69 | 8.4672 | 8.4675 | 0.0003
GEN-2018-108 | 03 CENTRAL | 525832 | TUCO_INT 7 | 345 | 13.2682 | 13.2683 | 0.0001
GEN-2018-108 | 03 CENTRAL | 525850 | ELK_CT1 | 345 | 13.181 | 13.1811 | 0.0001
GEN-2018-108 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8149 | 0.0021
GEN-2018-108 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8261 | 0.0023
GEN-2018-108 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0182 | 0.0012
GEN-2018-108 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8296 | 9.832 | 0.0024
GEN-2018-108 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.7842 | 0.0169
GEN-2018-108 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.3917 | 0.0044
GEN-2018-108 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.469 | 0.0028
GEN-2018-108 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.593 | 0.0028
GEN-2018-108 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5253 | 16.5269 | 0.0016
GEN-2018-108 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3463 | 16.3479 | 0.0016
GEN-2018-108 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.7442 | 12.7449 | 0.0007
GEN-2018-108 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3782 | 11.3835 | 0.0053
GEN-2018-108 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.1014 | 11.1033 | 0.0019
GEN-2018-108 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.6821 | 16.6827 | 0.0006
GEN-2018-108 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8481 | 13.8492 | 0.0011
GEN-2018-108 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.5466 | 20.5997 | 0.0531
GEN-2018-108 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.1428 | 7.1476 | 0.0048
GEN-2018-108 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9854 | 5.9886 | 0.0032
GEN-2018-108 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0095 | 5.0116 | 0.0021
GEN-2018-108 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9257 | 18.9401 | 0.0144
GEN-2018-108 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0737 | 7.0754 | 0.0017
GEN-2018-108 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.5534 | 18.5619 | 0.0085
GEN-2018-108 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6983 | 5.6993 | 0.001
GEN-2018-108 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5286 | 23.5744 | 0.0458
GEN-2018-108 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0612 | 18.0627 | 0.0015
GEN-2018-108 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1603 | 14.1694 | 0.0091
GEN-2018-108 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.1235 | 16.1245 | 0.001
GEN-2018-108 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3731 | 10.3746 | 0.0015
GEN-2018-108 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.214 | 9.2153 | 0.0013
GEN-2018-108 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5208 | 13.5216 | 0.0008
GEN-2018-108 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.7459 | 12.7474 | 0.0015
GEN-2018-108 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.2792 | 28.2915 | 0.0123
GEN-2018-108 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2505 | 19.256 | 0.0055
GEN-2018-108 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2952 | 11.2967 | 0.0015
GEN-2018-108 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1392 | 4.1394 | 0.0002
GEN-2018-108 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 11.0361 | 11.0385 | 0.0024
GEN-2018-108 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3822 | 8.3837 | 0.0015
GEN-2018-108 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8893 | 19.8952 | 0.0059
GEN-2018-108 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.765 | 21.7731 | 0.0081
GEN-2018-108 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5642 | 14.5682 | 0.004
GEN-2018-108 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3372 | 32.3603 | 0.0231
GEN-2018-108 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2611 | 32.284 | 0.0229
GEN-2018-108 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.3557 | 22.3646 | 0.0089
GEN-2018-108 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.576 | 20.5831 | 0.0071
GEN-2018-108 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.5501 | 17.5563 | 0.0062
GEN-2018-108 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.2249 | 21.2339 | 0.009
GEN-2018-108 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2813 | 31.2925 | 0.0112
GEN-2018-108 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.7409 | 19.7493 | 0.0084
GEN-2018-108 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.9741 | 23.9865 | 0.0124
GEN-2018-108 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.7292 | 24.7422 | 0.013
GEN-2018-108 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8145 | 18.8188 | 0.0043
GEN-2018-108 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3587 | 8.3595 | 0.0008
GEN-2018-108 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7602 | 0.0065
GEN-2018-108 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7766 | 8.7776 | 0.001
GEN-2018-108 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7762 | 6.7768 | 0.0006
GEN-2018-108 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.2518 | 11.2528 | 0.001
GEN-2018-108 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8167 | 4.8167 | 0
GEN-2018-108 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2257 | 6.2257 | 0
GEN-2018-108 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1282 | 4.1296 | 0.0014
GEN-2018-108 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2368 | 5.2386 | 0.0018
GEN-2018-108 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.9001 | 4.9013 | 0.0012
GEN-2018-108 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.1198 | 12.1234 | 0.0036
GEN-2018-108 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.6405 | 11.6445 | 0.004
GEN-2018-108 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.2813 | 0.0074
GEN-2018-108 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5092 | 0.0053
GEN-2018-108 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6588 | 0.0002
GEN-2018-108 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.7827 | 10.8033 | 0.0206
GEN-2018-108 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.0696 | 16.1169 | 0.0473
GEN-2018-108 | 03 CENTRAL | 539649 | SAWYER 3 | 115 | 4.7048 | 4.7064 | 0.0016
GEN-2018-108 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2018-108 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5202 | 7.5248 | 0.0046
GEN-2018-108 | 03 CENTRAL | 539673 | MED-LDG3 | 115 | 8.2526 | 8.26 | 0.0074
GEN-2018-108 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5413 | 8.5522 | 0.0109
GEN-2018-108 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2907 | 10.2941 | 0.0034
GEN-2018-108 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.7735 | 10.7763 | 0.0028
GEN-2018-108 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0731 | 0.001
GEN-2018-108 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.2423 | 0.0024
GEN-2018-108 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.5863 | 0.0078
GEN-2018-108 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5102 | 0.0003
GEN-2018-108 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3083 | 13.313 | 0.0047
GEN-2018-108 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.4345 | 8.4422 | 0.0077
GEN-2018-108 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1489 | 0.0021
GEN-2018-108 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2018-108 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2018-108 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6265 | 13.6566 | 0.0301
GEN-2018-108 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7204 | 16.9032 | 0.1828
GEN-2018-108 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.3192 | 0.0162
GEN-2018-108 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0903 | 18.1556 | 0.0653
GEN-2018-108 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3567 | 11.3774 | 0.0207
GEN-2018-108 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0566 | 12.0697 | 0.0131
GEN-2018-108 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6022 | 11.6224 | 0.0202
GEN-2018-108 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6022 | 11.6224 | 0.0202
GEN-2018-108 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8495 | 9.8635 | 0.014
GEN-2018-108 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9933 | 9.0052 | 0.0119
GEN-2018-108 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3743 | 0.0002
GEN-2018-108 | 03 CENTRAL | 560053 | G15-052T | 345 | 12.5409 | 12.5432 | 0.0023
GEN-2018-108 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 13.5709 | 13.5816 | 0.0107
GEN-2018-108 | 03 CENTRAL | 560078 | G16-037-TAP | 345 | 8.8639 | 8.8646 | 0.0007
GEN-2018-108 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8928 | 11.911 | 0.0182
GEN-2018-108 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.654 | 0.0003
GEN-2018-108 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7263 | 10.7309 | 0.0046
GEN-2018-108 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2338 | 5.2347 | 0.0009
GEN-2018-108 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.8781 | 0.0151
GEN-2018-108 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2566 | 7.2586 | 0.002
GEN-2018-108 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.4919 | 12.4942 | 0.0023
GEN-2018-108 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.1463 | 6.1476 | 0.0013
GEN-2018-108 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.5471 | 9.5537 | 0.0066
GEN-2018-108 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.0803 | 7.0806 | 0.0003
GEN-2018-108 | 03 CENTRAL | 587230 | GEN-2016-037 | 345 | 8.4595 | 8.4601 | 0.0006
GEN-2018-108 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4173 | 10.4311 | 0.0138
GEN-2018-108 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4892 | 15.4978 | 0.0086
GEN-2018-108 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5304 | 0.0002
GEN-2018-108 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.735 | 6.7362 | 0.0012
GEN-2018-108 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0508 | 10.0538 | 0.003
GEN-2018-108 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4358 | 7.4377 | 0.0019
GEN-2018-108 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7945 | 7.7966 | 0.0021
GEN-2018-108 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 11.254 | 11.2614 | 0.0074
GEN-2018-108 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7204 | 16.9032 | 0.1828
GEN-2018-108 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.4187 | 29.4377 | 0.019
GEN-2018-108 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.523 | 6.5245 | 0.0015
GEN-2018-108 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.2641 | 10.2658 | 0.0017
GEN-2018-108 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.4411 | 20.4937 | 0.0526
GEN-2018-108 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1663 | 32.1891 | 0.0228
GEN-2018-108 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 8.7391 | 8.7409 | 0.0018
GEN-2018-108 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.5807 | 9.5816 | 0.0009
GEN-2018-108 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1705 | 7.3636 | 0.1931
GEN-2018-108 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6612 | 17.6677 | 0.0065
GEN-2018-108 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.9826 | 10.9863 | 0.0037
GEN-2018-108 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.069 | 12.0734 | 0.0044
GEN-2018-108 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 16.4376 | 16.4571 | 0.0195
GEN-2018-108 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.6766 | 0.0107
GEN-2018-108 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.7341 | 0.0159
GEN-2018-108 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7586 | 0.0008
GEN-2018-108 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 15.5265 | 15.5414 | 0.0149
GEN-2018-108 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.6789 | 0.0018
GEN-2018-108 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7622 | 6.764 | 0.0018
GEN-2018-108 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3303 | 13.3591 | 0.0288
GEN-2018-108 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4245 | 5.4246 | 0.0001
GEN-2018-108 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.071 | 4.0712 | 0.0002
GEN-2018-108 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.7856 | 3.7857 | 0.0001
GEN-2018-108 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.723 | 4.7232 | 0.0002
GEN-2018-116 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.2193 | 0.0057
GEN-2018-116 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.718 | 0.0414
GEN-2018-116 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.957 | 0.2716
GEN-2018-116 | 03 CENTRAL | 530565 | SEWARD 2 | 69 | 5.4325 | 5.5362 | 0.1037
GEN-2018-116 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.9443 | 0.1648
GEN-2018-116 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.667 | 0.0093
GEN-2018-116 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2663 | 0.0054
GEN-2018-116 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1481 | 0.0044
GEN-2018-116 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.937 | 0.1159
GEN-2018-116 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.9156 | 0.0918
GEN-2018-116 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.773 | 0.042
GEN-2018-116 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.1327 | 0.1291
GEN-2018-116 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.1082 | 0.0898
GEN-2018-116 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.5049 | 0.0076
GEN-2018-116 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.2779 | 12.1181 | 0.8402
GEN-2018-116 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.2429 | 0.0647
GEN-2018-116 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6807 | 0.0488
GEN-2018-116 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.126 | 0.0516
GEN-2018-116 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5234 | 7.8887 | 0.3653
GEN-2018-116 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5493 | 0.0145
GEN-2018-116 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.3618 | 2.3772 | 0.0154
GEN-2018-116 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.5159 | 1.5222 | 0.0063
GEN-2018-116 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.628 | 1.6352 | 0.0072
GEN-2018-116 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.1728 | 2.1858 | 0.013
GEN-2018-116 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.0877 | 5.1609 | 0.0732
GEN-2018-116 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0397 | 5.1989 | 0.1592
GEN-2018-116 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.4513 | 0.3258
GEN-2018-116 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1062 | 0.0025
GEN-2018-116 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.5675 | 1.5742 | 0.0067
GEN-2018-116 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0651 | 0.0481
GEN-2018-116 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.403 | 0.0161
GEN-2018-116 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.5508 | 0.007
GEN-2018-116 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.6515 | 0.0549
GEN-2018-116 | 03 CENTRAL | 539010 | SADLHRN3 | 115 | 4.5214 | 4.5636 | 0.0422
GEN-2018-116 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.3304 | 0.0565
GEN-2018-116 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5448 | 0.0409
GEN-2018-116 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0695 | 0.0395
GEN-2018-116 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.733 | 0.0299
GEN-2018-116 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.3695 | 0.0156
GEN-2018-116 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2395 | 8.2352 | 0.9957
GEN-2018-116 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0773 | 8.7908 | 0.7135
GEN-2018-116 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.319 | 12.21 | 0.891
GEN-2018-116 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1741 | 8.502 | 0.3279
GEN-2018-116 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3955 | 9.1825 | 0.787
GEN-2018-116 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 3.0296 | 0.0583
GEN-2018-116 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2204 | 8.0782 | 0.8578
GEN-2018-116 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.873 | 0.2035
GEN-2018-116 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6381 | 0.0596
GEN-2018-116 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.1609 | 0.0732
GEN-2018-116 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.8529 | 0.0128
GEN-2018-116 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.5716 | 0.0276
GEN-2018-116 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2228 | 8.2189 | 0.9961
GEN-2018-116 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.7445 | 0.0674
GEN-2018-116 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7621 | 6.8314 | 0.0693
GEN-2018-116 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.5162 | 0.1533
GEN-2018-116 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.5972 | 0.1571
GEN-2018-128 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0349 | 16.0358 | 0.0009
GEN-2018-128 | 03 CENTRAL | 514708 | OTTER 4 | 138 | 8.9114 | 8.9143 | 0.0029
GEN-2018-128 | 03 CENTRAL | 514709 | FRMNTAP4 | 138 | 17.6164 | 17.6324 | 0.016
GEN-2018-128 | 03 CENTRAL | 514711 | WAUKOTP4 | 138 | 15.2498 | 15.2609 | 0.0111
GEN-2018-128 | 03 CENTRAL | 514714 | WOODRNG4 | 138 | 18.7729 | 18.7914 | 0.0185
GEN-2018-128 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 16.9567 | 17.0379 | 0.0812
GEN-2018-128 | 03 CENTRAL | 514719 | CLYDE 2 | 69 | 4.5845 | 4.5869 | 0.0024
GEN-2018-128 | 03 CENTRAL | 514733 | MARSHL 4 | 138 | 8.1497 | 8.1518 | 0.0021
GEN-2018-128 | 03 CENTRAL | 514739 | MEDFORD2 | 69 | 5.6437 | 5.6477 | 0.004
GEN-2018-128 | 03 CENTRAL | 514803 | SOONER 7 | 345 | 26.0048 | 26.0321 | 0.0273
GEN-2018-128 | 03 CENTRAL | 515426 | RDRUNNR4 | 138 | 7.95 | 7.9643 | 0.0143
GEN-2018-128 | 03 CENTRAL | 515427 | RCKFALL4 | 138 | 5.5567 | 5.5637 | 0.007
GEN-2018-128 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.19 | 12.3146 | 0.1246
GEN-2018-128 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.173 | 12.2972 | 0.1242
GEN-2018-128 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 30.2606 | 30.2867 | 0.0261
GEN-2018-128 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 11.9845 | 12.2297 | 0.2452
GEN-2018-128 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.2907 | 14.378 | 0.0873
GEN-2018-128 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.6085 | 6.625 | 0.0165
GEN-2018-128 | 03 CENTRAL | 515547 | GRANTCO2 | 69 | 7.7187 | 7.7273 | 0.0086
GEN-2018-128 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.3982 | 11.448 | 0.0498
GEN-2018-128 | 03 CENTRAL | 515581 | COYOTE 4 | 138 | 8.0434 | 8.0543 | 0.0109
GEN-2018-128 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.5868 | 10.7747 | 0.1879
GEN-2018-128 | 03 CENTRAL | 515694 | ARMFTWD4 | 138 | 8.8788 | 8.8817 | 0.0029
GEN-2018-128 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.4502 | 14.459 | 0.0088
GEN-2018-128 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 16.0783 | 16.1124 | 0.0341
GEN-2018-128 | 03 CENTRAL | 515877 | REDDIRT7 | 345 | 16.0746 | 16.1086 | 0.034
GEN-2018-128 | 03 CENTRAL | 515894 | THUNDER7 | 345 | 11.716 | 11.7215 | 0.0055
GEN-2018-128 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 4.2567 | 4.2618 | 0.0051
GEN-2018-128 | 03 CENTRAL | 516010 | PINTAIL7 | 345 | 15.1617 | 15.1957 | 0.034
GEN-2018-128 | 03 CENTRAL | 516019 | KINGWD 7 | 345 | 15.1094 | 15.1432 | 0.0338
GEN-2018-128 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.6914 | 10.7355 | 0.0441
GEN-2018-128 | 03 CENTRAL | 520434 | WAKTASW4 | 138 | 6.4324 | 6.4419 | 0.0095
GEN-2018-128 | 03 CENTRAL | 520447 | BLUFCRK4 | 138 | 3.8141 | 3.8165 | 0.0024
GEN-2018-128 | 03 CENTRAL | 520452 | WAKTASB4 | 138 | 6.3975 | 6.4069 | 0.0094
GEN-2018-128 | 03 CENTRAL | 521006 | MARSHAL4 | 138 | 8.1497 | 8.1518 | 0.0021
GEN-2018-128 | 03 CENTRAL | 521085 | WAKITA 2 | 69 | 4.8459 | 4.8482 | 0.0023
GEN-2018-128 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.5788 | 7.6009 | 0.0221
GEN-2018-128 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.2133 | 5.2237 | 0.0104
GEN-2018-128 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5223 | 16.5253 | 0.003
GEN-2018-128 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3434 | 16.3463 | 0.0029
GEN-2018-128 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.743 | 12.7442 | 0.0012
GEN-2018-128 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3695 | 11.3782 | 0.0087
GEN-2018-128 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.0987 | 11.1014 | 0.0027
GEN-2018-128 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.681 | 16.6821 | 0.0011
GEN-2018-128 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.846 | 13.8481 | 0.0021
GEN-2018-128 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.492 | 20.5466 | 0.0546
GEN-2018-128 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.1379 | 7.1428 | 0.0049
GEN-2018-128 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9822 | 5.9854 | 0.0032
GEN-2018-128 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0073 | 5.0095 | 0.0022
GEN-2018-128 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.8917 | 18.9257 | 0.034
GEN-2018-128 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0363 | 7.0737 | 0.0374
GEN-2018-128 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.529 | 18.5534 | 0.0244
GEN-2018-128 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6754 | 5.6983 | 0.0229
GEN-2018-128 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.445 | 23.5286 | 0.0836
GEN-2018-128 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0572 | 18.0612 | 0.004
GEN-2018-128 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 13.963 | 14.1603 | 0.1973
GEN-2018-128 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.1207 | 16.1235 | 0.0028
GEN-2018-128 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3684 | 10.3731 | 0.0047
GEN-2018-128 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2104 | 9.214 | 0.0036
GEN-2018-128 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5189 | 13.5208 | 0.0019
GEN-2018-128 | 03 CENTRAL | 532981 | CRESWLN4 | 138 | 10.0462 | 10.0511 | 0.0049
GEN-2018-128 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 11.3002 | 11.3087 | 0.0085
GEN-2018-128 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.7346 | 12.7459 | 0.0113
GEN-2018-128 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.2794 | 6.2819 | 0.0025
GEN-2018-128 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.2455 | 28.2792 | 0.0337
GEN-2018-128 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2346 | 19.2505 | 0.0159
GEN-2018-128 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2904 | 11.2952 | 0.0048
GEN-2018-128 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.7727 | 6.7757 | 0.003
GEN-2018-128 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1386 | 4.1392 | 0.0006
GEN-2018-128 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 11.03 | 11.0361 | 0.0061
GEN-2018-128 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3787 | 8.3822 | 0.0035
GEN-2018-128 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8723 | 19.8893 | 0.017
GEN-2018-128 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.6931 | 17.7169 | 0.0238
GEN-2018-128 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.7411 | 21.765 | 0.0239
GEN-2018-128 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5346 | 14.5642 | 0.0296
GEN-2018-128 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.2783 | 32.3372 | 0.0589
GEN-2018-128 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2024 | 32.2611 | 0.0587
GEN-2018-128 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 17.1669 | 17.1836 | 0.0167
GEN-2018-128 | 03 CENTRAL | 533044 | GILL E 4 | 138 | 22.2484 | 22.2976 | 0.0492
GEN-2018-128 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.3123 | 22.3619 | 0.0496
GEN-2018-128 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.3097 | 22.3592 | 0.0495
GEN-2018-128 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.3061 | 22.3557 | 0.0496
GEN-2018-128 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5554 | 20.576 | 0.0206
GEN-2018-128 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.5298 | 17.5501 | 0.0203
GEN-2018-128 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.2006 | 21.2249 | 0.0243
GEN-2018-128 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2438 | 31.2813 | 0.0375
GEN-2018-128 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 12.5419 | 12.5527 | 0.0108
GEN-2018-128 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.7197 | 19.7409 | 0.0212
GEN-2018-128 | 03 CENTRAL | 533070 | SLATECRK4 | 138 | 7.0968 | 7.0988 | 0.002
GEN-2018-128 | 03 CENTRAL | 533071 | WACO S 4 | 138 | 19.4822 | 19.5188 | 0.0366
GEN-2018-128 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.9398 | 23.9741 | 0.0343
GEN-2018-128 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.5701 | 24.7292 | 0.1591
GEN-2018-128 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8091 | 18.8145 | 0.0054
GEN-2018-128 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3575 | 8.3587 | 0.0012
GEN-2018-128 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7444 | 22.7537 | 0.0093
GEN-2018-128 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7747 | 8.7766 | 0.0019
GEN-2018-128 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7751 | 6.7762 | 0.0011
GEN-2018-128 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.2506 | 11.2518 | 0.0012
GEN-2018-128 | 03 CENTRAL | 533541 | AKRON 2 | 69 | 7.5709 | 7.5723 | 0.0014
GEN-2018-128 | 03 CENTRAL | 533545 | FLORAL 2 | 69 | 2.589 | 2.5891 | 0.0001
GEN-2018-128 | 03 CENTRAL | 533546 | FLORALJ2 | 69 | 2.9425 | 2.9427 | 0.0002
GEN-2018-128 | 03 CENTRAL | 533551 | SC1KING2 | 69 | 3.5627 | 3.563 | 0.0003
GEN-2018-128 | 03 CENTRAL | 533557 | TIMBER 2 | 69 | 2.6021 | 2.6023 | 0.0002
GEN-2018-128 | 03 CENTRAL | 533558 | TIMBJCT2 | 69 | 9.3157 | 9.3179 | 0.0022
GEN-2018-128 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8167 | 4.8167 | 0
GEN-2018-128 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2256 | 6.2257 | 0.0001
GEN-2018-128 | 03 CENTRAL | 533795 | GILL E 2 | 69 | 30.3257 | 30.365 | 0.0393
GEN-2018-128 | 03 CENTRAL | 533796 | GILL W 2 | 69 | 30.3344 | 30.3737 | 0.0393
GEN-2018-128 | 03 CENTRAL | 533850 | VULCAN 2 | 69 | 19.5172 | 19.5335 | 0.0163
GEN-2018-128 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1261 | 4.1282 | 0.0021
GEN-2018-128 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.8959 | 4.9001 | 0.0042
GEN-2018-128 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8028 | 5.8098 | 0.007
GEN-2018-128 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.0834 | 12.1198 | 0.0364
GEN-2018-128 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.6095 | 11.6405 | 0.031
GEN-2018-128 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5134 | 7.5202 | 0.0068
GEN-2018-128 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2675 | 10.2907 | 0.0232
GEN-2018-128 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.7447 | 10.7735 | 0.0288
GEN-2018-128 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6232 | 13.6265 | 0.0033
GEN-2018-128 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7033 | 16.7204 | 0.0171
GEN-2018-128 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0799 | 18.0903 | 0.0104
GEN-2018-128 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3544 | 11.3567 | 0.0023
GEN-2018-128 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6001 | 11.6022 | 0.0021
GEN-2018-128 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6001 | 11.6022 | 0.0021
GEN-2018-128 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.848 | 9.8495 | 0.0015
GEN-2018-128 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9921 | 8.9933 | 0.0012
GEN-2018-128 | 03 CENTRAL | 560053 | G15-052T | 345 | 12.5323 | 12.5409 | 0.0086
GEN-2018-128 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.718 | 10.7263 | 0.0083
GEN-2018-128 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2147 | 5.2338 | 0.0191
GEN-2018-128 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2529 | 7.2566 | 0.0037
GEN-2018-128 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.4834 | 12.4919 | 0.0085
GEN-2018-128 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.733 | 6.735 | 0.002
GEN-2018-128 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0462 | 10.0508 | 0.0046
GEN-2018-128 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 4.0594 | 4.0641 | 0.0047
GEN-2018-128 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.3929 | 7.4358 | 0.0429
GEN-2018-128 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7472 | 7.7945 | 0.0473
GEN-2018-128 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7033 | 16.7204 | 0.0171
GEN-2018-128 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.3701 | 29.4187 | 0.0486
GEN-2018-128 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.4903 | 6.523 | 0.0327
GEN-2018-128 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.3871 | 20.4411 | 0.054
GEN-2018-128 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1081 | 32.1663 | 0.0582
GEN-2018-128 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 8.6132 | 8.7391 | 0.1259
GEN-2018-128 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.5747 | 9.5807 | 0.006
GEN-2018-128 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 10.4092 | 10.4398 | 0.0306
GEN-2018-128 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.5096 | 7.5254 | 0.0158
GEN-2018-128 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1675 | 7.1705 | 0.003
GEN-2018-128 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6446 | 17.6612 | 0.0166
GEN-2018-128 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.6273 | 10.9826 | 0.3553
GEN-2018-128 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 11.7148 | 12.069 | 0.3542
GEN-2018-128 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3272 | 13.3303 | 0.0031
GEN-2018-128 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4236 | 5.4245 | 0.0009
GEN-2018-128 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.0706 | 4.071 | 0.0004
GEN-2018-128 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.7852 | 3.7856 | 0.0004
GEN-2018-128 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.7224 | 4.723 | 0.0006
GEN-2019-001 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0339 | 16.0358 | 0.0019
GEN-2019-001 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5975 | 24.5979 | 0.0004
GEN-2019-001 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.0028 | 13.0036 | 0.0008
GEN-2019-001 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.2729 | 10.2738 | 0.0009
GEN-2019-001 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.3405 | 13.3418 | 0.0013
GEN-2019-001 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.149 | 5.1492 | 0.0002
GEN-2019-001 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.0798 | 9.0808 | 0.001
GEN-2019-001 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.0326 | 10.0357 | 0.0031
GEN-2019-001 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.5434 | 7.5439 | 0.0005
GEN-2019-001 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.2378 | 12.2452 | 0.0074
GEN-2019-001 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2241 | 3.2241 | 0
GEN-2019-001 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 18.4986 | 18.5114 | 0.0128
GEN-2019-001 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 23.993 | 23.9995 | 0.0065
GEN-2019-001 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.131 | 9.1319 | 0.0009
GEN-2019-001 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.6976 | 9.6986 | 0.001
GEN-2019-001 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 16.6978 | 16.7031 | 0.0053
GEN-2019-001 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.6907 | 17.6938 | 0.0031
GEN-2019-001 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 11.9155 | 11.9181 | 0.0026
GEN-2019-001 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.4727 | 7.4731 | 0.0004
GEN-2019-001 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 12.3053 | 12.3146 | 0.0093
GEN-2019-001 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 12.288 | 12.2972 | 0.0092
GEN-2019-001 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 30.2798 | 30.2867 | 0.0069
GEN-2019-001 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.2138 | 12.2297 | 0.0159
GEN-2019-001 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.3711 | 14.378 | 0.0069
GEN-2019-001 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.5009 | 8.5022 | 0.0013
GEN-2019-001 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.1937 | 13.197 | 0.0033
GEN-2019-001 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.2689 | 12.2764 | 0.0075
GEN-2019-001 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.7625 | 10.7747 | 0.0122
GEN-2019-001 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 10.945 | 10.9472 | 0.0022
GEN-2019-001 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 10.0285 | 10.0304 | 0.0019
GEN-2019-001 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5706 | 19.5721 | 0.0015
GEN-2019-001 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 6.405 | 6.4051 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.5725 | 8.5753 | 0.0028
GEN-2019-001 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.434 | 14.459 | 0.025
GEN-2019-001 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 15.5185 | 15.5265 | 0.008
GEN-2019-001 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.357 | 10.361 | 0.004
GEN-2019-001 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.6843 | 11.6894 | 0.0051
GEN-2019-001 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.5287 | 9.5315 | 0.0028
GEN-2019-001 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.5181 | 9.5209 | 0.0028
GEN-2019-001 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.2002 | 8.2005 | 0.0003
GEN-2019-001 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.0994 | 10.1025 | 0.0031
GEN-2019-001 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.729 | 11.7335 | 0.0045
GEN-2019-001 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3408 | 19.3423 | 0.0015
GEN-2019-001 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.8532 | 6.8534 | 0.0002
GEN-2019-001 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.8024 | 6.8039 | 0.0015
GEN-2019-001 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.98 | 7.9803 | 0.0003
GEN-2019-001 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.8698 | 8.8699 | 0.0001
GEN-2019-001 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0074 | 20.009 | 0.0016
GEN-2019-001 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8112 | 7.8128 | 0.0016
GEN-2019-001 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7584 | 13.7673 | 0.0089
GEN-2019-001 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3849 | 9.3873 | 0.0024
GEN-2019-001 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4646 | 7.4662 | 0.0016
GEN-2019-001 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5886 | 7.5902 | 0.0016
GEN-2019-001 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 22.1375 | 22.1421 | 0.0046
GEN-2019-001 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.2361 | 10.2398 | 0.0037
GEN-2019-001 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5138 | 16.5253 | 0.0115
GEN-2019-001 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3351 | 16.3463 | 0.0112
GEN-2019-001 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.7395 | 12.7442 | 0.0047
GEN-2019-001 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.344 | 11.3782 | 0.0342
GEN-2019-001 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.091 | 11.1014 | 0.0104
GEN-2019-001 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.6782 | 16.6821 | 0.0039
GEN-2019-001 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8401 | 13.8481 | 0.008
GEN-2019-001 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7489 | 9.757 | 0.0081
GEN-2019-001 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4789 | 9.4865 | 0.0076
GEN-2019-001 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.1414 | 20.5466 | 0.4052
GEN-2019-001 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 6.6309 | 7.1428 | 0.5119
GEN-2019-001 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.4475 | 5.9854 | 0.5379
GEN-2019-001 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.4597 | 5.0095 | 0.5498
GEN-2019-001 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.8234 | 18.9257 | 0.1023
GEN-2019-001 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0643 | 7.0737 | 0.0094
GEN-2019-001 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1073 | 18.1108 | 0.0035
GEN-2019-001 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.4957 | 18.5534 | 0.0577
GEN-2019-001 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6926 | 5.6983 | 0.0057
GEN-2019-001 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.1938 | 23.5286 | 0.3348
GEN-2019-001 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0507 | 18.0612 | 0.0105
GEN-2019-001 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1106 | 14.1603 | 0.0497
GEN-2019-001 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.1162 | 16.1235 | 0.0073
GEN-2019-001 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3623 | 10.3731 | 0.0108
GEN-2019-001 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2056 | 9.214 | 0.0084
GEN-2019-001 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5157 | 13.5208 | 0.0051
GEN-2019-001 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.6508 | 21.6545 | 0.0037
GEN-2019-001 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0054 | 14.0092 | 0.0038
GEN-2019-001 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5909 | 8.5966 | 0.0057
GEN-2019-001 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2596 | 13.2675 | 0.0079
GEN-2019-001 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 11.3025 | 11.3087 | 0.0062
GEN-2019-001 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.7373 | 12.7459 | 0.0086
GEN-2019-001 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.28 | 6.2819 | 0.0019
GEN-2019-001 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.194 | 28.2792 | 0.0852
GEN-2019-001 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2348 | 11.2448 | 0.01
GEN-2019-001 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2122 | 19.2505 | 0.0383
GEN-2019-001 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2845 | 11.2952 | 0.0107
GEN-2019-001 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4767 | 22.5191 | 0.0424
GEN-2019-001 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.7734 | 6.7757 | 0.0023
GEN-2019-001 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.1378 | 4.1392 | 0.0014
GEN-2019-001 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.5334 | 8.5427 | 0.0093
GEN-2019-001 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1113 | 7.1169 | 0.0056
GEN-2019-001 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 11.0192 | 11.0361 | 0.0169
GEN-2019-001 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.3725 | 8.3822 | 0.0097
GEN-2019-001 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8484 | 19.8893 | 0.0409
GEN-2019-001 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.7096 | 21.765 | 0.0554
GEN-2019-001 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.5422 | 14.5642 | 0.022
GEN-2019-001 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.9292 | 18.9658 | 0.0366
GEN-2019-001 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.6972 | 17.7406 | 0.0434
GEN-2019-001 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.2982 | 25.3515 | 0.0533
GEN-2019-001 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.1768 | 32.3372 | 0.1604
GEN-2019-001 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.1014 | 32.2611 | 0.1597
GEN-2019-001 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 22.3085 | 22.3619 | 0.0534
GEN-2019-001 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 22.3059 | 22.3592 | 0.0533
GEN-2019-001 | 03 CENTRAL | 533047 | GILL 4 | 138 | 22.3024 | 22.3557 | 0.0533
GEN-2019-001 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.447 | 17.4849 | 0.0379
GEN-2019-001 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5274 | 20.576 | 0.0486
GEN-2019-001 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.5085 | 17.5501 | 0.0416
GEN-2019-001 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.1625 | 21.2249 | 0.0624
GEN-2019-001 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.7933 | 20.8367 | 0.0434
GEN-2019-001 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.207 | 31.2813 | 0.0743
GEN-2019-001 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 12.5441 | 12.5527 | 0.0086
GEN-2019-001 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.9327 | 17.968 | 0.0353
GEN-2019-001 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.6827 | 19.7409 | 0.0582
GEN-2019-001 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.8437 | 19.878 | 0.0343
GEN-2019-001 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.8888 | 23.9741 | 0.0853
GEN-2019-001 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.6698 | 24.7292 | 0.0594
GEN-2019-001 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.6029 | 15.6064 | 0.0035
GEN-2019-001 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6595 | 2.6599 | 0.0004
GEN-2019-001 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9702 | 3.9711 | 0.0009
GEN-2019-001 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.223 | 7.2245 | 0.0015
GEN-2019-001 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.8143 | 9.8197 | 0.0054
GEN-2019-001 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.0014 | 10.007 | 0.0056
GEN-2019-001 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.794 | 18.8145 | 0.0205
GEN-2019-001 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.1643 | 8.1684 | 0.0041
GEN-2019-001 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3542 | 8.3587 | 0.0045
GEN-2019-001 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7186 | 22.7537 | 0.0351
GEN-2019-001 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.6036 | 17.6217 | 0.0181
GEN-2019-001 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.2849 | 18.3044 | 0.0195
GEN-2019-001 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.6083 | 8.6109 | 0.0026
GEN-2019-001 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.8647 | 10.8689 | 0.0042
GEN-2019-001 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7706 | 8.7766 | 0.006
GEN-2019-001 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7726 | 6.7762 | 0.0036
GEN-2019-001 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.2472 | 11.2518 | 0.0046
GEN-2019-001 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.9926 | 6.9943 | 0.0017
GEN-2019-001 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0327 | 4.0333 | 0.0006
GEN-2019-001 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.4832 | 7.4853 | 0.0021
GEN-2019-001 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3431 | 6.3446 | 0.0015
GEN-2019-001 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1489 | 6.1504 | 0.0015
GEN-2019-001 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5225 | 6.5241 | 0.0016
GEN-2019-001 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6067 | 14.6156 | 0.0089
GEN-2019-001 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5463 | 3.5464 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1617 | 3.1617 | 0
GEN-2019-001 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.153 | 5.1531 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5449 | 3.5449 | 0
GEN-2019-001 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8166 | 4.8167 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2255 | 6.2257 | 0.0002
GEN-2019-001 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 20.4102 | 20.4334 | 0.0232
GEN-2019-001 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1265 | 4.1282 | 0.0017
GEN-2019-001 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2342 | 5.2368 | 0.0026
GEN-2019-001 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.8065 | 5.8098 | 0.0033
GEN-2019-001 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 12.1055 | 12.1198 | 0.0143
GEN-2019-001 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.6275 | 11.6405 | 0.013
GEN-2019-001 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2696 | 12.2739 | 0.0043
GEN-2019-001 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5007 | 10.5039 | 0.0032
GEN-2019-001 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.7717 | 10.7827 | 0.011
GEN-2019-001 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.0444 | 16.0696 | 0.0252
GEN-2019-001 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5147 | 7.5202 | 0.0055
GEN-2019-001 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5352 | 8.5413 | 0.0061
GEN-2019-001 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2806 | 10.2907 | 0.0101
GEN-2019-001 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.7622 | 10.7735 | 0.0113
GEN-2019-001 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5739 | 12.5785 | 0.0046
GEN-2019-001 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3057 | 13.3083 | 0.0026
GEN-2019-001 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.43 | 8.4345 | 0.0045
GEN-2019-001 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6119 | 13.6265 | 0.0146
GEN-2019-001 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6406 | 16.7204 | 0.0798
GEN-2019-001 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.2944 | 13.303 | 0.0086
GEN-2019-001 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0572 | 18.0903 | 0.0331
GEN-2019-001 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3466 | 11.3567 | 0.0101
GEN-2019-001 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0496 | 12.0566 | 0.007
GEN-2019-001 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.5925 | 11.6022 | 0.0097
GEN-2019-001 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.5925 | 11.6022 | 0.0097
GEN-2019-001 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8427 | 9.8495 | 0.0068
GEN-2019-001 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9876 | 8.9933 | 0.0057
GEN-2019-001 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6742 | 2.6742 | 0
GEN-2019-001 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.8936 | 27.8964 | 0.0028
GEN-2019-001 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 26.3207 | 26.3238 | 0.0031
GEN-2019-001 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.6602 | 25.6631 | 0.0029
GEN-2019-001 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.6602 | 25.6631 | 0.0029
GEN-2019-001 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8129 | 2.8129 | 0
GEN-2019-001 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6725 | 0.6725 | 0
GEN-2019-001 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6442 | 0.6442 | 0
GEN-2019-001 | 03 CENTRAL | 560053 | G15-052T | 345 | 12.5258 | 12.5409 | 0.0151
GEN-2019-001 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 13.5654 | 13.5709 | 0.0055
GEN-2019-001 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8837 | 11.8928 | 0.0091
GEN-2019-001 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.693 | 10.7263 | 0.0333
GEN-2019-001 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2291 | 5.2338 | 0.0047
GEN-2019-001 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.855 | 12.863 | 0.008
GEN-2019-001 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2419 | 7.2566 | 0.0147
GEN-2019-001 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.4769 | 12.4919 | 0.015
GEN-2019-001 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.1455 | 6.1463 | 0.0008
GEN-2019-001 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.5437 | 9.5471 | 0.0034
GEN-2019-001 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.0801 | 7.0803 | 0.0002
GEN-2019-001 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4105 | 10.4173 | 0.0068
GEN-2019-001 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4849 | 15.4892 | 0.0043
GEN-2019-001 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.7274 | 6.735 | 0.0076
GEN-2019-001 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0328 | 10.0508 | 0.018
GEN-2019-001 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.425 | 7.4358 | 0.0108
GEN-2019-001 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7827 | 7.7945 | 0.0118
GEN-2019-001 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 5.911 | 5.9129 | 0.0019
GEN-2019-001 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 6.5179 | 6.5202 | 0.0023
GEN-2019-001 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 11.2501 | 11.254 | 0.0039
GEN-2019-001 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6406 | 16.7204 | 0.0798
GEN-2019-001 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2862 | 29.4187 | 0.1325
GEN-2019-001 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.5148 | 6.523 | 0.0082
GEN-2019-001 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.2632 | 10.2641 | 0.0009
GEN-2019-001 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.0401 | 20.4411 | 0.401
GEN-2019-001 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.0077 | 32.1663 | 0.1586
GEN-2019-001 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 8.731 | 8.7391 | 0.0081
GEN-2019-001 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.5762 | 9.5807 | 0.0045
GEN-2019-001 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.8202 | 27.8229 | 0.0027
GEN-2019-001 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.742 | 27.7448 | 0.0028
GEN-2019-001 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9585 | 11.96 | 0.0015
GEN-2019-001 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1563 | 7.1705 | 0.0142
GEN-2019-001 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6157 | 17.6612 | 0.0455
GEN-2019-001 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.965 | 10.9826 | 0.0176
GEN-2019-001 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.0476 | 12.069 | 0.0214
GEN-2019-001 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 16.4275 | 16.4376 | 0.0101
GEN-2019-001 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6605 | 9.6659 | 0.0054
GEN-2019-001 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7101 | 11.7182 | 0.0081
GEN-2019-001 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 15.5185 | 15.5265 | 0.008
GEN-2019-001 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3163 | 13.3303 | 0.014
GEN-2019-001 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4242 | 5.4245 | 0.0003
GEN-2019-001 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.0709 | 4.071 | 0.0001
GEN-2019-001 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.7855 | 3.7856 | 0.0001
GEN-2019-001 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.7228 | 4.723 | 0.0002
GEN-2019-016 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.575 | 10.6145 | 0.0395
GEN-2019-016 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.816 | 14.0079 | 0.1919
GEN-2019-016 | 03 CENTRAL | 300051 | 7FRANKSRCTP | 345 | 16.3391 | 16.3542 | 0.0151
GEN-2019-016 | 03 CENTRAL | 300070 | 5CLARK | 161 | 8.1641 | 8.1821 | 0.018
GEN-2019-016 | 03 CENTRAL | 300088 | 5HUBEN | 161 | 15.9321 | 15.9635 | 0.0314
GEN-2019-016 | 03 CENTRAL | 300089 | 5JAMESV | 161 | 16.1242 | 16.1747 | 0.0505
GEN-2019-016 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 18.9584 | 19.7725 | 0.814
GEN-2019-016 | 03 CENTRAL | 300108 | 5OSCEOLTP | 161 | 6.6486 | 6.6616 | 0.013
GEN-2019-016 | 03 CENTRAL | 300118 | 5STKAEC | 161 | 9.2629 | 9.3264 | 0.0635
GEN-2019-016 | 03 CENTRAL | 300348 | 5BTLFD | 161 | 21.9339 | 22.0311 | 0.0972
GEN-2019-016 | 03 CENTRAL | 300657 | 2ASHGRV | 69 | 4.0508 | 4.053 | 0.0022
GEN-2019-016 | 03 CENTRAL | 300658 | 2BILLNG | 69 | 8.4299 | 8.444 | 0.0141
GEN-2019-016 | 03 CENTRAL | 300664 | 2CAVESP | 69 | 2.4067 | 2.4075 | 0.0008
GEN-2019-016 | 03 CENTRAL | 300665 | 2CLEVER | 69 | 4.7154 | 4.7185 | 0.0031
GEN-2019-016 | 03 CENTRAL | 300668 | 2DADEVL | 69 | 5.848 | 5.8595 | 0.0115
GEN-2019-016 | 03 CENTRAL | 300669 | 2ELWOOD | 69 | 5.4268 | 5.4301 | 0.0033
GEN-2019-016 | 03 CENTRAL | 300672 | 2GRNFLD | 69 | 6.1117 | 6.1205 | 0.0088
GEN-2019-016 | 03 CENTRAL | 300676 | 2LOCKWD | 69 | 4.0886 | 4.0919 | 0.0033
GEN-2019-016 | 03 CENTRAL | 300677 | 2MTVRN | 69 | 9.0865 | 9.1077 | 0.0212
GEN-2019-016 | 03 CENTRAL | 300678 | 5NIXA-1 | 161 | 19.3922 | 19.4693 | 0.0771
GEN-2019-016 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.5917 | 6.5947 | 0.003
GEN-2019-016 | 03 CENTRAL | 300683 | 2MIDWY | 69 | 4.78 | 4.7858 | 0.0058
GEN-2019-016 | 03 CENTRAL | 300684 | 2MIDWYTP | 69 | 8.9012 | 8.9214 | 0.0202
GEN-2019-016 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0009 | 16.0358 | 0.0349
GEN-2019-016 | 03 CENTRAL | 300770 | 2BUFFLO | 69 | 5.9335 | 5.9377 | 0.0042
GEN-2019-016 | 03 CENTRAL | 300774 | 2EUDORA | 69 | 6.162 | 6.1743 | 0.0123
GEN-2019-016 | 03 CENTRAL | 300782 | 2MORGAN | 69 | 7.1017 | 7.1211 | 0.0194
GEN-2019-016 | 03 CENTRAL | 300785 | 2PLEAST | 69 | 4.4105 | 4.4137 | 0.0032
GEN-2019-016 | 03 CENTRAL | 300788 | 2SLAGLE | 69 | 6.2312 | 6.239 | 0.0078
GEN-2019-016 | 03 CENTRAL | 300791 | 2WOODHL | 69 | 2.211 | 2.2116 | 0.0006
GEN-2019-016 | 03 CENTRAL | 300793 | 5HYDERHL | 161 | 8.5956 | 8.6437 | 0.0481
GEN-2019-016 | 03 CENTRAL | 300797 | 2ARCOLA | 69 | 4.9507 | 4.956 | 0.0053
GEN-2019-016 | 03 CENTRAL | 300798 | 2HYDERHL | 69 | 8.5537 | 8.5692 | 0.0155
GEN-2019-016 | 03 CENTRAL | 300800 | 2BONA | 69 | 3.4917 | 3.4958 | 0.0041
GEN-2019-016 | 03 CENTRAL | 300816 | 5COLLINS | 161 | 6.7429 | 6.7651 | 0.0222
GEN-2019-016 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.9544 | 13.0036 | 0.0492
GEN-2019-016 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.0616 | 13.0886 | 0.027
GEN-2019-016 | 03 CENTRAL | 301040 | 5OSCEOL | 161 | 6.6327 | 6.6456 | 0.0129
GEN-2019-016 | 03 CENTRAL | 301161 | 5LOGAN | 161 | 13.7047 | 13.7356 | 0.0309
GEN-2019-016 | 03 CENTRAL | 301393 | 2ROUNDGROVE | 69 | 4.3085 | 4.3118 | 0.0033
GEN-2019-016 | 03 CENTRAL | 301395 | 2ROUNDGRVETP | 69 | 4.4812 | 4.4848 | 0.0036
GEN-2019-016 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.6472 | 6.6602 | 0.013
GEN-2019-016 | 03 CENTRAL | 301521 | 5REEDSP | 161 | 8.6329 | 8.6427 | 0.0098
GEN-2019-016 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.6399 | 6.6528 | 0.0129
GEN-2019-016 | 03 CENTRAL | 301554 | 7FRANKSRCT | 345 | 16.2934 | 16.3085 | 0.0151
GEN-2019-016 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 18.9589 | 19.7712 | 0.8123
GEN-2019-016 | 03 CENTRAL | 505472 | TABLE R5 | 161 | 15.1069 | 15.1252 | 0.0183
GEN-2019-016 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.8836 | 15.8912 | 0.0076
GEN-2019-016 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.8316 | 16.8434 | 0.0118
GEN-2019-016 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 27.3841 | 27.5434 | 0.1593
GEN-2019-016 | 03 CENTRAL | 505494 | SPRGFLD2 | 69 | 16.1835 | 16.2088 | 0.0253
GEN-2019-016 | 03 CENTRAL | 505496 | NIXA 5 | 161 | 12.7225 | 12.7517 | 0.0292
GEN-2019-016 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 9.9754 | 10.0565 | 0.0811
GEN-2019-016 | 03 CENTRAL | 505501 | NIXA 2 | 69 | 12.4909 | 12.5033 | 0.0124
GEN-2019-016 | 03 CENTRAL | 506934 | FLINTCR5 | 161 | 34.5993 | 34.6129 | 0.0136
GEN-2019-016 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.7767 | 15.7865 | 0.0098
GEN-2019-016 | 03 CENTRAL | 506979 | SHIPERD7 | 345 | 10.5945 | 10.5987 | 0.0042
GEN-2019-016 | 03 CENTRAL | 512750 | TONECE7 | 345 | 15.5521 | 15.5609 | 0.0088
GEN-2019-016 | 03 CENTRAL | 547400 | MON376J2 | 69 | 4.1275 | 4.1288 | 0.0013
GEN-2019-016 | 03 CENTRAL | 547401 | MON376 2 | 69 | 6.6961 | 6.6995 | 0.0034
GEN-2019-016 | 03 CENTRAL | 547402 | MON416J2 | 69 | 3.6351 | 3.636 | 0.0009
GEN-2019-016 | 03 CENTRAL | 547403 | MON416 2 | 69 | 3.5406 | 3.5415 | 0.0009
GEN-2019-016 | 03 CENTRAL | 547404 | PUR390 2 | 69 | 1.7995 | 1.7997 | 0.0002
GEN-2019-016 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.9222 | 7.9269 | 0.0047
GEN-2019-016 | 03 CENTRAL | 547406 | MON352 2 | 69 | 7.6103 | 7.6147 | 0.0044
GEN-2019-016 | 03 CENTRAL | 547407 | MON311J2 | 69 | 6.7811 | 6.7845 | 0.0034
GEN-2019-016 | 03 CENTRAL | 547408 | MON311 2 | 69 | 6.6961 | 6.6995 | 0.0034
GEN-2019-016 | 03 CENTRAL | 547424 | RES364 2 | 69 | 4.0681 | 4.0716 | 0.0035
GEN-2019-016 | 03 CENTRAL | 547425 | HER209 2 | 69 | 1.3961 | 1.3973 | 0.0012
GEN-2019-016 | 03 CENTRAL | 547432 | BUF243J2 | 69 | 3.3765 | 3.3804 | 0.0039
GEN-2019-016 | 03 CENTRAL | 547434 | BUF409 2 | 69 | 2.6886 | 2.6917 | 0.0031
GEN-2019-016 | 03 CENTRAL | 547436 | CUPTAP 2 | 69 | 6.0806 | 6.1039 | 0.0233
GEN-2019-016 | 03 CENTRAL | 547437 | CUPSUB 2 | 69 | 4.9681 | 4.9836 | 0.0155
GEN-2019-016 | 03 CENTRAL | 547440 | EXP450T2 | 69 | 5.7468 | 5.7608 | 0.014
GEN-2019-016 | 03 CENTRAL | 547441 | EXP4502 | 69 | 4.6312 | 4.6403 | 0.0091
GEN-2019-016 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.756 | 5.7579 | 0.0019
GEN-2019-016 | 03 CENTRAL | 547464 | BOL 73 5 | 161 | 4.8753 | 4.9245 | 0.0492
GEN-2019-016 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.767 | 10.8055 | 0.0385
GEN-2019-016 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 18.0222 | 18.0324 | 0.0102
GEN-2019-016 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 8.0602 | 8.0698 | 0.0096
GEN-2019-016 | 03 CENTRAL | 547478 | DAD368 5 | 161 | 17.8368 | 18.6813 | 0.8445
GEN-2019-016 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 15.2212 | 15.237 | 0.0158
GEN-2019-016 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.13 | 12.1533 | 0.0233
GEN-2019-016 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.6105 | 20.62 | 0.0095
GEN-2019-016 | 03 CENTRAL | 547493 | BOL431 5 | 161 | 6.0629 | 6.1448 | 0.0819
GEN-2019-016 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.7125 | 8.7772 | 0.0647
GEN-2019-016 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.6686 | 14.6749 | 0.0063
GEN-2019-016 | 03 CENTRAL | 547528 | BOL 73 2 | 69 | 7.9908 | 8.0317 | 0.0409
GEN-2019-016 | 03 CENTRAL | 547529 | SED 80 2 | 69 | 17.1582 | 17.2068 | 0.0486
GEN-2019-016 | 03 CENTRAL | 547536 | ASH121 2 | 69 | 7.2541 | 7.2725 | 0.0184
GEN-2019-016 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.5857 | 12.6076 | 0.0219
GEN-2019-016 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.9882 | 10.9979 | 0.0097
GEN-2019-016 | 03 CENTRAL | 547545 | FRP217 2 | 69 | 4.5347 | 4.5483 | 0.0136
GEN-2019-016 | 03 CENTRAL | 547546 | BIL221 2 | 69 | 10.0962 | 10.1133 | 0.0171
GEN-2019-016 | 03 CENTRAL | 547547 | BUF243 2 | 69 | 3.3129 | 3.3167 | 0.0038
GEN-2019-016 | 03 CENTRAL | 547549 | ARC250 2 | 69 | 4.0715 | 4.0769 | 0.0054
GEN-2019-016 | 03 CENTRAL | 547550 | GLD251 2 | 69 | 3.8011 | 3.8036 | 0.0025
GEN-2019-016 | 03 CENTRAL | 547552 | LAW260 2 | 69 | 5.7083 | 5.7173 | 0.009
GEN-2019-016 | 03 CENTRAL | 547553 | ALB262 2 | 69 | 8.7509 | 8.7671 | 0.0162
GEN-2019-016 | 03 CENTRAL | 547567 | BRT323 2 | 69 | 5.9614 | 5.9735 | 0.0121
GEN-2019-016 | 03 CENTRAL | 547573 | HTC338 2 | 69 | 6.6048 | 6.6151 | 0.0103
GEN-2019-016 | 03 CENTRAL | 547575 | BUF342 2 | 69 | 3.5849 | 3.5903 | 0.0054
GEN-2019-016 | 03 CENTRAL | 547578 | AUR355 2 | 69 | 9.5662 | 9.5797 | 0.0135
GEN-2019-016 | 03 CENTRAL | 547580 | REP359 2 | 69 | 13.3256 | 13.3512 | 0.0256
GEN-2019-016 | 03 CENTRAL | 547584 | BOL367 2 | 69 | 5.2084 | 5.226 | 0.0176
GEN-2019-016 | 03 CENTRAL | 547585 | DAD368 2 | 69 | 9.8277 | 9.895 | 0.0673
GEN-2019-016 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.674 | 12.6861 | 0.0121
GEN-2019-016 | 03 CENTRAL | 547598 | LKW400 2 | 69 | 3.705 | 3.7087 | 0.0037
GEN-2019-016 | 03 CENTRAL | 547605 | STK418 2 | 69 | 7.5963 | 7.615 | 0.0187
GEN-2019-016 | 03 CENTRAL | 547606 | MTV420 2 | 69 | 7.1226 | 7.132 | 0.0094
GEN-2019-016 | 03 CENTRAL | 547611 | MAR437 2 | 69 | 6.0204 | 6.0256 | 0.0052
GEN-2019-016 | 03 CENTRAL | 547612 | BOL602 2 | 69 | 4.8615 | 4.8769 | 0.0154
GEN-2019-016 | 03 CENTRAL | 547613 | GRN614 2 | 69 | 4.2716 | 4.2776 | 0.006
GEN-2019-016 | 03 CENTRAL | 547616 | STK324J2 | 69 | 6.1239 | 6.1362 | 0.0123
GEN-2019-016 | 03 CENTRAL | 547618 | CPK446 2 | 69 | 10.4849 | 10.5141 | 0.0292
GEN-2019-016 | 03 CENTRAL | 547691 | WIL369 2 | 69 | 6.2953 | 6.3054 | 0.0101
GEN-2019-016 | 03 CENTRAL | 547726 | WIL482 | 69 | 7.2602 | 7.2737 | 0.0135
GEN-2019-016 | 03 CENTRAL | 547727 | WIL479 | 69 | 7.6824 | 7.6964 | 0.014
GEN-2019-016 | 03 CENTRAL | 549903 | JRPS 69B-2 2 | 69 | 19.5581 | 19.5904 | 0.0323
GEN-2019-016 | 03 CENTRAL | 549904 | JAMES RIVER2 | 69 | 16.1167 | 16.1374 | 0.0207
GEN-2019-016 | 03 CENTRAL | 549911 | GOLDEN 2 | 69 | 20.6553 | 20.6983 | 0.043
GEN-2019-016 | 03 CENTRAL | 549925 | NICHOLS 2 | 69 | 24.5494 | 24.6289 | 0.0795
GEN-2019-016 | 03 CENTRAL | 549954 | JTEC 5 | 161 | 26.9616 | 27.1091 | 0.1475
GEN-2019-016 | 03 CENTRAL | 549955 | JUNCTION 5 | 161 | 21.0027 | 21.1039 | 0.1012
GEN-2019-016 | 03 CENTRAL | 549956 | NICHOLS 5 | 161 | 19.1736 | 19.258 | 0.0844
GEN-2019-016 | 03 CENTRAL | 549957 | WEST BELT 5 | 161 | 18.8988 | 18.9798 | 0.081
GEN-2019-016 | 03 CENTRAL | 549958 | MAIN STREET5 | 161 | 19.1226 | 19.2044 | 0.0818
GEN-2019-016 | 03 CENTRAL | 549959 | BATTLEFIELD5 | 161 | 26.7342 | 26.886 | 0.1518
GEN-2019-016 | 03 CENTRAL | 549960 | SW DISP PLT5 | 161 | 25.6846 | 25.8194 | 0.1348
GEN-2019-016 | 03 CENTRAL | 549961 | JAMES RIVER5 | 161 | 15.8585 | 15.8992 | 0.0407
GEN-2019-016 | 03 CENTRAL | 549962 | MILL 5 | 161 | 16.0311 | 16.0758 | 0.0447
GEN-2019-016 | 03 CENTRAL | 549963 | MENTOR 5 | 161 | 15.0424 | 15.0812 | 0.0388
GEN-2019-016 | 03 CENTRAL | 549966 | SUMMIT 5 | 161 | 13.3972 | 13.4328 | 0.0356
GEN-2019-016 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 28.4082 | 28.602 | 0.1938
GEN-2019-016 | 03 CENTRAL | 549970 | CLAY 5 | 161 | 18.7957 | 18.858 | 0.0623
GEN-2019-016 | 03 CENTRAL | 549971 | PIC WEST 5 | 161 | 17.2908 | 17.3574 | 0.0666
GEN-2019-016 | 03 CENTRAL | 549979 | BATTLEFIELD2 | 69 | 20.9385 | 20.9821 | 0.0436
GEN-2019-016 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.8896 | 11.9767 | 0.0871
GEN-2019-016 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 6.1779 | 6.1802 | 0.0023
GEN-2019-016 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 8.2842 | 8.3496 | 0.0654
GEN-2019-016 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 8.2842 | 8.3496 | 0.0654
GEN-2019-016 | 03 CENTRAL | 763560 | GEN-2019-016 | 161 | 17.5255 | 18.3706 | 0.8451
GEN-2019-016 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.8557 | 7.8694 | 0.0137
GEN-2019-016 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.8732 | 7.887 | 0.0138
GEN-2019-018 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.2839 | 5.5459 | 0.262
GEN-2019-018 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.516 | 6.673 | 0.157
GEN-2019-018 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 5.005 | 5.0856 | 0.0806
GEN-2019-018 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1879 | 4.2442 | 0.0563
GEN-2019-018 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.2561 | 4.521 | 0.2649
GEN-2019-018 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.2206 | 4.286 | 0.0654
GEN-2019-018 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3563 | 11.3782 | 0.0219
GEN-2019-018 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.536 | 8.5966 | 0.0606
GEN-2019-018 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.8918 | 7.9396 | 0.0478
GEN-2019-018 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.5065 | 12.53 | 0.0235
GEN-2019-018 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.2023 | 7.2245 | 0.0222
GEN-2019-018 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.74 | 18.8145 | 0.0745
GEN-2019-018 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3463 | 8.3587 | 0.0124
GEN-2019-018 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.6743 | 22.7537 | 0.0794
GEN-2019-018 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.4679 | 11.5521 | 0.0842
GEN-2019-018 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.5565 | 8.6109 | 0.0544
GEN-2019-018 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.6046 | 10.69 | 0.0854
GEN-2019-018 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.7725 | 10.8689 | 0.0964
GEN-2019-018 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7718 | 8.7766 | 0.0048
GEN-2019-018 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7734 | 6.7762 | 0.0028
GEN-2019-018 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.1424 | 11.2518 | 0.1094
GEN-2019-018 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.8791 | 6.9943 | 0.1152
GEN-2019-018 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.336 | 3.3539 | 0.0179
GEN-2019-018 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.553 | 3.58 | 0.027
GEN-2019-018 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3523 | 6.363 | 0.0107
GEN-2019-018 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4292 | 6.4401 | 0.0109
GEN-2019-030 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.0326 | 10.0357 | 0.0031
GEN-2019-030 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 18.4934 | 18.5114 | 0.018
GEN-2019-030 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 23.9907 | 23.9995 | 0.0088
GEN-2019-030 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.1307 | 9.1319 | 0.0012
GEN-2019-030 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.6973 | 9.6986 | 0.0013
GEN-2019-030 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 16.697 | 16.7031 | 0.0061
GEN-2019-030 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 11.9151 | 11.9181 | 0.003
GEN-2019-030 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.5007 | 8.5022 | 0.0015
GEN-2019-030 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.1932 | 13.197 | 0.0038
GEN-2019-030 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.5714 | 8.5753 | 0.0039
GEN-2019-030 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.4271 | 14.459 | 0.0319
GEN-2019-030 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 15.5174 | 15.5265 | 0.0091
GEN-2019-030 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.3554 | 10.361 | 0.0056
GEN-2019-030 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.6823 | 11.6894 | 0.0071
GEN-2019-030 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.5268 | 9.5315 | 0.0047
GEN-2019-030 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.5162 | 9.5209 | 0.0047
GEN-2019-030 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.7285 | 11.7335 | 0.005
GEN-2019-030 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.8023 | 6.8039 | 0.0016
GEN-2019-030 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0072 | 20.009 | 0.0018
GEN-2019-030 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.0911 | 6.1077 | 0.0166
GEN-2019-030 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.3818 | 6.3888 | 0.007
GEN-2019-030 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.6719 | 9.7167 | 0.0448
GEN-2019-030 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2121 | 3.2136 | 0.0015
GEN-2019-030 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6656 | 8.6766 | 0.011
GEN-2019-030 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6976 | 10.7358 | 0.0382
GEN-2019-030 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2411 | 2.2418 | 0.0007
GEN-2019-030 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6379 | 10.6534 | 0.0155
GEN-2019-030 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.7966 | 8.8211 | 0.0245
GEN-2019-030 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7722 | 7.8128 | 0.0406
GEN-2019-030 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7848 | 10.8238 | 0.039
GEN-2019-030 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.2807 | 6.2841 | 0.0034
GEN-2019-030 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.5234 | 5.5259 | 0.0025
GEN-2019-030 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.7932 | 5.796 | 0.0028
GEN-2019-030 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5316 | 3.5348 | 0.0032
GEN-2019-030 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0659 | 10.0796 | 0.0137
GEN-2019-030 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6533 | 2.6543 | 0.001
GEN-2019-030 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1033 | 8.1255 | 0.0222
GEN-2019-030 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1031 | 2.1037 | 0.0006
GEN-2019-030 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.9965 | 8.017 | 0.0205
GEN-2019-030 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3827 | 5.3869 | 0.0042
GEN-2019-030 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6976 | 10.7358 | 0.0382
GEN-2019-030 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.542 | 3.5438 | 0.0018
GEN-2019-030 | 03 CENTRAL | 531210 | BLUEJAY3 | 115 | 2.2106 | 2.2108 | 0.0002
GEN-2019-030 | 03 CENTRAL | 531211 | CHRLSTN3 | 115 | 2.1469 | 2.1471 | 0.0002
GEN-2019-030 | 03 CENTRAL | 531212 | TWNSPRG3 | 115 | 1.6702 | 1.6704 | 0.0002
GEN-2019-030 | 03 CENTRAL | 531213 | SANTAFE3 | 115 | 2.8182 | 2.8186 | 0.0004
GEN-2019-030 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.9108 | 10.9175 | 0.0067
GEN-2019-030 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.9766 | 7.9799 | 0.0033
GEN-2019-030 | 03 CENTRAL | 531407 | INGALLS3 | 115 | 2.8167 | 2.8171 | 0.0004
GEN-2019-030 | 03 CENTRAL | 531408 | PIERCVL3 | 115 | 4.0375 | 4.0383 | 0.0008
GEN-2019-030 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 7.016 | 7.0187 | 0.0027
GEN-2019-030 | 03 CENTRAL | 531423 | GARDNCY2 | 69 | 3.7447 | 3.7451 | 0.0004
GEN-2019-030 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.9265 | 12.9343 | 0.0078
GEN-2019-030 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2958 | 21.3235 | 0.0277
GEN-2019-030 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.7834 | 9.8296 | 0.0462
GEN-2019-030 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.2125 | 6.2185 | 0.006
GEN-2019-030 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.5466 | 10.5561 | 0.0095
GEN-2019-030 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.9904 | 7.0058 | 0.0154
GEN-2019-030 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.3612 | 13.7673 | 0.4061
GEN-2019-030 | 03 CENTRAL | 531492 | OG ONEOK | 115 | 2.1624 | 2.1631 | 0.0007
GEN-2019-030 | 03 CENTRAL | 531497 | TURKEYR3 | 115 | 1.8102 | 1.8107 | 0.0005
GEN-2019-030 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2871 | 9.3873 | 0.1002
GEN-2019-030 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4026 | 7.4662 | 0.0636
GEN-2019-030 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5257 | 7.5902 | 0.0645
GEN-2019-030 | 03 CENTRAL | 531632 | GEN-2015-065 | 345 | 5.5055 | 5.5101 | 0.0046
GEN-2019-030 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3715 | 11.3782 | 0.0067
GEN-2019-030 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.5125 | 20.5466 | 0.0341
GEN-2019-030 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.1397 | 7.1428 | 0.0031
GEN-2019-030 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9834 | 5.9854 | 0.002
GEN-2019-030 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0081 | 5.0095 | 0.0014
GEN-2019-030 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9157 | 18.9257 | 0.01
GEN-2019-030 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0725 | 7.0737 | 0.0012
GEN-2019-030 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6976 | 5.6983 | 0.0007
GEN-2019-030 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.4973 | 23.5286 | 0.0313
GEN-2019-030 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.154 | 14.1603 | 0.0063
GEN-2019-030 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3209 | 32.3372 | 0.0163
GEN-2019-030 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1273 | 4.1282 | 0.0009
GEN-2019-030 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.1042 | 12.2739 | 0.1697
GEN-2019-030 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.3805 | 10.5039 | 0.1234
GEN-2019-030 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6547 | 3.6586 | 0.0039
GEN-2019-030 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.7693 | 10.7827 | 0.0134
GEN-2019-030 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.039 | 16.0696 | 0.0306
GEN-2019-030 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.742 | 3.7468 | 0.0048
GEN-2019-030 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 7.2232 | 7.2412 | 0.018
GEN-2019-030 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5629 | 2.5643 | 0.0014
GEN-2019-030 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5171 | 7.5202 | 0.0031
GEN-2019-030 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 10.0488 | 10.0837 | 0.0349
GEN-2019-030 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5323 | 8.5413 | 0.009
GEN-2019-030 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3006 | 11.3191 | 0.0185
GEN-2019-030 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1517 | 8.1742 | 0.0225
GEN-2019-030 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.8285 | 4.8365 | 0.008
GEN-2019-030 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.97 | 2.9713 | 0.0013
GEN-2019-030 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0558 | 7.0721 | 0.0163
GEN-2019-030 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.1894 | 10.2399 | 0.0505
GEN-2019-030 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.3997 | 12.5785 | 0.1788
GEN-2019-030 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5039 | 4.5099 | 0.006
GEN-2019-030 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.5866 | 6.6016 | 0.015
GEN-2019-030 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.4324 | 5.4404 | 0.008
GEN-2019-030 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.2006 | 13.3083 | 0.1077
GEN-2019-030 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.5784 | 3.5805 | 0.0021
GEN-2019-030 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.2623 | 4.2656 | 0.0033
GEN-2019-030 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1115 | 10.1468 | 0.0353
GEN-2019-030 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5629 | 2.5643 | 0.0014
GEN-2019-030 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5629 | 2.5643 | 0.0014
GEN-2019-030 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.859 | 4.863 | 0.004
GEN-2019-030 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.5833 | 3.5852 | 0.0019
GEN-2019-030 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.2465 | 13.6265 | 0.38
GEN-2019-030 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6194 | 16.7204 | 0.101
GEN-2019-030 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 12.9292 | 13.303 | 0.3738
GEN-2019-030 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0496 | 18.0903 | 0.0407
GEN-2019-030 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0941 | 11.3567 | 0.2626
GEN-2019-030 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.7509 | 12.0566 | 0.3057
GEN-2019-030 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.3461 | 11.6022 | 0.2561
GEN-2019-030 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.3461 | 11.6022 | 0.2561
GEN-2019-030 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.6709 | 9.8495 | 0.1786
GEN-2019-030 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.8421 | 8.9933 | 0.1512
GEN-2019-030 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3708 | 3.3741 | 0.0033
GEN-2019-030 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 13.5616 | 13.5709 | 0.0093
GEN-2019-030 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.6069 | 11.8928 | 0.2859
GEN-2019-030 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6472 | 6.6537 | 0.0065
GEN-2019-030 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.723 | 10.7263 | 0.0033
GEN-2019-030 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2332 | 5.2338 | 0.0006
GEN-2019-030 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.5139 | 12.863 | 0.3491
GEN-2019-030 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2551 | 7.2566 | 0.0015
GEN-2019-030 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.5424 | 9.5471 | 0.0047
GEN-2019-030 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.0801 | 7.0803 | 0.0002
GEN-2019-030 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.2009 | 10.4173 | 0.2164
GEN-2019-030 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.3525 | 15.4892 | 0.1367
GEN-2019-030 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5257 | 5.5302 | 0.0045
GEN-2019-030 | 03 CENTRAL | 587680 | GEN-2016-074 | 345 | 5.8107 | 5.8114 | 0.0007
GEN-2019-030 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4344 | 7.4358 | 0.0014
GEN-2019-030 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.793 | 7.7945 | 0.0015
GEN-2019-030 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 11.2476 | 11.254 | 0.0064
GEN-2019-030 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6194 | 16.7204 | 0.101
GEN-2019-030 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.4052 | 29.4187 | 0.0135
GEN-2019-030 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.5219 | 6.523 | 0.0011
GEN-2019-030 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4693 | 2.4722 | 0.0029
GEN-2019-030 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.0501 | 9.055 | 0.0049
GEN-2019-030 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 14.3777 | 14.3802 | 0.0025
GEN-2019-030 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.847 | 7.8486 | 0.0016
GEN-2019-030 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 10.1939 | 10.1962 | 0.0023
GEN-2019-030 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.2629 | 10.2641 | 0.0012
GEN-2019-030 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.4074 | 20.4411 | 0.0337
GEN-2019-030 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1502 | 32.1663 | 0.0161
GEN-2019-030 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1526 | 7.1705 | 0.0179
GEN-2019-030 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6566 | 17.6612 | 0.0046
GEN-2019-030 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 16.4235 | 16.4376 | 0.0141
GEN-2019-030 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.1203 | 9.6659 | 0.5456
GEN-2019-030 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.178 | 11.7182 | 0.5402
GEN-2019-030 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7431 | 6.7578 | 0.0147
GEN-2019-030 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 15.5174 | 15.5265 | 0.0091
GEN-2019-030 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6427 | 6.6771 | 0.0344
GEN-2019-030 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7269 | 6.7622 | 0.0353
GEN-2019-030 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3519 | 6.363 | 0.0111
GEN-2019-030 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4288 | 6.4401 | 0.0113
GEN-2019-030 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.9665 | 13.3303 | 0.3638
GEN-2019-035 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 19.7409 | 19.7725 | 0.0316
GEN-2019-035 | 03 CENTRAL | 300658 | 2BILLNG | 69 | 8.4312 | 8.444 | 0.0128
GEN-2019-035 | 03 CENTRAL | 300662 | 2CAPEFR | 69 | 5.6126 | 5.6206 | 0.008
GEN-2019-035 | 03 CENTRAL | 300665 | 2CLEVER | 69 | 4.715 | 4.7185 | 0.0035
GEN-2019-035 | 03 CENTRAL | 300667 | 2CRANE | 69 | 3.3442 | 3.3461 | 0.0019
GEN-2019-035 | 03 CENTRAL | 300670 | 2EPURDY | 69 | 3.6324 | 3.6346 | 0.0022
GEN-2019-035 | 03 CENTRAL | 300677 | 2MTVRN | 69 | 9.0884 | 9.1077 | 0.0193
GEN-2019-035 | 03 CENTRAL | 300678 | 5NIXA-1 | 161 | 19.4432 | 19.4693 | 0.0261
GEN-2019-035 | 03 CENTRAL | 300679 | 2PRDYTP | 69 | 5.1682 | 5.1726 | 0.0044
GEN-2019-035 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.586 | 6.5947 | 0.0087
GEN-2019-035 | 03 CENTRAL | 300683 | 2MIDWY | 69 | 4.7805 | 4.7858 | 0.0053
GEN-2019-035 | 03 CENTRAL | 300684 | 2MIDWYTP | 69 | 8.903 | 8.9214 | 0.0184
GEN-2019-035 | 03 CENTRAL | 300713 | 2BEARCK | 69 | 5.0552 | 5.0624 | 0.0072
GEN-2019-035 | 03 CENTRAL | 300714 | 2BLUWTP | 69 | 7.9747 | 7.9933 | 0.0186
GEN-2019-035 | 03 CENTRAL | 300715 | 2BLUWTR | 69 | 5.3987 | 5.4073 | 0.0086
GEN-2019-035 | 03 CENTRAL | 300720 | 2GRTNA | 69 | 5.6685 | 5.6787 | 0.0102
GEN-2019-035 | 03 CENTRAL | 300721 | 2KMBRLNTP | 69 | 7.179 | 7.1941 | 0.0151
GEN-2019-035 | 03 CENTRAL | 300722 | 2LAKE-K | 69 | 10.4465 | 10.4784 | 0.0319
GEN-2019-035 | 03 CENTRAL | 300725 | 2REEDSP | 69 | 10.3596 | 10.4001 | 0.0405
GEN-2019-035 | 03 CENTRAL | 300730 | 2SILDOL | 69 | 9.3562 | 9.3775 | 0.0213
GEN-2019-035 | 03 CENTRAL | 300733 | 2STONBR | 69 | 7.4615 | 7.4778 | 0.0163
GEN-2019-035 | 03 CENTRAL | 300734 | 2STULTS | 69 | 6.2251 | 6.233 | 0.0079
GEN-2019-035 | 03 CENTRAL | 300782 | 2MORGAN | 69 | 7.1197 | 7.1211 | 0.0014
GEN-2019-035 | 03 CENTRAL | 301521 | 5REEDSP | 161 | 8.5063 | 8.6427 | 0.1364
GEN-2019-035 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 19.7396 | 19.7712 | 0.0316
GEN-2019-035 | 03 CENTRAL | 301625 | 2KMBRLN | 69 | 6.4392 | 6.4514 | 0.0122
GEN-2019-035 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 8.3496 | 8.3546 | 0.005
GEN-2019-035 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.8757 | 15.8912 | 0.0155
GEN-2019-035 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.8231 | 16.8434 | 0.0203
GEN-2019-035 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 14.0753 | 14.082 | 0.0067
GEN-2019-035 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 27.4975 | 27.5434 | 0.0459
GEN-2019-035 | 03 CENTRAL | 505494 | SPRGFLD2 | 69 | 16.202 | 16.2088 | 0.0068
GEN-2019-035 | 03 CENTRAL | 505496 | NIXA 5 | 161 | 12.7365 | 12.7517 | 0.0152
GEN-2019-035 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 10.0528 | 10.0565 | 0.0037
GEN-2019-035 | 03 CENTRAL | 547400 | MON376J2 | 69 | 4.1244 | 4.1288 | 0.0044
GEN-2019-035 | 03 CENTRAL | 547401 | MON376 2 | 69 | 6.6881 | 6.6995 | 0.0114
GEN-2019-035 | 03 CENTRAL | 547402 | MON416J2 | 69 | 3.6327 | 3.636 | 0.0033
GEN-2019-035 | 03 CENTRAL | 547403 | MON416 2 | 69 | 3.5383 | 3.5415 | 0.0032
GEN-2019-035 | 03 CENTRAL | 547404 | PUR390 2 | 69 | 1.7989 | 1.7997 | 0.0008
GEN-2019-035 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.9109 | 7.9269 | 0.016
GEN-2019-035 | 03 CENTRAL | 547406 | MON352 2 | 69 | 7.5999 | 7.6147 | 0.0148
GEN-2019-035 | 03 CENTRAL | 547407 | MON311J2 | 69 | 6.7728 | 6.7845 | 0.0117
GEN-2019-035 | 03 CENTRAL | 547408 | MON311 2 | 69 | 6.6881 | 6.6995 | 0.0114
GEN-2019-035 | 03 CENTRAL | 547436 | CUPTAP 2 | 69 | 6.1024 | 6.1039 | 0.0015
GEN-2019-035 | 03 CENTRAL | 547437 | CUPSUB 2 | 69 | 4.9826 | 4.9836 | 0.001
GEN-2019-035 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.7516 | 5.7579 | 0.0063
GEN-2019-035 | 03 CENTRAL | 547459 | WWR477 | 161 | 23.1548 | 23.1713 | 0.0165
GEN-2019-035 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.6516 | 14.6627 | 0.0111
GEN-2019-035 | 03 CENTRAL | 547464 | BOL 73 5 | 161 | 4.9222 | 4.9245 | 0.0023
GEN-2019-035 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 16.5966 | 16.6099 | 0.0133
GEN-2019-035 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.6161 | 10.8055 | 0.1894
GEN-2019-035 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.6295 | 14.6418 | 0.0123
GEN-2019-035 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 18.0091 | 18.0324 | 0.0233
GEN-2019-035 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 7.9122 | 8.0698 | 0.1576
GEN-2019-035 | 03 CENTRAL | 547474 | OZD312 5 | 161 | 9.7927 | 9.8505 | 0.0578
GEN-2019-035 | 03 CENTRAL | 547475 | BRN331 5 | 161 | 9.8273 | 9.9115 | 0.0842
GEN-2019-035 | 03 CENTRAL | 547478 | DAD368 5 | 161 | 18.6501 | 18.6813 | 0.0312
GEN-2019-035 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 15.2026 | 15.237 | 0.0344
GEN-2019-035 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.0639 | 12.1533 | 0.0894
GEN-2019-035 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.6007 | 20.62 | 0.0193
GEN-2019-035 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 12.5044 | 12.5144 | 0.01
GEN-2019-035 | 03 CENTRAL | 547488 | BRN412 5 | 161 | 10.1365 | 10.2309 | 0.0944
GEN-2019-035 | 03 CENTRAL | 547489 | BRN413 5 | 161 | 10.6672 | 10.7378 | 0.0706
GEN-2019-035 | 03 CENTRAL | 547493 | BOL431 5 | 161 | 6.1414 | 6.1448 | 0.0034
GEN-2019-035 | 03 CENTRAL | 547495 | GRT433 5 | 161 | 10.0781 | 10.1555 | 0.0774
GEN-2019-035 | 03 CENTRAL | 547498 | STL439 5 | 161 | 25.3964 | 25.4162 | 0.0198
GEN-2019-035 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.7181 | 8.7772 | 0.0591
GEN-2019-035 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.6611 | 14.6749 | 0.0138
GEN-2019-035 | 03 CENTRAL | 547536 | ASH121 2 | 69 | 7.2687 | 7.2725 | 0.0038
GEN-2019-035 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.5393 | 12.6076 | 0.0683
GEN-2019-035 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.9653 | 10.9979 | 0.0326
GEN-2019-035 | 03 CENTRAL | 547544 | WEN205 2 | 69 | 4.5478 | 4.5506 | 0.0028
GEN-2019-035 | 03 CENTRAL | 547545 | FRP217 2 | 69 | 4.5474 | 4.5483 | 0.0009
GEN-2019-035 | 03 CENTRAL | 547546 | BIL221 2 | 69 | 10.0978 | 10.1133 | 0.0155
GEN-2019-035 | 03 CENTRAL | 547577 | MTV351 2 | 69 | 7.1923 | 7.2054 | 0.0131
GEN-2019-035 | 03 CENTRAL | 547578 | AUR355 2 | 69 | 9.5435 | 9.5797 | 0.0362
GEN-2019-035 | 03 CENTRAL | 547580 | REP359 2 | 69 | 13.3381 | 13.3512 | 0.0131
GEN-2019-035 | 03 CENTRAL | 547585 | DAD368 2 | 69 | 9.8906 | 9.895 | 0.0044
GEN-2019-035 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.6456 | 12.6861 | 0.0405
GEN-2019-035 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.661 | 15.6657 | 0.0047
GEN-2019-035 | 03 CENTRAL | 547593 | JOP391 5 | 161 | 13.7686 | 13.78 | 0.0114
GEN-2019-035 | 03 CENTRAL | 547595 | RNM393 2 | 69 | 19.7781 | 19.7883 | 0.0102
GEN-2019-035 | 03 CENTRAL | 547606 | MTV420 2 | 69 | 7.1186 | 7.132 | 0.0134
GEN-2019-035 | 03 CENTRAL | 547611 | MAR437 2 | 69 | 6.0148 | 6.0256 | 0.0108
GEN-2019-035 | 03 CENTRAL | 547618 | CPK446 2 | 69 | 10.4876 | 10.5141 | 0.0265
GEN-2019-035 | 03 CENTRAL | 547620 | MTV348 2 | 69 | 6.0349 | 6.0441 | 0.0092
GEN-2019-035 | 03 CENTRAL | 549959 | BATTLEFIELD5 | 161 | 26.8428 | 26.886 | 0.0432
GEN-2019-035 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 28.5578 | 28.602 | 0.0442
GEN-2019-035 | 03 CENTRAL | 549970 | CLAY 5 | 161 | 18.8403 | 18.858 | 0.0177
GEN-2019-035 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 6.1751 | 6.1802 | 0.0051
GEN-2019-035 | 03 CENTRAL | 763560 | GEN-2019-016 | 161 | 18.3405 | 18.3706 | 0.0301
GEN-2019-035 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.5343 | 7.8694 | 0.3351
GEN-2019-035 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.5519 | 7.887 | 0.3351
GEN-2019-044 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1028 | 6.1077 | 0.0049
GEN-2019-044 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7034 | 9.7167 | 0.0133
GEN-2019-044 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7248 | 10.7358 | 0.011
GEN-2019-044 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8132 | 8.8211 | 0.0079
GEN-2019-044 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.802 | 7.8128 | 0.0108
GEN-2019-044 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8126 | 10.8238 | 0.0112
GEN-2019-044 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5338 | 3.5348 | 0.001
GEN-2019-044 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1164 | 8.1255 | 0.0091
GEN-2019-044 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.0111 | 8.017 | 0.0059
GEN-2019-044 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7248 | 10.7358 | 0.011
GEN-2019-044 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3129 | 21.3235 | 0.0106
GEN-2019-044 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8159 | 9.8296 | 0.0137
GEN-2019-044 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0012 | 7.0058 | 0.0046
GEN-2019-044 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6704 | 13.7673 | 0.0969
GEN-2019-044 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3618 | 9.3873 | 0.0255
GEN-2019-044 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.45 | 7.4662 | 0.0162
GEN-2019-044 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5738 | 7.5902 | 0.0164
GEN-2019-044 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.1857 | 12.2739 | 0.0882
GEN-2019-044 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.4399 | 10.5039 | 0.064
GEN-2019-044 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.5887 | 3.6586 | 0.0699
GEN-2019-044 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.6617 | 3.7468 | 0.0851
GEN-2019-044 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.9299 | 7.2412 | 0.3113
GEN-2019-044 | 03 CENTRAL | 539646 | KISMET 3 | 115 | 5.4129 | 5.4265 | 0.0136
GEN-2019-044 | 03 CENTRAL | 539652 | CMRIVTP3 | 115 | 6.0605 | 6.0732 | 0.0127
GEN-2019-044 | 03 CENTRAL | 539659 | CUDAHY 3 | 115 | 4.2975 | 4.3303 | 0.0328
GEN-2019-044 | 03 CENTRAL | 539664 | GRNBURG3 | 115 | 3.9598 | 3.9859 | 0.0261
GEN-2019-044 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5388 | 2.5643 | 0.0255
GEN-2019-044 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.4923 | 10.0837 | 0.5914
GEN-2019-044 | 03 CENTRAL | 539673 | MED-LDG3 | 115 | 8.2433 | 8.2526 | 0.0093
GEN-2019-044 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3113 | 11.3191 | 0.0078
GEN-2019-044 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.165 | 8.1742 | 0.0092
GEN-2019-044 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.6957 | 4.8365 | 0.1408
GEN-2019-044 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9707 | 2.9713 | 0.0006
GEN-2019-044 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7884 | 7.0721 | 0.2837
GEN-2019-044 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.0798 | 10.2399 | 0.1601
GEN-2019-044 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.4856 | 12.5785 | 0.0929
GEN-2019-044 | 03 CENTRAL | 539697 | SUNCITY3 | 115 | 4.2068 | 4.2173 | 0.0105
GEN-2019-044 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.4042 | 4.5099 | 0.1057
GEN-2019-044 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.3418 | 6.6016 | 0.2598
GEN-2019-044 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.3148 | 5.4404 | 0.1256
GEN-2019-044 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.1394 | 13.3083 | 0.1689
GEN-2019-044 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.5549 | 3.5805 | 0.0256
GEN-2019-044 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.2266 | 4.2656 | 0.039
GEN-2019-044 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.547 | 10.1468 | 0.5998
GEN-2019-044 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5388 | 2.5643 | 0.0255
GEN-2019-044 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5388 | 2.5643 | 0.0255
GEN-2019-044 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.8037 | 4.863 | 0.0593
GEN-2019-044 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.5571 | 3.5852 | 0.0281
GEN-2019-044 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.575 | 13.6265 | 0.0515
GEN-2019-044 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7006 | 16.7204 | 0.0198
GEN-2019-044 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.2164 | 13.303 | 0.0866
GEN-2019-044 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3213 | 11.3567 | 0.0354
GEN-2019-044 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.9859 | 12.0566 | 0.0707
GEN-2019-044 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.5677 | 11.6022 | 0.0345
GEN-2019-044 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.5677 | 11.6022 | 0.0345
GEN-2019-044 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8256 | 9.8495 | 0.0239
GEN-2019-044 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9731 | 8.9933 | 0.0202
GEN-2019-044 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3146 | 3.3741 | 0.0595
GEN-2019-044 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8445 | 11.8928 | 0.0483
GEN-2019-044 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.652 | 6.6537 | 0.0017
GEN-2019-044 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.7823 | 12.863 | 0.0807
GEN-2019-044 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.3809 | 10.4173 | 0.0364
GEN-2019-044 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4665 | 15.4892 | 0.0227
GEN-2019-044 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.529 | 5.5302 | 0.0012
GEN-2019-044 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7006 | 16.7204 | 0.0198
GEN-2019-044 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4713 | 2.4722 | 0.0009
GEN-2019-044 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.0537 | 9.055 | 0.0013
GEN-2019-044 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.167 | 7.1705 | 0.0035
GEN-2019-044 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6306 | 9.6659 | 0.0353
GEN-2019-044 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.6652 | 11.7182 | 0.053
GEN-2019-044 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.141 | 6.7578 | 0.6168
GEN-2019-044 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6603 | 6.6771 | 0.0168
GEN-2019-044 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.745 | 6.7622 | 0.0172
GEN-2019-044 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3585 | 6.363 | 0.0045
GEN-2019-044 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4356 | 6.4401 | 0.0045
GEN-2019-044 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.2811 | 13.3303 | 0.0492
GEN-2019-048 | 03 CENTRAL | 300091 | 5LATHRP | 161 | 7.3072 | 7.3084 | 0.0012
GEN-2019-048 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.4118 | 19.4286 | 0.0168
GEN-2019-048 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.7989 | 8.8021 | 0.0032
GEN-2019-048 | 03 CENTRAL | 300304 | 2MOCITY | 69 | 9.5339 | 9.5351 | 0.0012
GEN-2019-048 | 03 CENTRAL | 300320 | 5LEVASY | 161 | 10.5527 | 10.5581 | 0.0054
GEN-2019-048 | 03 CENTRAL | 301563 | 5MOCITYB1 | 161 | 19.4356 | 19.4525 | 0.0169
GEN-2019-048 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 14.7883 | 14.7891 | 0.0008
GEN-2019-048 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 28.6191 | 28.6297 | 0.0106
GEN-2019-048 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.7481 | 18.7562 | 0.0081
GEN-2019-048 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.3131 | 21.3284 | 0.0153
GEN-2019-048 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.3347 | 27.3795 | 0.0448
GEN-2019-048 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 34.2982 | 34.3134 | 0.0152
GEN-2019-048 | 03 CENTRAL | 541205 | BLSPE 5 | 161 | 21.2412 | 21.2929 | 0.0517
GEN-2019-048 | 03 CENTRAL | 541206 | PRALEE 5 | 161 | 20.7441 | 20.7686 | 0.0245
GEN-2019-048 | 03 CENTRAL | 541211 | BLSPS 5 | 161 | 19.9333 | 19.968 | 0.0347
GEN-2019-048 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 14.1665 | 14.1725 | 0.006
GEN-2019-048 | 03 CENTRAL | 541219 | RAYTOWN5 | 161 | 13.2101 | 13.2209 | 0.0108
GEN-2019-048 | 03 CENTRAL | 541226 | GRAINVL5 | 161 | 14.047 | 14.0672 | 0.0202
GEN-2019-048 | 03 CENTRAL | 541227 | OAKGRV 5 | 161 | 12.3645 | 12.3791 | 0.0146
GEN-2019-048 | 03 CENTRAL | 541229 | ODESSA 5 | 161 | 9.8923 | 9.8993 | 0.007
GEN-2019-048 | 03 CENTRAL | 541232 | LEX161 5 | 161 | 7.8008 | 7.8049 | 0.0041
GEN-2019-048 | 03 CENTRAL | 541233 | LEESUM 5 | 161 | 20.4506 | 20.4681 | 0.0175
GEN-2019-048 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.7672 | 19.8341 | 0.0669
GEN-2019-048 | 03 CENTRAL | 541236 | RICHMND5 | 161 | 8.0566 | 8.061 | 0.0044
GEN-2019-048 | 03 CENTRAL | 541237 | BLSPW 5 | 161 | 15.5622 | 15.5851 | 0.0229
GEN-2019-048 | 03 CENTRAL | 541238 | LKWOOD 5 | 161 | 13.4527 | 13.4663 | 0.0136
GEN-2019-048 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 14.1067 | 14.12 | 0.0133
GEN-2019-048 | 03 CENTRAL | 541246 | STROTHR5 | 161 | 14.6842 | 14.6929 | 0.0087
GEN-2019-048 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 16.0078 | 16.0138 | 0.006
GEN-2019-048 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.9237 | 28.9792 | 0.0555
GEN-2019-048 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.8781 | 5.8794 | 0.0013
GEN-2019-048 | 03 CENTRAL | 541262 | LIBERTY2 | 69 | 10.0905 | 10.096 | 0.0055
GEN-2019-048 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.8705 | 11.8752 | 0.0047
GEN-2019-048 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.013 | 19.0251 | 0.0121
GEN-2019-048 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.9605 | 7.9613 | 0.0008
GEN-2019-048 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 7.095 | 7.0956 | 0.0006
GEN-2019-048 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.2901 | 23.3078 | 0.0177
GEN-2019-048 | 03 CENTRAL | 543004 | BLUMILS5 | 161 | 17.4329 | 17.465 | 0.0321
GEN-2019-048 | 03 CENTRAL | 543087 | LAKCTYJ2 | 69 | 10.7003 | 10.9523 | 0.252
GEN-2019-048 | 03 CENTRAL | 543088 | BLUSPRG2 | 69 | 8.3776 | 8.6855 | 0.3079
GEN-2019-048 | 03 CENTRAL | 543091 | DUNCNRD2 | 69 | 6.6588 | 7.1836 | 0.5248
GEN-2019-048 | 03 CENTRAL | 543092 | LAKCTY 2 | 69 | 9.2959 | 9.5738 | 0.2779
GEN-2019-048 | 03 CENTRAL | 543093 | LAKCTYK2 | 69 | 7.8236 | 8.1606 | 0.337
GEN-2019-048 | 03 CENTRAL | 543114 | PLUMRRD2 | 69 | 12.6963 | 12.707 | 0.0107
GEN-2019-048 | 03 CENTRAL | 543116 | BLUEMLS2 | 69 | 7.663 | 7.6657 | 0.0027
GEN-2019-048 | 03 CENTRAL | 548806 | BLUVLY | 69 | 23.6696 | 23.875 | 0.2054
GEN-2019-048 | 03 CENTRAL | 548807 | BLUVLY-161 | 161 | 18.4778 | 18.5256 | 0.0478
GEN-2019-048 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.5618 | 25.6048 | 0.043
GEN-2019-048 | 03 CENTRAL | 762669 | GEN-2018-031 | 161 | 18.4757 | 18.5235 | 0.0478
GEN-2019-048 | 03 CENTRAL | 763802 | GEN-2019-048 | 69 | 6.5173 | 7.0432 | 0.5259
GEN-2019-051 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.2156 | 0.002
GEN-2019-051 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.691 | 0.0144
GEN-2019-051 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.7779 | 0.0925
GEN-2019-051 | 03 CENTRAL | 530565 | SEWARD 2 | 69 | 5.4325 | 5.4682 | 0.0357
GEN-2019-051 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.836 | 0.0565
GEN-2019-051 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.6609 | 0.0032
GEN-2019-051 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2628 | 0.0019
GEN-2019-051 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1452 | 0.0015
GEN-2019-051 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.861 | 0.0399
GEN-2019-051 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8555 | 0.0317
GEN-2019-051 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.7456 | 0.0146
GEN-2019-051 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.048 | 0.0444
GEN-2019-051 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.0493 | 0.0309
GEN-2019-051 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.4999 | 0.0026
GEN-2019-051 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.278 | 11.5564 | 0.2784
GEN-2019-051 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.2006 | 0.0224
GEN-2019-051 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6488 | 0.0169
GEN-2019-051 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.0922 | 0.0178
GEN-2019-051 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5235 | 7.6465 | 0.123
GEN-2019-051 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5398 | 0.005
GEN-2019-051 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.3618 | 2.3671 | 0.0053
GEN-2019-051 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.5159 | 1.5181 | 0.0022
GEN-2019-051 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.628 | 1.6305 | 0.0025
GEN-2019-051 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.1728 | 2.1773 | 0.0045
GEN-2019-051 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.0877 | 5.1131 | 0.0254
GEN-2019-051 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0398 | 5.0941 | 0.0543
GEN-2019-051 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.2357 | 0.1102
GEN-2019-051 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1046 | 0.0009
GEN-2019-051 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.5675 | 1.5698 | 0.0023
GEN-2019-051 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0337 | 0.0167
GEN-2019-051 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.3925 | 0.0056
GEN-2019-051 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.5462 | 0.0024
GEN-2019-051 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.6156 | 0.019
GEN-2019-051 | 03 CENTRAL | 539010 | SADLHRN3 | 115 | 4.5214 | 4.5361 | 0.0147
GEN-2019-051 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.2935 | 0.0196
GEN-2019-051 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5181 | 0.0142
GEN-2019-051 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0437 | 0.0137
GEN-2019-051 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.7135 | 0.0104
GEN-2019-051 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.3593 | 0.0054
GEN-2019-051 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2395 | 7.5569 | 0.3174
GEN-2019-051 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0774 | 8.3118 | 0.2344
GEN-2019-051 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3191 | 11.6136 | 0.2945
GEN-2019-051 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.2851 | 0.1109
GEN-2019-051 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3956 | 8.6532 | 0.2576
GEN-2019-051 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 2.9913 | 0.02
GEN-2019-051 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2205 | 7.4969 | 0.2764
GEN-2019-051 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.7389 | 0.0694
GEN-2019-051 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.5992 | 0.0207
GEN-2019-051 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.1131 | 0.0254
GEN-2019-051 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.8446 | 0.0045
GEN-2019-051 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.5536 | 0.0096
GEN-2019-051 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2229 | 7.5403 | 0.3174
GEN-2019-051 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.7004 | 0.0233
GEN-2019-051 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7622 | 6.786 | 0.0238
GEN-2019-051 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.4153 | 0.0524
GEN-2019-051 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.4938 | 0.0537
GEN-2019-053 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1077 | 6.1107 | 0.003
GEN-2019-053 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7167 | 9.7246 | 0.0079
GEN-2019-053 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.215 | 0.0014
GEN-2019-053 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.6864 | 0.0098
GEN-2019-053 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.7604 | 0.0246
GEN-2019-053 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2418 | 2.2423 | 0.0005
GEN-2019-053 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6534 | 10.6649 | 0.0115
GEN-2019-053 | 03 CENTRAL | 530562 | HAYS 3 | 115 | 7.901 | 7.9085 | 0.0075
GEN-2019-053 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.6991 | 0.0137
GEN-2019-053 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.7878 | 0.0083
GEN-2019-053 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.6582 | 0.0005
GEN-2019-053 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2612 | 0.0003
GEN-2019-053 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1439 | 0.0002
GEN-2019-053 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.8471 | 0.026
GEN-2019-053 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8289 | 0.0161
GEN-2019-053 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8489 | 0.0251
GEN-2019-053 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.7333 | 0.0023
GEN-2019-053 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.0101 | 0.0065
GEN-2019-053 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.0229 | 0.0045
GEN-2019-053 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.4977 | 0.0004
GEN-2019-053 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.2841 | 6.2864 | 0.0023
GEN-2019-053 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.5259 | 5.5277 | 0.0018
GEN-2019-053 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.796 | 5.798 | 0.002
GEN-2019-053 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.278 | 11.3208 | 0.0428
GEN-2019-053 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.1819 | 0.0037
GEN-2019-053 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6347 | 0.0028
GEN-2019-053 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.0774 | 0.003
GEN-2019-053 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5235 | 7.5425 | 0.019
GEN-2019-053 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5381 | 0.0033
GEN-2019-053 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.673 | 6.6752 | 0.0022
GEN-2019-053 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0796 | 10.0898 | 0.0102
GEN-2019-053 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6543 | 2.655 | 0.0007
GEN-2019-053 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0398 | 5.0454 | 0.0056
GEN-2019-053 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.1828 | 0.0573
GEN-2019-053 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1043 | 0.0006
GEN-2019-053 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.2442 | 4.2459 | 0.0017
GEN-2019-053 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.8601 | 2.8607 | 0.0006
GEN-2019-053 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.6795 | 8.6885 | 0.009
GEN-2019-053 | 03 CENTRAL | 530694 | VINE2 3 | 115 | 7.9902 | 7.9979 | 0.0077
GEN-2019-053 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.627 | 8.636 | 0.009
GEN-2019-053 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0302 | 0.0132
GEN-2019-053 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.3907 | 0.0038
GEN-2019-053 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.286 | 4.287 | 0.001
GEN-2019-053 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.7604 | 0.0246
GEN-2019-053 | 03 CENTRAL | 530721 | VINEDE_N | 115 | 7.9902 | 7.9979 | 0.0077
GEN-2019-053 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.9902 | 7.9979 | 0.0077
GEN-2019-053 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.5455 | 0.0017
GEN-2019-053 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3235 | 21.3287 | 0.0052
GEN-2019-053 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8296 | 9.8377 | 0.0081
GEN-2019-053 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0058 | 7.0089 | 0.0031
GEN-2019-053 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.8325 | 0.0652
GEN-2019-053 | 03 CENTRAL | 531492 | OG ONEOK | 115 | 2.1631 | 2.1635 | 0.0004
GEN-2019-053 | 03 CENTRAL | 531497 | TURKEYR3 | 115 | 1.8107 | 1.811 | 0.0003
GEN-2019-053 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.4036 | 0.0163
GEN-2019-053 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4765 | 0.0103
GEN-2019-053 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.6007 | 0.0105
GEN-2019-053 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.6049 | 0.0083
GEN-2019-053 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.9396 | 7.9438 | 0.0042
GEN-2019-053 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2675 | 13.2721 | 0.0046
GEN-2019-053 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.8197 | 9.8231 | 0.0034
GEN-2019-053 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.007 | 10.0105 | 0.0035
GEN-2019-053 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8145 | 18.8251 | 0.0106
GEN-2019-053 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7641 | 0.0104
GEN-2019-053 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.5521 | 11.5561 | 0.004
GEN-2019-053 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.6217 | 17.6309 | 0.0092
GEN-2019-053 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.3044 | 18.3145 | 0.0101
GEN-2019-053 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.3804 | 0.1065
GEN-2019-053 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5038 | 10.581 | 0.0772
GEN-2019-053 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6599 | 0.0013
GEN-2019-053 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.7468 | 3.7483 | 0.0015
GEN-2019-053 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0325 | 0.0025
GEN-2019-053 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.7051 | 0.002
GEN-2019-053 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 7.2412 | 7.247 | 0.0058
GEN-2019-053 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.355 | 0.0011
GEN-2019-053 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2396 | 7.2563 | 0.0167
GEN-2019-053 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0774 | 8.0973 | 0.0199
GEN-2019-053 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5647 | 0.0004
GEN-2019-053 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 10.0837 | 10.0949 | 0.0112
GEN-2019-053 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3191 | 11.3621 | 0.043
GEN-2019-053 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.2322 | 0.058
GEN-2019-053 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.8365 | 4.839 | 0.0025
GEN-2019-053 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3956 | 8.4188 | 0.0232
GEN-2019-053 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 2.9742 | 0.0029
GEN-2019-053 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0774 | 0.0053
GEN-2019-053 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2205 | 7.2369 | 0.0164
GEN-2019-053 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.6765 | 0.007
GEN-2019-053 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.2661 | 0.0262
GEN-2019-053 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6908 | 0.1123
GEN-2019-053 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.0908 | 0.0031
GEN-2019-053 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.841 | 0.0009
GEN-2019-053 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5118 | 0.0019
GEN-2019-053 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.5457 | 0.0017
GEN-2019-053 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.6016 | 6.6064 | 0.0048
GEN-2019-053 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.4404 | 5.443 | 0.0026
GEN-2019-053 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3082 | 13.3282 | 0.02
GEN-2019-053 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.5805 | 3.5812 | 0.0007
GEN-2019-053 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.2656 | 4.2665 | 0.0009
GEN-2019-053 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1582 | 0.0114
GEN-2019-053 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5647 | 0.0004
GEN-2019-053 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5647 | 0.0004
GEN-2019-053 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.863 | 4.8642 | 0.0012
GEN-2019-053 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.5852 | 3.5858 | 0.0006
GEN-2019-053 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6264 | 13.6602 | 0.0338
GEN-2019-053 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7204 | 16.7319 | 0.0115
GEN-2019-053 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.361 | 0.058
GEN-2019-053 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3567 | 11.3799 | 0.0232
GEN-2019-053 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.1038 | 0.0473
GEN-2019-053 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6022 | 11.6248 | 0.0226
GEN-2019-053 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6022 | 11.6248 | 0.0226
GEN-2019-053 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8495 | 9.8652 | 0.0157
GEN-2019-053 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9933 | 9.0066 | 0.0133
GEN-2019-053 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3752 | 0.0011
GEN-2019-053 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8928 | 11.9247 | 0.0319
GEN-2019-053 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.6562 | 0.0025
GEN-2019-053 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.9171 | 0.0541
GEN-2019-053 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4173 | 10.4414 | 0.0241
GEN-2019-053 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4892 | 15.5042 | 0.015
GEN-2019-053 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5319 | 0.0017
GEN-2019-053 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7204 | 16.7319 | 0.0115
GEN-2019-053 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4722 | 2.4727 | 0.0005
GEN-2019-053 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.055 | 9.0569 | 0.0019
GEN-2019-053 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1705 | 7.1725 | 0.002
GEN-2019-053 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2229 | 7.2395 | 0.0166
GEN-2019-053 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.6894 | 0.0235
GEN-2019-053 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.7534 | 0.0352
GEN-2019-053 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7625 | 0.0047
GEN-2019-053 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.8689 | 0.1918
GEN-2019-053 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7621 | 6.9539 | 0.1918
GEN-2019-053 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.39 | 0.0271
GEN-2019-053 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.4678 | 0.0277
GEN-2019-053 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3303 | 13.3626 | 0.0323
GEN-2019-054 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.2199 | 0.0063
GEN-2019-054 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.7222 | 0.0456
GEN-2019-054 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.8362 | 0.1004
GEN-2019-054 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2418 | 2.244 | 0.0022
GEN-2019-054 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6534 | 10.7039 | 0.0505
GEN-2019-054 | 03 CENTRAL | 530562 | HAYS 3 | 115 | 7.901 | 7.9358 | 0.0348
GEN-2019-054 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.7705 | 0.0851
GEN-2019-054 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.8305 | 0.051
GEN-2019-054 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.6607 | 0.003
GEN-2019-054 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2626 | 0.0017
GEN-2019-054 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1451 | 0.0014
GEN-2019-054 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.9514 | 0.1303
GEN-2019-054 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8604 | 0.0476
GEN-2019-054 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.9261 | 0.1023
GEN-2019-054 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.7446 | 0.0136
GEN-2019-054 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.0436 | 0.04
GEN-2019-054 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.0463 | 0.0279
GEN-2019-054 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.4997 | 0.0024
GEN-2019-054 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.2841 | 6.2972 | 0.0131
GEN-2019-054 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.5259 | 5.5358 | 0.0099
GEN-2019-054 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.796 | 5.8071 | 0.0111
GEN-2019-054 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.2779 | 11.548 | 0.2701
GEN-2019-054 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.2001 | 0.0219
GEN-2019-054 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6484 | 0.0165
GEN-2019-054 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.0919 | 0.0175
GEN-2019-054 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5234 | 7.6428 | 0.1194
GEN-2019-054 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5511 | 0.0163
GEN-2019-054 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.3618 | 2.3658 | 0.004
GEN-2019-054 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.1026 | 4.1113 | 0.0087
GEN-2019-054 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.5159 | 1.5176 | 0.0017
GEN-2019-054 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.5459 | 5.5597 | 0.0138
GEN-2019-054 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.628 | 1.6299 | 0.0019
GEN-2019-054 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.1728 | 2.1762 | 0.0034
GEN-2019-054 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.673 | 6.6976 | 0.0246
GEN-2019-054 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.0877 | 5.1069 | 0.0192
GEN-2019-054 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0796 | 10.1245 | 0.0449
GEN-2019-054 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6543 | 2.6574 | 0.0031
GEN-2019-054 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0398 | 5.0744 | 0.0346
GEN-2019-054 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.4946 | 0.3691
GEN-2019-054 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 5.0855 | 5.1011 | 0.0156
GEN-2019-054 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1064 | 0.0027
GEN-2019-054 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.5675 | 1.5692 | 0.0017
GEN-2019-054 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.2442 | 4.2648 | 0.0206
GEN-2019-054 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.8601 | 2.8678 | 0.0077
GEN-2019-054 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.6795 | 8.7207 | 0.0412
GEN-2019-054 | 03 CENTRAL | 530694 | VINE2 3 | 115 | 7.9902 | 8.0259 | 0.0357
GEN-2019-054 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.627 | 8.6686 | 0.0416
GEN-2019-054 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0706 | 0.0536
GEN-2019-054 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.521 | 4.53 | 0.009
GEN-2019-054 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.4046 | 0.0177
GEN-2019-054 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.286 | 4.2962 | 0.0102
GEN-2019-054 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.8362 | 0.1004
GEN-2019-054 | 03 CENTRAL | 530721 | VINEDE_N | 115 | 7.9902 | 8.0259 | 0.0357
GEN-2019-054 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.9902 | 8.0259 | 0.0357
GEN-2019-054 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.5515 | 0.0077
GEN-2019-054 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.8229 | 0.0556
GEN-2019-054 | 03 CENTRAL | 531492 | OG ONEOK | 115 | 2.1631 | 2.1652 | 0.0021
GEN-2019-054 | 03 CENTRAL | 531497 | TURKEYR3 | 115 | 1.8107 | 1.8121 | 0.0014
GEN-2019-054 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.4025 | 0.0152
GEN-2019-054 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4758 | 0.0096
GEN-2019-054 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.5999 | 0.0097
GEN-2019-054 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.2398 | 10.2473 | 0.0075
GEN-2019-054 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3782 | 11.4092 | 0.031
GEN-2019-054 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.1014 | 11.1242 | 0.0228
GEN-2019-054 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5286 | 23.5543 | 0.0257
GEN-2019-054 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0092 | 14.014 | 0.0048
GEN-2019-054 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.707 | 0.1104
GEN-2019-054 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.9396 | 7.9878 | 0.0482
GEN-2019-054 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2675 | 13.3079 | 0.0404
GEN-2019-054 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.2495 | 8.256 | 0.0065
GEN-2019-054 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.8827 | 4.8846 | 0.0019
GEN-2019-054 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1169 | 7.1203 | 0.0034
GEN-2019-054 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8762 | 3.8769 | 0.0007
GEN-2019-054 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4554 | 3.456 | 0.0006
GEN-2019-054 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6599 | 2.6603 | 0.0004
GEN-2019-054 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.1793 | 12.1937 | 0.0144
GEN-2019-054 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.53 | 12.5494 | 0.0194
GEN-2019-054 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.5098 | 10.5231 | 0.0133
GEN-2019-054 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9711 | 3.972 | 0.0009
GEN-2019-054 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 17.774 | 17.8098 | 0.0358
GEN-2019-054 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.2245 | 7.2351 | 0.0106
GEN-2019-054 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.8197 | 9.8545 | 0.0348
GEN-2019-054 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.007 | 10.0432 | 0.0362
GEN-2019-054 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8145 | 18.9331 | 0.1186
GEN-2019-054 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.1684 | 8.1874 | 0.019
GEN-2019-054 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3587 | 8.3766 | 0.0179
GEN-2019-054 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.8615 | 0.1078
GEN-2019-054 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.5521 | 11.5973 | 0.0452
GEN-2019-054 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.6216 | 17.7251 | 0.1035
GEN-2019-054 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.3044 | 18.4167 | 0.1123
GEN-2019-054 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.6109 | 8.635 | 0.0241
GEN-2019-054 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.69 | 10.7269 | 0.0369
GEN-2019-054 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.8689 | 10.906 | 0.0371
GEN-2019-054 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7766 | 8.7835 | 0.0069
GEN-2019-054 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7762 | 6.7803 | 0.0041
GEN-2019-054 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.2517 | 11.2907 | 0.039
GEN-2019-054 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.9943 | 7.0112 | 0.0169
GEN-2019-054 | 03 CENTRAL | 533440 | 43LORAN | 115 | 12.706 | 12.7578 | 0.0518
GEN-2019-054 | 03 CENTRAL | 533455 | TWR 33 3 | 115 | 10.5484 | 10.5828 | 0.0344
GEN-2019-054 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 5.0305 | 5.0355 | 0.005
GEN-2019-054 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 5.1075 | 5.1127 | 0.0052
GEN-2019-054 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0333 | 4.0361 | 0.0028
GEN-2019-054 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.0601 | 4.0629 | 0.0028
GEN-2019-054 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.4853 | 7.4944 | 0.0091
GEN-2019-054 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 5.2371 | 5.2426 | 0.0055
GEN-2019-054 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 6.0462 | 6.0535 | 0.0073
GEN-2019-054 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.6376 | 5.644 | 0.0064
GEN-2019-054 | 03 CENTRAL | 533513 | HEC 2 | 69 | 8.2014 | 8.2148 | 0.0134
GEN-2019-054 | 03 CENTRAL | 533514 | HEC GT 2 | 69 | 7.9855 | 7.9982 | 0.0127
GEN-2019-054 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3446 | 6.3511 | 0.0065
GEN-2019-054 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1504 | 6.1565 | 0.0061
GEN-2019-054 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.4999 | 6.5083 | 0.0084
GEN-2019-054 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.82 | 5.8267 | 0.0067
GEN-2019-054 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.298 | 5.3036 | 0.0056
GEN-2019-054 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5241 | 6.531 | 0.0069
GEN-2019-054 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.3342 | 0.0603
GEN-2019-054 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5475 | 0.0436
GEN-2019-054 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6595 | 0.0009
GEN-2019-054 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0471 | 0.0171
GEN-2019-054 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.7168 | 0.0137
GEN-2019-054 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.3631 | 0.0092
GEN-2019-054 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2396 | 7.3442 | 0.1046
GEN-2019-054 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.58 | 3.5894 | 0.0094
GEN-2019-054 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0774 | 8.2021 | 0.1247
GEN-2019-054 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5646 | 0.0003
GEN-2019-054 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3191 | 11.5904 | 0.2713
GEN-2019-054 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1741 | 8.5482 | 0.3741
GEN-2019-054 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3956 | 8.5412 | 0.1456
GEN-2019-054 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 2.9899 | 0.0186
GEN-2019-054 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.076 | 0.0039
GEN-2019-054 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2205 | 7.3234 | 0.1029
GEN-2019-054 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.7129 | 0.0434
GEN-2019-054 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.2558 | 0.0159
GEN-2019-054 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6421 | 0.0636
GEN-2019-054 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.1069 | 0.0192
GEN-2019-054 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.846 | 0.0059
GEN-2019-054 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5113 | 0.0014
GEN-2019-054 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.5561 | 0.0121
GEN-2019-054 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3082 | 13.3247 | 0.0165
GEN-2019-054 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1552 | 0.0084
GEN-2019-054 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5646 | 0.0003
GEN-2019-054 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5646 | 0.0003
GEN-2019-054 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.3527 | 0.0497
GEN-2019-054 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.0971 | 0.0406
GEN-2019-054 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3749 | 0.0008
GEN-2019-054 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.661 | 0.0073
GEN-2019-054 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.9094 | 0.0464
GEN-2019-054 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5353 | 0.0051
GEN-2019-054 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.735 | 6.7439 | 0.0089
GEN-2019-054 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0508 | 10.0721 | 0.0213
GEN-2019-054 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 5.9129 | 5.9176 | 0.0047
GEN-2019-054 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 6.5202 | 6.5259 | 0.0057
GEN-2019-054 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2229 | 7.3271 | 0.1042
GEN-2019-054 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.6867 | 0.0208
GEN-2019-054 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.7493 | 0.0311
GEN-2019-054 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7612 | 0.0034
GEN-2019-054 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.7522 | 0.0751
GEN-2019-054 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7621 | 6.8393 | 0.0772
GEN-2019-054 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.867 | 0.5041
GEN-2019-054 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.9436 | 0.5035
GEN-2019-055 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1077 | 6.115 | 0.0073
GEN-2019-055 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7167 | 9.7362 | 0.0195
GEN-2019-055 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.2169 | 0.0033
GEN-2019-055 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.7009 | 0.0243
GEN-2019-055 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.797 | 0.0612
GEN-2019-055 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2418 | 2.243 | 0.0012
GEN-2019-055 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6534 | 10.6821 | 0.0287
GEN-2019-055 | 03 CENTRAL | 530562 | HAYS 3 | 115 | 7.901 | 7.9198 | 0.0188
GEN-2019-055 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.7196 | 0.0342
GEN-2019-055 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.8 | 0.0205
GEN-2019-055 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.6589 | 0.0012
GEN-2019-055 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2616 | 0.0007
GEN-2019-055 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1442 | 0.0005
GEN-2019-055 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.8859 | 0.0648
GEN-2019-055 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8527 | 0.0399
GEN-2019-055 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8862 | 0.0624
GEN-2019-055 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.7365 | 0.0055
GEN-2019-055 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.0196 | 0.016
GEN-2019-055 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.0296 | 0.0112
GEN-2019-055 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.4982 | 0.0009
GEN-2019-055 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.2841 | 6.2899 | 0.0058
GEN-2019-055 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.5259 | 5.5303 | 0.0044
GEN-2019-055 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.796 | 5.801 | 0.005
GEN-2019-055 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.278 | 11.3849 | 0.1069
GEN-2019-055 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.1874 | 0.0092
GEN-2019-055 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6389 | 0.007
GEN-2019-055 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.0819 | 0.0075
GEN-2019-055 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5235 | 7.5709 | 0.0474
GEN-2019-055 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5429 | 0.0081
GEN-2019-055 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.673 | 6.6786 | 0.0056
GEN-2019-055 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0796 | 10.105 | 0.0254
GEN-2019-055 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6543 | 2.6561 | 0.0018
GEN-2019-055 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0398 | 5.0536 | 0.0138
GEN-2019-055 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.2692 | 0.1437
GEN-2019-055 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1052 | 0.0015
GEN-2019-055 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.2442 | 4.2485 | 0.0043
GEN-2019-055 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.8601 | 2.8617 | 0.0016
GEN-2019-055 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.6795 | 8.7019 | 0.0224
GEN-2019-055 | 03 CENTRAL | 530694 | VINE2 3 | 115 | 7.9902 | 8.0094 | 0.0192
GEN-2019-055 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.627 | 8.6494 | 0.0224
GEN-2019-055 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0497 | 0.0327
GEN-2019-055 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.3963 | 0.0094
GEN-2019-055 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.286 | 4.2884 | 0.0024
GEN-2019-055 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.797 | 0.0612
GEN-2019-055 | 03 CENTRAL | 530721 | VINEDE_N | 115 | 7.9902 | 8.0094 | 0.0192
GEN-2019-055 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.9902 | 8.0094 | 0.0192
GEN-2019-055 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.5479 | 0.0041
GEN-2019-055 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3235 | 21.3363 | 0.0128
GEN-2019-055 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8296 | 9.8498 | 0.0202
GEN-2019-055 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0058 | 7.0135 | 0.0077
GEN-2019-055 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.93 | 0.1627
GEN-2019-055 | 03 CENTRAL | 531492 | OG ONEOK | 115 | 2.1631 | 2.1643 | 0.0012
GEN-2019-055 | 03 CENTRAL | 531497 | TURKEYR3 | 115 | 1.8107 | 1.8115 | 0.0008
GEN-2019-055 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.428 | 0.0407
GEN-2019-055 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4919 | 0.0257
GEN-2019-055 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.6162 | 0.026
GEN-2019-055 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.6172 | 0.0206
GEN-2019-055 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.9396 | 7.9498 | 0.0102
GEN-2019-055 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2675 | 13.279 | 0.0115
GEN-2019-055 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.8197 | 9.8281 | 0.0084
GEN-2019-055 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.007 | 10.0157 | 0.0087
GEN-2019-055 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8145 | 18.8409 | 0.0264
GEN-2019-055 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7796 | 0.0259
GEN-2019-055 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.5521 | 11.562 | 0.0099
GEN-2019-055 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.6216 | 17.6447 | 0.0231
GEN-2019-055 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.3044 | 18.3294 | 0.025
GEN-2019-055 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.5414 | 0.2675
GEN-2019-055 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5038 | 10.6971 | 0.1933
GEN-2019-055 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6618 | 0.0032
GEN-2019-055 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.7468 | 3.7506 | 0.0038
GEN-2019-055 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0361 | 0.0061
GEN-2019-055 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.7079 | 0.0048
GEN-2019-055 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 7.2412 | 7.2556 | 0.0144
GEN-2019-055 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.3567 | 0.0028
GEN-2019-055 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2396 | 7.2812 | 0.0416
GEN-2019-055 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0774 | 8.127 | 0.0496
GEN-2019-055 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5654 | 0.0011
GEN-2019-055 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 10.0837 | 10.1115 | 0.0278
GEN-2019-055 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3191 | 11.4264 | 0.1073
GEN-2019-055 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.3197 | 0.1455
GEN-2019-055 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.8365 | 4.8428 | 0.0063
GEN-2019-055 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3956 | 8.4533 | 0.0577
GEN-2019-055 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 2.9787 | 0.0074
GEN-2019-055 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0852 | 0.0131
GEN-2019-055 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2205 | 7.2614 | 0.0409
GEN-2019-055 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.6869 | 0.0174
GEN-2019-055 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.3052 | 0.0653
GEN-2019-055 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.8607 | 0.2822
GEN-2019-055 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.0955 | 0.0078
GEN-2019-055 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.8423 | 0.0022
GEN-2019-055 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5146 | 0.0047
GEN-2019-055 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.5484 | 0.0044
GEN-2019-055 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.6016 | 6.6135 | 0.0119
GEN-2019-055 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.4404 | 5.4467 | 0.0063
GEN-2019-055 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3082 | 13.358 | 0.0498
GEN-2019-055 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.5805 | 3.5821 | 0.0016
GEN-2019-055 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.2656 | 4.268 | 0.0024
GEN-2019-055 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1751 | 0.0283
GEN-2019-055 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5654 | 0.0011
GEN-2019-055 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5654 | 0.0011
GEN-2019-055 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.863 | 4.866 | 0.003
GEN-2019-055 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.5852 | 3.5866 | 0.0014
GEN-2019-055 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6264 | 13.7105 | 0.0841
GEN-2019-055 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7204 | 16.7489 | 0.0285
GEN-2019-055 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.4478 | 0.1448
GEN-2019-055 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3567 | 11.4144 | 0.0577
GEN-2019-055 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.1745 | 0.118
GEN-2019-055 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6022 | 11.6585 | 0.0563
GEN-2019-055 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6022 | 11.6585 | 0.0563
GEN-2019-055 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8495 | 9.8886 | 0.0391
GEN-2019-055 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9933 | 9.0263 | 0.033
GEN-2019-055 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3768 | 0.0027
GEN-2019-055 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8928 | 11.9723 | 0.0795
GEN-2019-055 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.6599 | 0.0062
GEN-2019-055 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.9981 | 0.1351
GEN-2019-055 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4173 | 10.4773 | 0.06
GEN-2019-055 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4892 | 15.5264 | 0.0372
GEN-2019-055 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5345 | 0.0043
GEN-2019-055 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7204 | 16.7489 | 0.0285
GEN-2019-055 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4722 | 2.4735 | 0.0013
GEN-2019-055 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.055 | 9.0597 | 0.0047
GEN-2019-055 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1705 | 7.1755 | 0.005
GEN-2019-055 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2229 | 7.2643 | 0.0414
GEN-2019-055 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.7243 | 0.0584
GEN-2019-055 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.8059 | 0.0877
GEN-2019-055 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7694 | 0.0116
GEN-2019-055 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.677 | 7.1743 | 0.4973
GEN-2019-055 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7621 | 7.2588 | 0.4967
GEN-2019-055 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.4305 | 0.0676
GEN-2019-055 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.5093 | 0.0692
GEN-2019-055 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3303 | 13.4107 | 0.0804
GEN-2019-058 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.2738 | 10.2747 | 0.0009
GEN-2019-058 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.3418 | 13.3429 | 0.0011
GEN-2019-058 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1492 | 5.1493 | 0.0001
GEN-2019-058 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.0808 | 9.0815 | 0.0007
GEN-2019-058 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.0357 | 10.0381 | 0.0024
GEN-2019-058 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.5439 | 7.5443 | 0.0004
GEN-2019-058 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2241 | 3.2242 | 0.0001
GEN-2019-058 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 18.5114 | 18.5242 | 0.0128
GEN-2019-058 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 23.9995 | 24.0059 | 0.0064
GEN-2019-058 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.1319 | 9.1327 | 0.0008
GEN-2019-058 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.6986 | 9.6996 | 0.001
GEN-2019-058 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 16.7031 | 16.7074 | 0.0043
GEN-2019-058 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.6938 | 17.6969 | 0.0031
GEN-2019-058 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 11.9181 | 11.9202 | 0.0021
GEN-2019-058 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.4731 | 7.4736 | 0.0005
GEN-2019-058 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 30.2867 | 30.2898 | 0.0031
GEN-2019-058 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.5022 | 8.5032 | 0.001
GEN-2019-058 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.197 | 13.1997 | 0.0027
GEN-2019-058 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 10.9472 | 10.9507 | 0.0035
GEN-2019-058 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 10.0304 | 10.0333 | 0.0029
GEN-2019-058 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5721 | 19.5733 | 0.0012
GEN-2019-058 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 6.4051 | 6.4052 | 0.0001
GEN-2019-058 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.5753 | 8.578 | 0.0027
GEN-2019-058 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.459 | 14.4833 | 0.0243
GEN-2019-058 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 15.5265 | 15.5333 | 0.0068
GEN-2019-058 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.361 | 10.365 | 0.004
GEN-2019-058 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.6894 | 11.6945 | 0.0051
GEN-2019-058 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.5315 | 9.5346 | 0.0031
GEN-2019-058 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.5209 | 9.524 | 0.0031
GEN-2019-058 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.2005 | 8.2006 | 0.0001
GEN-2019-058 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.1025 | 10.1049 | 0.0024
GEN-2019-058 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.7335 | 11.7372 | 0.0037
GEN-2019-058 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3423 | 19.3435 | 0.0012
GEN-2019-058 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.8534 | 6.8535 | 0.0001
GEN-2019-058 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.8039 | 6.8052 | 0.0013
GEN-2019-058 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.9803 | 7.9805 | 0.0002
GEN-2019-058 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.8699 | 8.8701 | 0.0002
GEN-2019-058 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.009 | 20.0102 | 0.0012
GEN-2019-058 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1077 | 6.1143 | 0.0066
GEN-2019-058 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7167 | 9.7345 | 0.0178
GEN-2019-058 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.7512 | 0.0154
GEN-2019-058 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.831 | 0.0099
GEN-2019-058 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.829 | 0.0162
GEN-2019-058 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8395 | 0.0157
GEN-2019-058 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.536 | 0.0012
GEN-2019-058 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0252 | 0.0082
GEN-2019-058 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.7512 | 0.0154
GEN-2019-058 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3235 | 21.3346 | 0.0111
GEN-2019-058 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8296 | 9.848 | 0.0184
GEN-2019-058 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0058 | 7.0119 | 0.0061
GEN-2019-058 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.9316 | 0.1643
GEN-2019-058 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.427 | 0.0397
GEN-2019-058 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4913 | 0.0251
GEN-2019-058 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.6156 | 0.0254
GEN-2019-058 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5253 | 16.5263 | 0.001
GEN-2019-058 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3782 | 11.3822 | 0.004
GEN-2019-058 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8481 | 13.8488 | 0.0007
GEN-2019-058 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.5466 | 20.572 | 0.0254
GEN-2019-058 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.1428 | 7.1451 | 0.0023
GEN-2019-058 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9854 | 5.987 | 0.0016
GEN-2019-058 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0095 | 5.0105 | 0.001
GEN-2019-058 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9257 | 18.9329 | 0.0072
GEN-2019-058 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0737 | 7.0745 | 0.0008
GEN-2019-058 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.5534 | 18.5577 | 0.0043
GEN-2019-058 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6983 | 5.6988 | 0.0005
GEN-2019-058 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5286 | 23.5514 | 0.0228
GEN-2019-058 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0612 | 18.062 | 0.0008
GEN-2019-058 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1603 | 14.1648 | 0.0045
GEN-2019-058 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.2792 | 28.2854 | 0.0062
GEN-2019-058 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3372 | 32.349 | 0.0118
GEN-2019-058 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2611 | 32.2728 | 0.0117
GEN-2019-058 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.2249 | 21.2295 | 0.0046
GEN-2019-058 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.7409 | 19.7453 | 0.0044
GEN-2019-058 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.7292 | 24.7357 | 0.0065
GEN-2019-058 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7603 | 0.0066
GEN-2019-058 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1282 | 4.1289 | 0.0007
GEN-2019-058 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2368 | 5.2377 | 0.0009
GEN-2019-058 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.3414 | 0.0675
GEN-2019-058 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5527 | 0.0488
GEN-2019-058 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6602 | 0.0016
GEN-2019-058 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.7827 | 10.7926 | 0.0099
GEN-2019-058 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.0696 | 16.0923 | 0.0227
GEN-2019-058 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.7468 | 3.7487 | 0.0019
GEN-2019-058 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 7.2412 | 7.2484 | 0.0072
GEN-2019-058 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5649 | 0.0006
GEN-2019-058 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5202 | 7.5224 | 0.0022
GEN-2019-058 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 10.0837 | 10.0976 | 0.0139
GEN-2019-058 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5413 | 8.5475 | 0.0062
GEN-2019-058 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2907 | 10.2924 | 0.0017
GEN-2019-058 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.1835 | 0.0093
GEN-2019-058 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.8365 | 4.8397 | 0.0032
GEN-2019-058 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0787 | 0.0066
GEN-2019-058 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.2599 | 0.02
GEN-2019-058 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6496 | 0.0711
GEN-2019-058 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5123 | 0.0024
GEN-2019-058 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.6016 | 6.6075 | 0.0059
GEN-2019-058 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.4404 | 5.4438 | 0.0034
GEN-2019-058 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3082 | 13.3507 | 0.0425
GEN-2019-058 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.4345 | 8.4394 | 0.0049
GEN-2019-058 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.161 | 0.0142
GEN-2019-058 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5649 | 0.0006
GEN-2019-058 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5649 | 0.0006
GEN-2019-058 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6264 | 13.9494 | 0.323
GEN-2019-058 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7204 | 16.7997 | 0.0793
GEN-2019-058 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.462 | 0.159
GEN-2019-058 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0903 | 18.1209 | 0.0306
GEN-2019-058 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3566 | 11.5778 | 0.2212
GEN-2019-058 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.1861 | 0.1296
GEN-2019-058 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6022 | 11.8176 | 0.2154
GEN-2019-058 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6022 | 11.8176 | 0.2154
GEN-2019-058 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8495 | 9.9986 | 0.1491
GEN-2019-058 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9933 | 9.1193 | 0.126
GEN-2019-058 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3755 | 0.0014
GEN-2019-058 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 13.5709 | 13.5772 | 0.0063
GEN-2019-058 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8928 | 12.0827 | 0.1899
GEN-2019-058 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.6562 | 0.0025
GEN-2019-058 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7263 | 10.7287 | 0.0024
GEN-2019-058 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2338 | 5.2343 | 0.0005
GEN-2019-058 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 13.0113 | 0.1483
GEN-2019-058 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2566 | 7.2576 | 0.001
GEN-2019-058 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.1463 | 6.1473 | 0.001
GEN-2019-058 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.5471 | 9.5505 | 0.0034
GEN-2019-058 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.0803 | 7.0805 | 0.0002
GEN-2019-058 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4173 | 10.5603 | 0.143
GEN-2019-058 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4892 | 15.5777 | 0.0885
GEN-2019-058 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.532 | 0.0018
GEN-2019-058 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.735 | 6.736 | 0.001
GEN-2019-058 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0508 | 10.0533 | 0.0025
GEN-2019-058 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4358 | 7.4367 | 0.0009
GEN-2019-058 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7945 | 7.7956 | 0.0011
GEN-2019-058 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 11.254 | 11.2583 | 0.0043
GEN-2019-058 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7204 | 16.7997 | 0.0793
GEN-2019-058 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.4187 | 29.4284 | 0.0097
GEN-2019-058 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.523 | 6.5237 | 0.0007
GEN-2019-058 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4722 | 2.4734 | 0.0012
GEN-2019-058 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.055 | 9.057 | 0.002
GEN-2019-058 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.2641 | 10.265 | 0.0009
GEN-2019-058 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.4411 | 20.4662 | 0.0251
GEN-2019-058 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1663 | 32.178 | 0.0117
GEN-2019-058 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1705 | 7.1845 | 0.014
GEN-2019-058 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6612 | 17.6645 | 0.0033
GEN-2019-058 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.9826 | 10.9844 | 0.0018
GEN-2019-058 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.069 | 12.0712 | 0.0022
GEN-2019-058 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 16.4376 | 16.4477 | 0.0101
GEN-2019-058 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.7744 | 0.1085
GEN-2019-058 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.8815 | 0.1633
GEN-2019-058 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7636 | 0.0058
GEN-2019-058 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 15.5265 | 15.5333 | 0.0068
GEN-2019-058 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.6908 | 0.0137
GEN-2019-058 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7622 | 6.7762 | 0.014
GEN-2019-058 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3303 | 13.6534 | 0.3231
GEN-2019-058 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4245 | 5.4246 | 0.0001
GEN-2019-058 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.071 | 4.0711 | 0.0001
GEN-2019-058 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.7856 | 3.7857 | 0.0001
GEN-2019-058 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.723 | 4.7231 | 0.0001
GEN-2019-063 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 10.2738 | 10.2742 | 0.0004
GEN-2019-063 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.3418 | 13.3422 | 0.0004
GEN-2019-063 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1492 | 5.1492 | 0
GEN-2019-063 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 9.0808 | 9.0811 | 0.0003
GEN-2019-063 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.0357 | 10.0367 | 0.001
GEN-2019-063 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.5439 | 7.544 | 0.0001
GEN-2019-063 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.2241 | 3.2242 | 0.0001
GEN-2019-063 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 18.5114 | 18.5165 | 0.0051
GEN-2019-063 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 23.9995 | 24.0021 | 0.0026
GEN-2019-063 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 9.1319 | 9.1322 | 0.0003
GEN-2019-063 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.6986 | 9.699 | 0.0004
GEN-2019-063 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 16.7031 | 16.7048 | 0.0017
GEN-2019-063 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.6938 | 17.6951 | 0.0013
GEN-2019-063 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 11.9181 | 11.919 | 0.0009
GEN-2019-063 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 7.4731 | 7.4733 | 0.0002
GEN-2019-063 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 30.2867 | 30.288 | 0.0013
GEN-2019-063 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.5022 | 8.5026 | 0.0004
GEN-2019-063 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.197 | 13.1981 | 0.0011
GEN-2019-063 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 10.9472 | 10.9486 | 0.0014
GEN-2019-063 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 10.0304 | 10.0316 | 0.0012
GEN-2019-063 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5721 | 19.5726 | 0.0005
GEN-2019-063 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 6.4051 | 6.4052 | 0.0001
GEN-2019-063 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.5753 | 8.5764 | 0.0011
GEN-2019-063 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.459 | 14.4688 | 0.0098
GEN-2019-063 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 15.5265 | 15.5292 | 0.0027
GEN-2019-063 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.361 | 10.3626 | 0.0016
GEN-2019-063 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.6894 | 11.6915 | 0.0021
GEN-2019-063 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.5315 | 9.5327 | 0.0012
GEN-2019-063 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.5209 | 9.5221 | 0.0012
GEN-2019-063 | 03 CENTRAL | 520425 | PIC4 | 138 | 8.2005 | 8.2005 | 0
GEN-2019-063 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.1025 | 10.1035 | 0.001
GEN-2019-063 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 11.7335 | 11.735 | 0.0015
GEN-2019-063 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3423 | 19.3428 | 0.0005
GEN-2019-063 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.8534 | 6.8534 | 0
GEN-2019-063 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.8039 | 6.8044 | 0.0005
GEN-2019-063 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.9803 | 7.9803 | 0
GEN-2019-063 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.8699 | 8.87 | 0.0001
GEN-2019-063 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.009 | 20.0095 | 0.0005
GEN-2019-063 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1077 | 6.1104 | 0.0027
GEN-2019-063 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7167 | 9.7239 | 0.0072
GEN-2019-063 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.742 | 0.0062
GEN-2019-063 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.8251 | 0.004
GEN-2019-063 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8193 | 0.0065
GEN-2019-063 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8302 | 0.0064
GEN-2019-063 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5353 | 0.0005
GEN-2019-063 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0203 | 0.0033
GEN-2019-063 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.742 | 0.0062
GEN-2019-063 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3235 | 21.328 | 0.0045
GEN-2019-063 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8296 | 9.837 | 0.0074
GEN-2019-063 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0058 | 7.0083 | 0.0025
GEN-2019-063 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.8331 | 0.0658
GEN-2019-063 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.4033 | 0.016
GEN-2019-063 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4763 | 0.0101
GEN-2019-063 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.6004 | 0.0102
GEN-2019-063 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5253 | 16.5257 | 0.0004
GEN-2019-063 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3782 | 11.3798 | 0.0016
GEN-2019-063 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8481 | 13.8484 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.5466 | 20.5569 | 0.0103
GEN-2019-063 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.1428 | 7.1438 | 0.001
GEN-2019-063 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9854 | 5.9861 | 0.0007
GEN-2019-063 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0095 | 5.0099 | 0.0004
GEN-2019-063 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9257 | 18.9286 | 0.0029
GEN-2019-063 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0737 | 7.074 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.5534 | 18.5552 | 0.0018
GEN-2019-063 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6983 | 5.6985 | 0.0002
GEN-2019-063 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5286 | 23.5378 | 0.0092
GEN-2019-063 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0612 | 18.0615 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1603 | 14.1621 | 0.0018
GEN-2019-063 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.2792 | 28.2817 | 0.0025
GEN-2019-063 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3372 | 32.342 | 0.0048
GEN-2019-063 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2611 | 32.2658 | 0.0047
GEN-2019-063 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.2249 | 21.2268 | 0.0019
GEN-2019-063 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.7409 | 19.7426 | 0.0017
GEN-2019-063 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.7292 | 24.7318 | 0.0026
GEN-2019-063 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7563 | 0.0026
GEN-2019-063 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1282 | 4.1285 | 0.0003
GEN-2019-063 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.2368 | 5.2372 | 0.0004
GEN-2019-063 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.301 | 0.0271
GEN-2019-063 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.5235 | 0.0196
GEN-2019-063 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.6593 | 0.0007
GEN-2019-063 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.7827 | 10.7867 | 0.004
GEN-2019-063 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.0696 | 16.0788 | 0.0092
GEN-2019-063 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.7468 | 3.7475 | 0.0007
GEN-2019-063 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 7.2412 | 7.2441 | 0.0029
GEN-2019-063 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5645 | 0.0002
GEN-2019-063 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5202 | 7.5211 | 0.0009
GEN-2019-063 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 10.0837 | 10.0893 | 0.0056
GEN-2019-063 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.5413 | 8.5438 | 0.0025
GEN-2019-063 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 10.2907 | 10.2914 | 0.0007
GEN-2019-063 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.1779 | 0.0037
GEN-2019-063 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.8365 | 4.8378 | 0.0013
GEN-2019-063 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0748 | 0.0027
GEN-2019-063 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.248 | 0.0081
GEN-2019-063 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6071 | 0.0286
GEN-2019-063 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5108 | 0.0009
GEN-2019-063 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.6016 | 6.604 | 0.0024
GEN-2019-063 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.4404 | 5.4418 | 0.0014
GEN-2019-063 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3083 | 13.3254 | 0.0171
GEN-2019-063 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.4345 | 8.4365 | 0.002
GEN-2019-063 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1525 | 0.0057
GEN-2019-063 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5645 | 0.0002
GEN-2019-063 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5645 | 0.0002
GEN-2019-063 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.6264 | 13.755 | 0.1286
GEN-2019-063 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.7204 | 16.7523 | 0.0319
GEN-2019-063 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.3667 | 0.0637
GEN-2019-063 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.0903 | 18.1026 | 0.0123
GEN-2019-063 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3567 | 11.4449 | 0.0882
GEN-2019-063 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.1085 | 0.052
GEN-2019-063 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6022 | 11.6882 | 0.086
GEN-2019-063 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 11.6022 | 11.6882 | 0.086
GEN-2019-063 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.8495 | 9.9092 | 0.0597
GEN-2019-063 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.9933 | 9.0437 | 0.0504
GEN-2019-063 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3747 | 0.0006
GEN-2019-063 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 13.5709 | 13.5735 | 0.0026
GEN-2019-063 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.8928 | 11.9687 | 0.0759
GEN-2019-063 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.6547 | 0.001
GEN-2019-063 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.7263 | 10.7273 | 0.001
GEN-2019-063 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2338 | 5.234 | 0.0002
GEN-2019-063 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.9225 | 0.0595
GEN-2019-063 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 7.2566 | 7.257 | 0.0004
GEN-2019-063 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.1463 | 6.1467 | 0.0004
GEN-2019-063 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.5471 | 9.5485 | 0.0014
GEN-2019-063 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.0803 | 7.0804 | 0.0001
GEN-2019-063 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.4173 | 10.4746 | 0.0573
GEN-2019-063 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.4892 | 15.5248 | 0.0356
GEN-2019-063 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5309 | 0.0007
GEN-2019-063 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.735 | 6.7354 | 0.0004
GEN-2019-063 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0508 | 10.0518 | 0.001
GEN-2019-063 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4358 | 7.4362 | 0.0004
GEN-2019-063 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7945 | 7.7949 | 0.0004
GEN-2019-063 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 11.254 | 11.2557 | 0.0017
GEN-2019-063 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.7204 | 16.7523 | 0.0319
GEN-2019-063 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.4187 | 29.4226 | 0.0039
GEN-2019-063 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.523 | 6.5233 | 0.0003
GEN-2019-063 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4722 | 2.4727 | 0.0005
GEN-2019-063 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.055 | 9.0558 | 0.0008
GEN-2019-063 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 10.2641 | 10.2645 | 0.0004
GEN-2019-063 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.4411 | 20.4512 | 0.0101
GEN-2019-063 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1663 | 32.171 | 0.0047
GEN-2019-063 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1705 | 7.1761 | 0.0056
GEN-2019-063 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6612 | 17.6626 | 0.0014
GEN-2019-063 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.9826 | 10.9834 | 0.0008
GEN-2019-063 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.069 | 12.0699 | 0.0009
GEN-2019-063 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 16.4376 | 16.4417 | 0.0041
GEN-2019-063 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.7094 | 0.0435
GEN-2019-063 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.7835 | 0.0653
GEN-2019-063 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7601 | 0.0023
GEN-2019-063 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 15.5265 | 15.5292 | 0.0027
GEN-2019-063 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.6826 | 0.0055
GEN-2019-063 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7622 | 6.7678 | 0.0056
GEN-2019-063 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.3303 | 13.4588 | 0.1285
GEN-2019-063 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 5.4245 | 5.4245 | 0
GEN-2019-063 | 03 CENTRAL | 900002 | TRAVERSE-2 | 345 | 4.071 | 4.0711 | 0.0001
GEN-2019-063 | 03 CENTRAL | 900003 | TRAVERSE1 | 345 | 3.7856 | 3.7856 | 0
GEN-2019-063 | 03 CENTRAL | 900004 | TRW2-TRW3 | 345 | 4.723 | 4.723 | 0
GEN-2019-068 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2136 | 3.2162 | 0.0026
GEN-2019-068 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.6766 | 8.6955 | 0.0189
GEN-2019-068 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.7358 | 10.7773 | 0.0415
GEN-2019-068 | 03 CENTRAL | 530560 | WKNNY 3 | 115 | 2.2418 | 2.2427 | 0.0009
GEN-2019-068 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6534 | 10.6743 | 0.0209
GEN-2019-068 | 03 CENTRAL | 530562 | HAYS 3 | 115 | 7.901 | 7.9154 | 0.0144
GEN-2019-068 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.6854 | 8.7205 | 0.0351
GEN-2019-068 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7795 | 6.8006 | 0.0211
GEN-2019-068 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6577 | 1.6589 | 0.0012
GEN-2019-068 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2609 | 1.2616 | 0.0007
GEN-2019-068 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1437 | 1.1443 | 0.0006
GEN-2019-068 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.8211 | 8.8747 | 0.0536
GEN-2019-068 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.8128 | 7.8325 | 0.0197
GEN-2019-068 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.8238 | 10.8661 | 0.0423
GEN-2019-068 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.731 | 3.7367 | 0.0057
GEN-2019-068 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.0036 | 6.0202 | 0.0166
GEN-2019-068 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.0184 | 5.03 | 0.0116
GEN-2019-068 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.4973 | 1.4983 | 0.001
GEN-2019-068 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.2841 | 6.2895 | 0.0054
GEN-2019-068 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.5259 | 5.53 | 0.0041
GEN-2019-068 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.796 | 5.8006 | 0.0046
GEN-2019-068 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 11.278 | 11.3885 | 0.1105
GEN-2019-068 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.1782 | 4.1873 | 0.0091
GEN-2019-068 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.6319 | 3.6387 | 0.0068
GEN-2019-068 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.0744 | 4.0816 | 0.0072
GEN-2019-068 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.5235 | 7.5725 | 0.049
GEN-2019-068 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5348 | 3.5415 | 0.0067
GEN-2019-068 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.3618 | 2.3635 | 0.0017
GEN-2019-068 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.1026 | 4.1062 | 0.0036
GEN-2019-068 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.5159 | 1.5166 | 0.0007
GEN-2019-068 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.5459 | 5.5516 | 0.0057
GEN-2019-068 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.628 | 1.6288 | 0.0008
GEN-2019-068 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.1728 | 2.1742 | 0.0014
GEN-2019-068 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.673 | 6.6832 | 0.0102
GEN-2019-068 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.0877 | 5.0957 | 0.008
GEN-2019-068 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0796 | 10.0982 | 0.0186
GEN-2019-068 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.6543 | 2.6556 | 0.0013
GEN-2019-068 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.0398 | 5.0541 | 0.0143
GEN-2019-068 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.1255 | 8.2748 | 0.1493
GEN-2019-068 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 5.0856 | 5.092 | 0.0064
GEN-2019-068 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1037 | 2.1049 | 0.0012
GEN-2019-068 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.5675 | 1.5682 | 0.0007
GEN-2019-068 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.2442 | 4.2527 | 0.0085
GEN-2019-068 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.8601 | 2.8633 | 0.0032
GEN-2019-068 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.6795 | 8.6966 | 0.0171
GEN-2019-068 | 03 CENTRAL | 530694 | VINE2 3 | 115 | 7.9902 | 8.0049 | 0.0147
GEN-2019-068 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.627 | 8.6442 | 0.0172
GEN-2019-068 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.017 | 8.0392 | 0.0222
GEN-2019-068 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.521 | 4.5247 | 0.0037
GEN-2019-068 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.3869 | 5.3942 | 0.0073
GEN-2019-068 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.286 | 4.2903 | 0.0043
GEN-2019-068 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.7358 | 10.7773 | 0.0415
GEN-2019-068 | 03 CENTRAL | 530721 | VINEDE_N | 115 | 7.9902 | 8.0049 | 0.0147
GEN-2019-068 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.9902 | 8.0049 | 0.0147
GEN-2019-068 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5438 | 3.547 | 0.0032
GEN-2019-068 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.7673 | 13.7904 | 0.0231
GEN-2019-068 | 03 CENTRAL | 531492 | OG ONEOK | 115 | 2.1631 | 2.1639 | 0.0008
GEN-2019-068 | 03 CENTRAL | 531497 | TURKEYR3 | 115 | 1.8107 | 1.8113 | 0.0006
GEN-2019-068 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3873 | 9.3936 | 0.0063
GEN-2019-068 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4662 | 7.4702 | 0.004
GEN-2019-068 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.5902 | 7.5942 | 0.004
GEN-2019-068 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.2398 | 10.2429 | 0.0031
GEN-2019-068 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.3782 | 11.391 | 0.0128
GEN-2019-068 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 11.1014 | 11.1108 | 0.0094
GEN-2019-068 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.5286 | 23.5393 | 0.0107
GEN-2019-068 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0092 | 14.0112 | 0.002
GEN-2019-068 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.5966 | 8.6421 | 0.0455
GEN-2019-068 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.9396 | 7.9596 | 0.02
GEN-2019-068 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2675 | 13.2843 | 0.0168
GEN-2019-068 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.2495 | 8.2522 | 0.0027
GEN-2019-068 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.8827 | 4.8835 | 0.0008
GEN-2019-068 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.1169 | 7.1183 | 0.0014
GEN-2019-068 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8762 | 3.8765 | 0.0003
GEN-2019-068 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4554 | 3.4556 | 0.0002
GEN-2019-068 | 03 CENTRAL | 533369 | HILSBOR3 | 115 | 2.6599 | 2.6601 | 0.0002
GEN-2019-068 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.1793 | 12.1853 | 0.006
GEN-2019-068 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.53 | 12.5381 | 0.0081
GEN-2019-068 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.5098 | 10.5153 | 0.0055
GEN-2019-068 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.9711 | 3.9715 | 0.0004
GEN-2019-068 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 17.774 | 17.7888 | 0.0148
GEN-2019-068 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.2245 | 7.2289 | 0.0044
GEN-2019-068 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.8197 | 9.8341 | 0.0144
GEN-2019-068 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 10.007 | 10.022 | 0.015
GEN-2019-068 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.8145 | 18.8636 | 0.0491
GEN-2019-068 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 8.1684 | 8.1763 | 0.0079
GEN-2019-068 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.3587 | 8.3661 | 0.0074
GEN-2019-068 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.7537 | 22.7984 | 0.0447
GEN-2019-068 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.5521 | 11.5708 | 0.0187
GEN-2019-068 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.6216 | 17.6645 | 0.0429
GEN-2019-068 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 18.3044 | 18.3509 | 0.0465
GEN-2019-068 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.6109 | 8.6209 | 0.01
GEN-2019-068 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.69 | 10.7053 | 0.0153
GEN-2019-068 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.8689 | 10.8843 | 0.0154
GEN-2019-068 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.7766 | 8.7795 | 0.0029
GEN-2019-068 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.7762 | 6.7779 | 0.0017
GEN-2019-068 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 11.2517 | 11.2679 | 0.0162
GEN-2019-068 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.9943 | 7.0013 | 0.007
GEN-2019-068 | 03 CENTRAL | 533440 | 43LORAN | 115 | 12.706 | 12.7275 | 0.0215
GEN-2019-068 | 03 CENTRAL | 533455 | TWR 33 3 | 115 | 10.5484 | 10.5627 | 0.0143
GEN-2019-068 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 5.0305 | 5.0326 | 0.0021
GEN-2019-068 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 5.1075 | 5.1097 | 0.0022
GEN-2019-068 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.0333 | 4.0345 | 0.0012
GEN-2019-068 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.0601 | 4.0613 | 0.0012
GEN-2019-068 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.4853 | 7.4891 | 0.0038
GEN-2019-068 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 5.2371 | 5.2394 | 0.0023
GEN-2019-068 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 6.0462 | 6.0492 | 0.003
GEN-2019-068 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.6376 | 5.6402 | 0.0026
GEN-2019-068 | 03 CENTRAL | 533513 | HEC 2 | 69 | 8.2014 | 8.207 | 0.0056
GEN-2019-068 | 03 CENTRAL | 533514 | HEC GT 2 | 69 | 7.9855 | 7.9908 | 0.0053
GEN-2019-068 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 6.3446 | 6.3473 | 0.0027
GEN-2019-068 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.1504 | 6.1529 | 0.0025
GEN-2019-068 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.4999 | 6.5034 | 0.0035
GEN-2019-068 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.82 | 5.8228 | 0.0028
GEN-2019-068 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.298 | 5.3003 | 0.0023
GEN-2019-068 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 6.5241 | 6.527 | 0.0029
GEN-2019-068 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.2739 | 12.2989 | 0.025
GEN-2019-068 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5039 | 10.522 | 0.0181
GEN-2019-068 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.6586 | 3.659 | 0.0004
GEN-2019-068 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.03 | 4.0371 | 0.0071
GEN-2019-068 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7031 | 3.7088 | 0.0057
GEN-2019-068 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.3539 | 3.3577 | 0.0038
GEN-2019-068 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.2396 | 7.2827 | 0.0431
GEN-2019-068 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.58 | 3.5839 | 0.0039
GEN-2019-068 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0774 | 8.1287 | 0.0513
GEN-2019-068 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2019-068 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 11.3191 | 11.4301 | 0.111
GEN-2019-068 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.1742 | 8.3255 | 0.1513
GEN-2019-068 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.3956 | 8.4554 | 0.0598
GEN-2019-068 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9713 | 2.979 | 0.0077
GEN-2019-068 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 7.0721 | 7.0737 | 0.0016
GEN-2019-068 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.2205 | 7.2629 | 0.0424
GEN-2019-068 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.6695 | 5.6875 | 0.018
GEN-2019-068 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2399 | 10.2465 | 0.0066
GEN-2019-068 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.5785 | 12.6048 | 0.0263
GEN-2019-068 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.0877 | 5.0957 | 0.008
GEN-2019-068 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.8401 | 2.8425 | 0.0024
GEN-2019-068 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.5099 | 4.5105 | 0.0006
GEN-2019-068 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.544 | 3.549 | 0.005
GEN-2019-068 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.3083 | 13.3151 | 0.0068
GEN-2019-068 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 10.1468 | 10.1503 | 0.0035
GEN-2019-068 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2019-068 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.5643 | 2.5644 | 0.0001
GEN-2019-068 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.303 | 13.3236 | 0.0206
GEN-2019-068 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.0565 | 12.0733 | 0.0168
GEN-2019-068 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.3741 | 3.3744 | 0.0003
GEN-2019-068 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.6537 | 6.6567 | 0.003
GEN-2019-068 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.863 | 12.8822 | 0.0192
GEN-2019-068 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.5302 | 5.5323 | 0.0021
GEN-2019-068 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.735 | 6.7387 | 0.0037
GEN-2019-068 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.0508 | 10.0596 | 0.0088
GEN-2019-068 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 5.9129 | 5.9149 | 0.002
GEN-2019-068 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 6.5202 | 6.5225 | 0.0023
GEN-2019-068 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 7.2229 | 7.2658 | 0.0429
GEN-2019-068 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6659 | 9.6745 | 0.0086
GEN-2019-068 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7182 | 11.7311 | 0.0129
GEN-2019-068 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.7578 | 6.7592 | 0.0014
GEN-2019-068 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.6771 | 6.7081 | 0.031
GEN-2019-068 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.7622 | 6.794 | 0.0318
GEN-2019-068 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.3629 | 6.563 | 0.2001
GEN-2019-068 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.4401 | 6.64 | 0.1999
GEN-2018-064 | 04 SOUTHEAST | 300045 | 7MORGAN | 345 | 13.9865 | 13.9886 | 0.0021
GEN-2018-064 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7146 | 15.7161 | 0.0015
GEN-2018-064 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 24.8594 | 24.8788 | 0.0194
GEN-2018-064 | 04 SOUTHEAST | 300741 | 5SPORTSMAN | 161 | 41.3361 | 41.3518 | 0.0157
GEN-2018-064 | 04 SOUTHEAST | 504201 | GENTRY 5 | 161 | 27.6538 | 27.7504 | 0.0966
GEN-2018-064 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 20.2399 | 20.2949 | 0.055
GEN-2018-064 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 34.7312 | 34.8857 | 0.1545
GEN-2018-064 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.8074 | 15.884 | 0.0766
GEN-2018-064 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.14 | 24.2224 | 0.0824
GEN-2018-064 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.544 | 10.5636 | 0.0196
GEN-2018-064 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.6667 | 22.8283 | 0.1616
GEN-2018-064 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.0944 | 23.1458 | 0.0514
GEN-2018-064 | 04 SOUTHEAST | 506972 | LINCOLN2 | 69 | 4.9961 | 4.998 | 0.0019
GEN-2018-064 | 04 SOUTHEAST | 506973 | SILOAM 2 | 69 | 11.4518 | 11.4674 | 0.0156
GEN-2018-064 | 04 SOUTHEAST | 506979 | SHIPERD7 | 345 | 10.6392 | 10.672 | 0.0328
GEN-2018-064 | 04 SOUTHEAST | 506980 | SHIPERD5 | 161 | 15.9139 | 15.9441 | 0.0302
GEN-2018-064 | 04 SOUTHEAST | 506992 | WEDINGTON | 161 | 16.8347 | 16.8722 | 0.0375
GEN-2018-064 | 04 SOUTHEAST | 512637 | 412SUB 5 | 161 | 12.2414 | 12.2567 | 0.0153
GEN-2018-064 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 15.2833 | 15.3663 | 0.083
GEN-2018-064 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 20.518 | 20.7044 | 0.1864
GEN-2018-064 | 04 SOUTHEAST | 512648 | MAID 5 | 161 | 46.5635 | 46.5904 | 0.0269
GEN-2018-064 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 27.3261 | 27.3522 | 0.0261
GEN-2018-064 | 04 SOUTHEAST | 512656 | GRDA1 5 | 161 | 46.0133 | 46.0394 | 0.0261
GEN-2018-064 | 04 SOUTHEAST | 512700 | WAGNOR 5 | 161 | 10.0312 | 10.0318 | 0.0006
GEN-2018-064 | 04 SOUTHEAST | 512714 | KANSATP5 | 161 | 12.0847 | 12.1147 | 0.03
GEN-2018-064 | 04 SOUTHEAST | 512716 | KANSAS 5 | 161 | 11.4817 | 11.5086 | 0.0269
GEN-2018-064 | 04 SOUTHEAST | 512727 | GRDA1 2 | 69 | 12.6512 | 12.652 | 0.0008
GEN-2018-064 | 04 SOUTHEAST | 512728 | ARKLIN2 | 69 | 3.8315 | 4.3012 | 0.4697
GEN-2018-064 | 04 SOUTHEAST | 512730 | SSSWES2 | 69 | 11.8538 | 11.8794 | 0.0256
GEN-2018-064 | 04 SOUTHEAST | 512737 | SSSWTP2 | 69 | 12.9545 | 12.985 | 0.0305
GEN-2018-064 | 04 SOUTHEAST | 512742 | WMAIN ST5 | 161 | 29.0792 | 29.0894 | 0.0102
GEN-2018-064 | 04 SOUTHEAST | 512744 | SSMOSS2 | 69 | 10.6702 | 10.6912 | 0.021
GEN-2018-064 | 04 SOUTHEAST | 512745 | SSLINC2 | 69 | 2.9171 | 3.1768 | 0.2597
GEN-2018-064 | 04 SOUTHEAST | 512746 | SSNORT2 | 69 | 2.9729 | 3.2433 | 0.2704
GEN-2018-064 | 04 SOUTHEAST | 512747 | SSNEWN2 | 69 | 3.2127 | 3.5328 | 0.3201
GEN-2018-064 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 15.578 | 15.6574 | 0.0794
GEN-2018-064 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.6221 | 15.9272 | 0.3051
GEN-2018-064 | 04 SOUTHEAST | 512753 | TONNEC2 | 69 | 4.9055 | 5.7109 | 0.8054
GEN-2018-064 | 04 SOUTHEAST | 512756 | TONECESTR2 | 69 | 3.9409 | 4.4402 | 0.4993
GEN-2018-064 | 04 SOUTHEAST | 512820 | SILMCTY2 | 69 | 13.8996 | 13.9345 | 0.0349
GEN-2018-064 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.1037 | 26.1263 | 0.0226
GEN-2018-064 | 04 SOUTHEAST | 513570 | CHOUTEAUCRK5 | 161 | 21.4416 | 21.4462 | 0.0046
GEN-2018-064 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7058 | 20.7183 | 0.0125
GEN-2018-064 | 04 SOUTHEAST | 547484 | DEC392 5 | 161 | 15.8991 | 15.9241 | 0.025
GEN-2018-064 | 04 SOUTHEAST | 549969 | BROOKLINE 5 | 161 | 29.0066 | 29.0101 | 0.0035
GEN-2018-064 | 04 SOUTHEAST | 549984 | BROOKLINE 7 | 345 | 12.231 | 12.2346 | 0.0036
GEN-2018-064 | 04 SOUTHEAST | 589140 | GEN-2017-076 | 161 | 21.5022 | 21.5675 | 0.0653
GEN-2018-064 | 04 SOUTHEAST | 762999 | GEN-2018-064 | 69 | 3.5872 | 4.424 | 0.8368
GEN-2018-071 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.5262 | 15.5277 | 0.0015
GEN-2018-071 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 17.4041 | 17.4082 | 0.0041
GEN-2018-071 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 16.5805 | 16.5823 | 0.0018
GEN-2018-071 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7145 | 15.7161 | 0.0016
GEN-2018-071 | 04 SOUTHEAST | 301011 | 4REDRCK | 138 | 16.4526 | 16.4571 | 0.0045
GEN-2018-071 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.4045 | 7.4049 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.3237 | 23.3268 | 0.0031
GEN-2018-071 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.0959 | 23.1075 | 0.0116
GEN-2018-071 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.4513 | 33.4578 | 0.0065
GEN-2018-071 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.2894 | 26.2907 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.0226 | 52.0266 | 0.004
GEN-2018-071 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.1102 | 33.1151 | 0.0049
GEN-2018-071 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.7159 | 8.7163 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.4054 | 30.4082 | 0.0028
GEN-2018-071 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.7222 | 26.7247 | 0.0025
GEN-2018-071 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.5523 | 29.5552 | 0.0029
GEN-2018-071 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.8129 | 36.8184 | 0.0055
GEN-2018-071 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.7891 | 19.7906 | 0.0015
GEN-2018-071 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.7322 | 30.7363 | 0.0041
GEN-2018-071 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.7442 | 25.7455 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.8118 | 15.8131 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.8058 | 24.8173 | 0.0115
GEN-2018-071 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.3833 | 12.3839 | 0.0006
GEN-2018-071 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.5666 | 23.572 | 0.0054
GEN-2018-071 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.1473 | 34.1501 | 0.0028
GEN-2018-071 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.9351 | 52.9391 | 0.004
GEN-2018-071 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.1389 | 24.1401 | 0.0012
GEN-2018-071 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.7815 | 36.787 | 0.0055
GEN-2018-071 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.8159 | 28.8187 | 0.0028
GEN-2018-071 | 04 SOUTHEAST | 510376 | WEBBTAP4 | 138 | 7.9842 | 7.9846 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.1756 | 12.1769 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.4877 | 19.491 | 0.0033
GEN-2018-071 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.4533 | 15.4685 | 0.0152
GEN-2018-071 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.4172 | 16.419 | 0.0018
GEN-2018-071 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 17.4042 | 17.4083 | 0.0041
GEN-2018-071 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.1249 | 26.1263 | 0.0014
GEN-2018-071 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5641 | 17.5645 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5641 | 17.5645 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.717 | 20.7183 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.965 | 20.9722 | 0.0072
GEN-2018-071 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.2487 | 4.2488 | 0.0001
GEN-2018-071 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.655 | 11.6567 | 0.0017
GEN-2018-071 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.3816 | 11.3833 | 0.0017
GEN-2018-071 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 9.0114 | 9.0122 | 0.0008
GEN-2018-071 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 18.5789 | 18.5819 | 0.003
GEN-2018-071 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.1058 | 16.1078 | 0.002
GEN-2018-071 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 8.8393 | 8.8402 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.8075 | 19.811 | 0.0035
GEN-2018-071 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.064 | 19.0785 | 0.0145
GEN-2018-071 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3188 | 8.3193 | 0.0005
GEN-2018-071 | 04 SOUTHEAST | 514737 | OTOE 4 | 138 | 16.78 | 16.7847 | 0.0047
GEN-2018-071 | 04 SOUTHEAST | 514742 | OSGE 2 | 69 | 19.2767 | 19.2778 | 0.0011
GEN-2018-071 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.8403 | 17.8436 | 0.0033
GEN-2018-071 | 04 SOUTHEAST | 514758 | STDBEAR4 | 138 | 14.9729 | 14.9752 | 0.0023
GEN-2018-071 | 04 SOUTHEAST | 514761 | WHEAGLE4 | 138 | 16.8838 | 16.8869 | 0.0031
GEN-2018-071 | 04 SOUTHEAST | 514770 | MARLNDT4 | 138 | 11.6075 | 11.6088 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.0212 | 21.0283 | 0.0071
GEN-2018-071 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.6937 | 11.696 | 0.0023
GEN-2018-071 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 31.8717 | 31.8894 | 0.0177
GEN-2018-071 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 28.4062 | 28.5498 | 0.1436
GEN-2018-071 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 12.7907 | 12.9849 | 0.1942
GEN-2018-071 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0598 | 46.0655 | 0.0057
GEN-2018-071 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.6241 | 33.6344 | 0.0103
GEN-2018-071 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.9868 | 23.9957 | 0.0089
GEN-2018-071 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.899 | 34.9065 | 0.0075
GEN-2018-071 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.686 | 27.6884 | 0.0024
GEN-2018-071 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.8164 | 26.8185 | 0.0021
GEN-2018-071 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.4124 | 14.4147 | 0.0023
GEN-2018-071 | 04 SOUTHEAST | 515009 | MCELROY4 | 138 | 14.4494 | 14.4507 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.7686 | 14.77 | 0.0014
GEN-2018-071 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.4702 | 22.471 | 0.0008
GEN-2018-071 | 04 SOUTHEAST | 515400 | DMANCRK4 | 138 | 8.4546 | 8.4556 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 14.3946 | 14.3975 | 0.0029
GEN-2018-071 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.4404 | 14.4427 | 0.0023
GEN-2018-071 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.4198 | 13.4257 | 0.0059
GEN-2018-071 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.4008 | 13.4067 | 0.0059
GEN-2018-071 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.1785 | 33.1877 | 0.0092
GEN-2018-071 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.9098 | 12.9145 | 0.0047
GEN-2018-071 | 04 SOUTHEAST | 515574 | SPGVLLY4 | 138 | 11.1865 | 11.1871 | 0.0006
GEN-2018-071 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.6295 | 14.9814 | 0.3519
GEN-2018-071 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 12.825 | 13.0203 | 0.1953
GEN-2018-071 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 11.5433 | 11.7586 | 0.2153
GEN-2018-071 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.1462 | 17.1527 | 0.0065
GEN-2018-071 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.1419 | 17.1484 | 0.0065
GEN-2018-071 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 12.596 | 12.6229 | 0.0269
GEN-2018-071 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.8263 | 16.831 | 0.0047
GEN-2018-071 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6558 | 4.6566 | 0.0008
GEN-2018-071 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.0899 | 17.1141 | 0.0242
GEN-2018-071 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.0323 | 17.0564 | 0.0241
GEN-2018-071 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.5007 | 11.7238 | 0.2231
GEN-2018-071 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 14.6054 | 14.956 | 0.3506
GEN-2018-071 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.5219 | 9.5288 | 0.0069
GEN-2018-071 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 17.95 | 17.9751 | 0.0251
GEN-2018-071 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 17.7622 | 17.808 | 0.0458
GEN-2018-071 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 21.3127 | 21.3282 | 0.0155
GEN-2018-071 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 17.7085 | 17.7137 | 0.0052
GEN-2018-071 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 15.8103 | 15.814 | 0.0037
GEN-2018-071 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.1112 | 10.1202 | 0.009
GEN-2018-071 | 04 SOUTHEAST | 532801 | ELKRVR17 | 345 | 9.0053 | 9.0123 | 0.007
GEN-2018-071 | 04 SOUTHEAST | 532986 | BENTON 4 | 138 | 26.8075 | 26.8284 | 0.0209
GEN-2018-071 | 04 SOUTHEAST | 532991 | WEAVER 4 | 138 | 21.8421 | 21.8583 | 0.0162
GEN-2018-071 | 04 SOUTHEAST | 533039 | ELPASO 4 | 138 | 24.3107 | 24.3294 | 0.0187
GEN-2018-071 | 04 SOUTHEAST | 533062 | ROSEHIL4 | 138 | 29.6135 | 29.6523 | 0.0388
GEN-2018-071 | 04 SOUTHEAST | 533068 | STEARMN4 | 138 | 19.3694 | 19.3817 | 0.0123
GEN-2018-071 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 6.0885 | 6.0886 | 0.0001
GEN-2018-071 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 12.1325 | 12.2121 | 0.0796
GEN-2018-071 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.5116 | 19.5641 | 0.0525
GEN-2018-071 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.4513 | 33.4578 | 0.0065
GEN-2018-071 | 04 SOUTHEAST | 584900 | GEN-2015-052 | 345 | 12.0816 | 12.1604 | 0.0788
GEN-2018-071 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 19.3259 | 19.3774 | 0.0515
GEN-2018-071 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.6253 | 15.6447 | 0.0194
GEN-2018-071 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.3055 | 9.3117 | 0.0062
GEN-2018-071 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.0236 | 8.0282 | 0.0046
GEN-2018-071 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.1102 | 33.1151 | 0.0049
GEN-2018-071 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.4535 | 4.4542 | 0.0007
GEN-2018-071 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.5047 | 11.5098 | 0.0051
GEN-2018-071 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.1067 | 8.1092 | 0.0025
GEN-2018-071 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 30.5022 | 30.506 | 0.0038
GEN-2018-071 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 14.1757 | 14.5296 | 0.3539
GEN-2018-071 | 04 SOUTHEAST | 763069 | G18-071-TAP | 345 | 14.2312 | 14.5849 | 0.3537
GEN-2018-072 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.5264 | 15.5277 | 0.0013
GEN-2018-072 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 17.4045 | 17.4082 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 16.5806 | 16.5823 | 0.0017
GEN-2018-072 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7146 | 15.7161 | 0.0015
GEN-2018-072 | 04 SOUTHEAST | 301011 | 4REDRCK | 138 | 16.453 | 16.4571 | 0.0041
GEN-2018-072 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.4046 | 7.4049 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.324 | 23.3268 | 0.0028
GEN-2018-072 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.0969 | 23.1075 | 0.0106
GEN-2018-072 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.4519 | 33.4578 | 0.0059
GEN-2018-072 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.2895 | 26.2907 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.023 | 52.0266 | 0.0036
GEN-2018-072 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.1107 | 33.1151 | 0.0044
GEN-2018-072 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.7159 | 8.7163 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.4056 | 30.4082 | 0.0026
GEN-2018-072 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.7224 | 26.7247 | 0.0023
GEN-2018-072 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.5525 | 29.5552 | 0.0027
GEN-2018-072 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.8134 | 36.8184 | 0.005
GEN-2018-072 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.7892 | 19.7906 | 0.0014
GEN-2018-072 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.7326 | 30.7363 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.7443 | 25.7455 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.8119 | 15.8131 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.8068 | 24.8173 | 0.0105
GEN-2018-072 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.3833 | 12.3839 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.5671 | 23.572 | 0.0049
GEN-2018-072 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.1475 | 34.1501 | 0.0026
GEN-2018-072 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.9354 | 52.9391 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.139 | 24.1401 | 0.0011
GEN-2018-072 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.7819 | 36.787 | 0.0051
GEN-2018-072 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.8161 | 28.8187 | 0.0026
GEN-2018-072 | 04 SOUTHEAST | 510376 | WEBBTAP4 | 138 | 7.9842 | 7.9846 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.1757 | 12.1769 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.488 | 19.491 | 0.003
GEN-2018-072 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.4546 | 15.4685 | 0.0139
GEN-2018-072 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.4174 | 16.419 | 0.0016
GEN-2018-072 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 17.4046 | 17.4083 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.125 | 26.1263 | 0.0013
GEN-2018-072 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5641 | 17.5645 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5641 | 17.5645 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7171 | 20.7183 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.9657 | 20.9722 | 0.0065
GEN-2018-072 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.2487 | 4.2488 | 0.0001
GEN-2018-072 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.6552 | 11.6567 | 0.0015
GEN-2018-072 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.3818 | 11.3833 | 0.0015
GEN-2018-072 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 9.0115 | 9.0122 | 0.0007
GEN-2018-072 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 18.5792 | 18.5819 | 0.0027
GEN-2018-072 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.1059 | 16.1078 | 0.0019
GEN-2018-072 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 8.8393 | 8.8402 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.8078 | 19.811 | 0.0032
GEN-2018-072 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.0653 | 19.0785 | 0.0132
GEN-2018-072 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3189 | 8.3193 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 514737 | OTOE 4 | 138 | 16.7804 | 16.7847 | 0.0043
GEN-2018-072 | 04 SOUTHEAST | 514742 | OSGE 2 | 69 | 19.2768 | 19.2778 | 0.001
GEN-2018-072 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.8406 | 17.8436 | 0.003
GEN-2018-072 | 04 SOUTHEAST | 514758 | STDBEAR4 | 138 | 14.9731 | 14.9752 | 0.0021
GEN-2018-072 | 04 SOUTHEAST | 514761 | WHEAGLE4 | 138 | 16.8841 | 16.8869 | 0.0028
GEN-2018-072 | 04 SOUTHEAST | 514770 | MARLNDT4 | 138 | 11.6076 | 11.6088 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.0218 | 21.0283 | 0.0065
GEN-2018-072 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.6939 | 11.696 | 0.0021
GEN-2018-072 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 31.8732 | 31.8894 | 0.0162
GEN-2018-072 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 28.4184 | 28.5498 | 0.1314
GEN-2018-072 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 12.807 | 12.9849 | 0.1779
GEN-2018-072 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0603 | 46.0655 | 0.0052
GEN-2018-072 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.625 | 33.6344 | 0.0094
GEN-2018-072 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.9876 | 23.9957 | 0.0081
GEN-2018-072 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.8997 | 34.9065 | 0.0068
GEN-2018-072 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.6862 | 27.6884 | 0.0022
GEN-2018-072 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.8166 | 26.8185 | 0.0019
GEN-2018-072 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.4126 | 14.4147 | 0.0021
GEN-2018-072 | 04 SOUTHEAST | 515009 | MCELROY4 | 138 | 14.4495 | 14.4507 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.7687 | 14.77 | 0.0013
GEN-2018-072 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.4702 | 22.471 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 515400 | DMANCRK4 | 138 | 8.4547 | 8.4556 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 14.3948 | 14.3975 | 0.0027
GEN-2018-072 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.4406 | 14.4427 | 0.0021
GEN-2018-072 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.4203 | 13.4257 | 0.0054
GEN-2018-072 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.4013 | 13.4067 | 0.0054
GEN-2018-072 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.1793 | 33.1877 | 0.0084
GEN-2018-072 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.9102 | 12.9145 | 0.0043
GEN-2018-072 | 04 SOUTHEAST | 515574 | SPGVLLY4 | 138 | 11.1865 | 11.1871 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.6588 | 14.9814 | 0.3226
GEN-2018-072 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 12.8414 | 13.0203 | 0.1789
GEN-2018-072 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 11.5613 | 11.7586 | 0.1973
GEN-2018-072 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.1467 | 17.1527 | 0.006
GEN-2018-072 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.1424 | 17.1484 | 0.006
GEN-2018-072 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 12.5983 | 12.6229 | 0.0246
GEN-2018-072 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.8267 | 16.831 | 0.0043
GEN-2018-072 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6559 | 4.6566 | 0.0007
GEN-2018-072 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.092 | 17.1141 | 0.0221
GEN-2018-072 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.0344 | 17.0564 | 0.022
GEN-2018-072 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.5194 | 11.7238 | 0.2044
GEN-2018-072 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 14.6346 | 14.956 | 0.3214
GEN-2018-072 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.5225 | 9.5288 | 0.0063
GEN-2018-072 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 17.9521 | 17.9751 | 0.023
GEN-2018-072 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 17.7661 | 17.808 | 0.0419
GEN-2018-072 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 21.314 | 21.3282 | 0.0142
GEN-2018-072 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 17.7089 | 17.7137 | 0.0048
GEN-2018-072 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 15.8106 | 15.814 | 0.0034
GEN-2018-072 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.112 | 10.1202 | 0.0082
GEN-2018-072 | 04 SOUTHEAST | 532801 | ELKRVR17 | 345 | 9.0059 | 9.0123 | 0.0064
GEN-2018-072 | 04 SOUTHEAST | 532986 | BENTON 4 | 138 | 26.8093 | 26.8284 | 0.0191
GEN-2018-072 | 04 SOUTHEAST | 532991 | WEAVER 4 | 138 | 21.8435 | 21.8583 | 0.0148
GEN-2018-072 | 04 SOUTHEAST | 533039 | ELPASO 4 | 138 | 24.3123 | 24.3294 | 0.0171
GEN-2018-072 | 04 SOUTHEAST | 533062 | ROSEHIL4 | 138 | 29.6168 | 29.6523 | 0.0355
GEN-2018-072 | 04 SOUTHEAST | 533068 | STEARMN4 | 138 | 19.3705 | 19.3817 | 0.0112
GEN-2018-072 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 6.0885 | 6.0886 | 0.0001
GEN-2018-072 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 12.1393 | 12.2121 | 0.0728
GEN-2018-072 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.516 | 19.5641 | 0.0481
GEN-2018-072 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.4519 | 33.4578 | 0.0059
GEN-2018-072 | 04 SOUTHEAST | 584900 | GEN-2015-052 | 345 | 12.0882 | 12.1604 | 0.0722
GEN-2018-072 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 19.3303 | 19.3774 | 0.0471
GEN-2018-072 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.627 | 15.6447 | 0.0177
GEN-2018-072 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.306 | 9.3117 | 0.0057
GEN-2018-072 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.024 | 8.0282 | 0.0042
GEN-2018-072 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.1107 | 33.1151 | 0.0044
GEN-2018-072 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.4535 | 4.4542 | 0.0007
GEN-2018-072 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.5051 | 11.5098 | 0.0047
GEN-2018-072 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.1069 | 8.1092 | 0.0023
GEN-2018-072 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 30.5025 | 30.506 | 0.0035
GEN-2018-072 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 14.2052 | 14.5296 | 0.3244
GEN-2018-072 | 04 SOUTHEAST | 763069 | G18-071-TAP | 345 | 14.2606 | 14.5849 | 0.3243
GEN-2018-079 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.701 | 15.7161 | 0.0151
GEN-2018-079 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 24.8729 | 24.8788 | 0.0059
GEN-2018-079 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.8018 | 12.8088 | 0.007
GEN-2018-079 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.0222 | 21.0267 | 0.0045
GEN-2018-079 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.0957 | 23.1075 | 0.0118
GEN-2018-079 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.1039 | 33.1151 | 0.0112
GEN-2018-079 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.1335 | 50.1538 | 0.0203
GEN-2018-079 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.3879 | 30.4082 | 0.0203
GEN-2018-079 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.0932 | 30.1129 | 0.0197
GEN-2018-079 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.7858 | 24.8173 | 0.0315
GEN-2018-079 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.7648 | 36.787 | 0.0222
GEN-2018-079 | 04 SOUTHEAST | 510378 | SCOFCTY4 | 138 | 8.8956 | 9.0273 | 0.1317
GEN-2018-079 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.2324 | 11.8051 | 0.5727
GEN-2018-079 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.0112 | 12.1769 | 0.1657
GEN-2018-079 | 04 SOUTHEAST | 510386 | NBVILLE4 | 138 | 9.6937 | 9.7305 | 0.0368
GEN-2018-079 | 04 SOUTHEAST | 510391 | BV-SE--4 | 138 | 12.4907 | 12.5157 | 0.025
GEN-2018-079 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.4093 | 19.491 | 0.0817
GEN-2018-079 | 04 SOUTHEAST | 510420 | SCOFFEYV4 | 138 | 8.5015 | 8.6217 | 0.1202
GEN-2018-079 | 04 SOUTHEAST | 510422 | COFFEYT4 | 138 | 10.2412 | 10.3424 | 0.1012
GEN-2018-079 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.4629 | 15.4685 | 0.0056
GEN-2018-079 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.5501 | 8.77 | 0.2199
GEN-2018-079 | 04 SOUTHEAST | 512735 | COFCTY2 | 69 | 9.2491 | 9.3312 | 0.0821
GEN-2018-079 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7131 | 20.7183 | 0.0052
GEN-2018-079 | 04 SOUTHEAST | 532777 | G17-009-TAP | 345 | 11.6296 | 11.6486 | 0.019
GEN-2018-079 | 04 SOUTHEAST | 532778 | GEN-2017-009 | 345 | 10.7702 | 10.7865 | 0.0163
GEN-2018-079 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.5247 | 9.5288 | 0.0041
GEN-2018-079 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.6412 | 17.7001 | 0.0589
GEN-2018-079 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 17.7105 | 17.7137 | 0.0032
GEN-2018-079 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 15.8115 | 15.814 | 0.0025
GEN-2018-079 | 04 SOUTHEAST | 532935 | MARMTNW5 | 161 | 7.6702 | 7.6716 | 0.0014
GEN-2018-079 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.2945 | 22.3364 | 0.0419
GEN-2018-079 | 04 SOUTHEAST | 533002 | DEARING4 | 138 | 9.5684 | 9.638 | 0.0696
GEN-2018-079 | 04 SOUTHEAST | 533003 | LIBERTY4 | 138 | 7.5919 | 7.623 | 0.0311
GEN-2018-079 | 04 SOUTHEAST | 533004 | MONTGOM4 | 138 | 7.2608 | 7.2876 | 0.0268
GEN-2018-079 | 04 SOUTHEAST | 533020 | NEOSHOS4 | 138 | 25.1941 | 25.2476 | 0.0535
GEN-2018-079 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 25.2407 | 25.2942 | 0.0535
GEN-2018-079 | 04 SOUTHEAST | 533022 | NEOSHON4 | 138 | 25.1214 | 25.1745 | 0.0531
GEN-2018-079 | 04 SOUTHEAST | 533688 | DEARING2 | 69 | 8.2988 | 8.3221 | 0.0233
GEN-2018-079 | 04 SOUTHEAST | 533778 | NEOSHOS2 | 69 | 23.8821 | 23.9036 | 0.0215
GEN-2018-079 | 04 SOUTHEAST | 542965 | W.GRDNR7 | 345 | 26.9269 | 26.9283 | 0.0014
GEN-2018-079 | 04 SOUTHEAST | 542968 | STILWEL7 | 345 | 25.4036 | 25.4051 | 0.0015
GEN-2018-079 | 04 SOUTHEAST | 542981 | LACYGNE7 | 345 | 25.7479 | 25.7529 | 0.005
GEN-2018-079 | 04 SOUTHEAST | 543629 | LACYGNE11_7 | 345 | 25.1165 | 25.1212 | 0.0047
GEN-2018-079 | 04 SOUTHEAST | 543632 | LACYGNE22_7 | 345 | 25.1147 | 25.1194 | 0.0047
GEN-2018-079 | 04 SOUTHEAST | 543659 | LACYGNE2 | 69 | 2.8502 | 2.8502 | 0
GEN-2018-079 | 04 SOUTHEAST | 543667 | LAC3_STAR7 | 345 | 0.6722 | 0.6723 | 0.0001
GEN-2018-079 | 04 SOUTHEAST | 543669 | LAC8_STAR7 | 345 | 0.6438 | 0.6438 | 0
GEN-2018-079 | 04 SOUTHEAST | 547469 | RIV4525 | 161 | 24.4936 | 24.4987 | 0.0051
GEN-2018-079 | 04 SOUTHEAST | 762680 | GEN-2018-032 | 345 | 11.7326 | 11.7586 | 0.026
GEN-2018-079 | 04 SOUTHEAST | 763109 | GEN-2018-079 | 138 | 6.526 | 7.2926 | 0.7666
GEN-2018-079 | 04 SOUTHEAST | 763113 | G18-079-TAP | 138 | 9.2756 | 10.0196 | 0.744
GEN-2018-082 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.3285 | 21.3294 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.9677 | 8.9683 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.1582 | 6.1585 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.3452 | 10.3462 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 8.8326 | 8.8358 | 0.0032
GEN-2018-082 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.5634 | 10.5636 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.5871 | 10.5879 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.3744 | 10.375 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3349 | 14.3357 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.7234 | 13.725 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.9074 | 3.9075 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.1715 | 25.1746 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.4333 | 9.4351 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 19.6479 | 19.6492 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.3506 | 16.3509 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.4516 | 20.4552 | 0.0036
GEN-2018-082 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.4208 | 21.4248 | 0.004
GEN-2018-082 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.1918 | 25.1977 | 0.0059
GEN-2018-082 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.2209 | 26.2274 | 0.0065
GEN-2018-082 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.841 | 13.8466 | 0.0056
GEN-2018-082 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.1517 | 17.1529 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6313 | 12.6325 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.0667 | 18.0696 | 0.0029
GEN-2018-082 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.7506 | 9.7512 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.299 | 13.3059 | 0.0069
GEN-2018-082 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.4829 | 21.487 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.8125 | 17.813 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2826 | 16.283 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.7404 | 29.7417 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.6902 | 19.6919 | 0.0017
GEN-2018-082 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.1367 | 31.1377 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.7694 | 15.7703 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.0237 | 21.0267 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.0242 | 52.0266 | 0.0024
GEN-2018-082 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.1121 | 33.1151 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.4059 | 30.4082 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.7338 | 30.7363 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.5708 | 23.572 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.9367 | 52.9391 | 0.0024
GEN-2018-082 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.4286 | 6.4295 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.781 | 9.7849 | 0.0039
GEN-2018-082 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.6254 | 2.6256 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 4.0463 | 4.0467 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.6918 | 6.6927 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.6054 | 3.6057 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 5.0969 | 5.0974 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 8.3778 | 8.3786 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.0754 | 7.0768 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.4733 | 7.4745 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 9.0377 | 9.0391 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.2943 | 5.2948 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.8379 | 2.838 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 510897 | LONEOAK4 | 138 | 8.8804 | 8.8834 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 510899 | MCALEST2 | 69 | 5.0405 | 5.041 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.6408 | 3.6413 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 510906 | SMCALTP4 | 138 | 8.7373 | 8.741 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.6587 | 14.8617 | 0.203
GEN-2018-082 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 10.1566 | 10.1619 | 0.0053
GEN-2018-082 | 04 SOUTHEAST | 510909 | MCALESTIND 4 | 138 | 5.8792 | 5.8815 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.6916 | 7.6927 | 0.0011
GEN-2018-082 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.612 | 13.6363 | 0.0243
GEN-2018-082 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 3.9578 | 3.9581 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.0499 | 15.0591 | 0.0092
GEN-2018-082 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 4.0527 | 4.053 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 510921 | DUSTIN-4 | 138 | 9.1495 | 9.1508 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.395 | 14.5907 | 0.1957
GEN-2018-082 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.9923 | 14.0149 | 0.0226
GEN-2018-082 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.8437 | 8.8446 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.0946 | 10.1016 | 0.007
GEN-2018-082 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.6581 | 16.6589 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 14.3362 | 14.3397 | 0.0035
GEN-2018-082 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.8237 | 6.8239 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.5854 | 10.5904 | 0.005
GEN-2018-082 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.7404 | 6.7422 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.4069 | 23.4079 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3192 | 8.3193 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.1085 | 23.1128 | 0.0043
GEN-2018-082 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.81 | 15.8268 | 0.0168
GEN-2018-082 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.2873 | 10.3152 | 0.0279
GEN-2018-082 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.616 | 19.6165 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.005 | 28.0064 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 13.8077 | 13.8079 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.747 | 21.7479 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.9765 | 32.9784 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.4982 | 23.4992 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.3313 | 28.3327 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0617 | 46.0655 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.6295 | 33.6344 | 0.0049
GEN-2018-082 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.9937 | 23.9957 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.8446 | 45.849 | 0.0044
GEN-2018-082 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.8995 | 34.9065 | 0.007
GEN-2018-082 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 33.1912 | 33.1941 | 0.0029
GEN-2018-082 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.4877 | 21.4886 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.6723 | 42.676 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.6843 | 27.6884 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.815 | 26.8185 | 0.0035
GEN-2018-082 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 40.6501 | 40.6578 | 0.0077
GEN-2018-082 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 22.0102 | 22.013 | 0.0028
GEN-2018-082 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.6326 | 42.6452 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.3336 | 26.3496 | 0.016
GEN-2018-082 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 43.2836 | 43.2875 | 0.0039
GEN-2018-082 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.713 | 34.7198 | 0.0068
GEN-2018-082 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 24.3327 | 24.3361 | 0.0034
GEN-2018-082 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.4066 | 23.4097 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.0313 | 36.0377 | 0.0064
GEN-2018-082 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.8384 | 22.841 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.6452 | 20.6472 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 31.5716 | 31.5756 | 0.004
GEN-2018-082 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 16.0667 | 16.0678 | 0.0011
GEN-2018-082 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.6823 | 14.6833 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.8988 | 16.9002 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.8057 | 4.8059 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 48.9688 | 49.0102 | 0.0414
GEN-2018-082 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8326 | 29.884 | 0.0514
GEN-2018-082 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.5003 | 4.5004 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 11.1337 | 11.1345 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.7896 | 21.7954 | 0.0058
GEN-2018-082 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.6935 | 8.6939 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.8451 | 11.8455 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.6478 | 14.6494 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.8981 | 9.8991 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 9.0452 | 9.0459 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.7919 | 10.7939 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 6.1252 | 6.1256 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 7.3521 | 7.3527 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.5549 | 8.5566 | 0.0017
GEN-2018-082 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.4525 | 6.453 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.3647 | 16.3726 | 0.0079
GEN-2018-082 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6587 | 11.6659 | 0.0072
GEN-2018-082 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.3477 | 11.3546 | 0.0069
GEN-2018-082 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.4997 | 11.5069 | 0.0072
GEN-2018-082 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 13.2843 | 13.2894 | 0.0051
GEN-2018-082 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.36 | 6.3609 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 6.2407 | 6.2419 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 7.5863 | 7.5884 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 11.0041 | 11.0069 | 0.0028
GEN-2018-082 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 18.662 | 18.6779 | 0.0159
GEN-2018-082 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.0819 | 11.0985 | 0.0166
GEN-2018-082 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 12.9023 | 12.9094 | 0.0071
GEN-2018-082 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 13.4214 | 13.4295 | 0.0081
GEN-2018-082 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 8.6152 | 8.619 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 8.6122 | 8.616 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.3874 | 9.3917 | 0.0043
GEN-2018-082 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.5801 | 7.5827 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 8.6691 | 8.6722 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 515158 | MADLIND4 | 138 | 8.0279 | 8.0311 | 0.0032
GEN-2018-082 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.6715 | 7.6738 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 8.1766 | 8.1779 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.0677 | 12.0739 | 0.0062
GEN-2018-082 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.0834 | 12.0897 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.5759 | 8.5786 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 14.0178 | 14.0223 | 0.0045
GEN-2018-082 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.9126 | 14.9149 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 17.4148 | 17.4211 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 515196 | MILLCRK4 | 138 | 9.3535 | 9.3582 | 0.0047
GEN-2018-082 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.2064 | 28.2205 | 0.0141
GEN-2018-082 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.7033 | 21.7053 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.4649 | 22.471 | 0.0061
GEN-2018-082 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.5583 | 14.5597 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.8191 | 23.8196 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.4546 | 10.455 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.727 | 8.7272 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 12.013 | 12.016 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.7379 | 12.7448 | 0.0069
GEN-2018-082 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.9894 | 14.9897 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 11.1352 | 11.1353 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.4367 | 17.4372 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.1293 | 12.1359 | 0.0066
GEN-2018-082 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.4873 | 11.5368 | 0.0495
GEN-2018-082 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.0199 | 23.0241 | 0.0042
GEN-2018-082 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 21.0536 | 21.0556 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.6281 | 40.6314 | 0.0033
GEN-2018-082 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.0185 | 22.0195 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.5682 | 10.5692 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.618 | 4.6182 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.1831 | 33.1877 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.9146 | 4.9147 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.1533 | 14.1579 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.3041 | 14.3057 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.8612 | 14.8677 | 0.0065
GEN-2018-082 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 7.7203 | 7.7224 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 3.6132 | 3.6137 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 5.96 | 5.9608 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.5886 | 16.5901 | 0.0015
GEN-2018-082 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8991 | 18.9019 | 0.0028
GEN-2018-082 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.2056 | 11.2111 | 0.0055
GEN-2018-082 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.152 | 17.1527 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.1837 | 10.1884 | 0.0047
GEN-2018-082 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 47.6528 | 47.6921 | 0.0393
GEN-2018-082 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.2113 | 7.2244 | 0.0131
GEN-2018-082 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.186 | 27.1979 | 0.0119
GEN-2018-082 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 43.3542 | 43.3629 | 0.0087
GEN-2018-082 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.8025 | 10.8056 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 6.2068 | 6.2076 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.3737 | 4.3747 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 520467 | ENOSJCT4 | 138 | 7.8693 | 7.8723 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3571 | 22.3716 | 0.0145
GEN-2018-082 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 30.2032 | 30.2082 | 0.005
GEN-2018-082 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.9157 | 10.9191 | 0.0034
GEN-2018-082 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.6217 | 22.6359 | 0.0142
GEN-2018-082 | 04 SOUTHEAST | 520972 | LEBANTP4 | 138 | 7.141 | 7.1433 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 7.0726 | 7.074 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 11.5891 | 11.5962 | 0.0071
GEN-2018-082 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.2977 | 9.302 | 0.0043
GEN-2018-082 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.8743 | 8.8763 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.8015 | 6.8029 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 11.3914 | 11.3985 | 0.0071
GEN-2018-082 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3373 | 11.3519 | 0.0146
GEN-2018-082 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.2601 | 7.2664 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.6443 | 15.6447 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.1121 | 33.1151 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.5397 | 13.5451 | 0.0054
GEN-2018-082 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.7979 | 18.8078 | 0.0099
GEN-2018-082 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 7.6852 | 7.6873 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 18.3239 | 18.3457 | 0.0218
GEN-2018-082 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 18.7354 | 18.7582 | 0.0228
GEN-2018-082 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 18.7354 | 18.7582 | 0.0228
GEN-2018-082 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.2512 | 7.2575 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 15.3048 | 15.3199 | 0.0151
GEN-2018-082 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.9142 | 5.9143 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.8994 | 1.8994 | 0
GEN-2018-082 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.8003 | 3.8035 | 0.0032
GEN-2018-082 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.6917 | 11.6957 | 0.004
GEN-2018-082 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.6264 | 11.6304 | 0.004
GEN-2018-082 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.387 | 22.391 | 0.004
GEN-2018-082 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.428 | 11.4288 | 0.0008
GEN-2018-082 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 18.1828 | 18.2043 | 0.0215
GEN-2018-082 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 16.2769 | 16.2801 | 0.0032
GEN-2018-082 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 6.2921 | 6.2937 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.5025 | 9.71 | 0.2075
GEN-2018-082 | 04 SOUTHEAST | 763164 | GEN-2018-088 | 345 | 12.7858 | 12.7922 | 0.0064
GEN-2018-082 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0693 | 7.0695 | 0.0002
GEN-2018-088 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 5.026 | 5.026 | 0
GEN-2018-088 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 5925 | ERCOTMAINBUS | 345 | 5.026 | 5.026 | 0
GEN-2018-088 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.3326 | 20.3346 | 0.002
GEN-2018-088 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.1406 | 10.1423 | 0.0017
GEN-2018-088 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2638 | 14.2643 | 0.0005
GEN-2018-088 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 3.0789 | 3.0793 | 0.0004
GEN-2018-088 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.6742 | 12.6758 | 0.0016
GEN-2018-088 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.4818 | 15.4829 | 0.0011
GEN-2018-088 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.9599 | 8.9683 | 0.0084
GEN-2018-088 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 2.9532 | 2.9537 | 0.0005
GEN-2018-088 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 15.3003 | 15.3108 | 0.0105
GEN-2018-088 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.1549 | 6.1585 | 0.0036
GEN-2018-088 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.3358 | 10.3462 | 0.0104
GEN-2018-088 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.5678 | 5.5693 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.5772 | 10.5879 | 0.0107
GEN-2018-088 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.8083 | 3.809 | 0.0007
GEN-2018-088 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.4659 | 7.4681 | 0.0022
GEN-2018-088 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.3659 | 10.375 | 0.0091
GEN-2018-088 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3249 | 14.3357 | 0.0108
GEN-2018-088 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.706 | 13.725 | 0.019
GEN-2018-088 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.9065 | 3.9075 | 0.001
GEN-2018-088 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.1248 | 25.1746 | 0.0498
GEN-2018-088 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.405 | 9.4351 | 0.0301
GEN-2018-088 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 19.6281 | 19.6492 | 0.0211
GEN-2018-088 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.828 | 3.8293 | 0.0013
GEN-2018-088 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.6212 | 18.6252 | 0.004
GEN-2018-088 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.3554 | 20.3593 | 0.0039
GEN-2018-088 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.2795 | 24.2849 | 0.0054
GEN-2018-088 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.7846 | 11.786 | 0.0014
GEN-2018-088 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.5717 | 32.584 | 0.0123
GEN-2018-088 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.3411 | 16.3509 | 0.0098
GEN-2018-088 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.7186 | 17.7221 | 0.0035
GEN-2018-088 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.3975 | 23.4033 | 0.0058
GEN-2018-088 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.3941 | 20.4552 | 0.0611
GEN-2018-088 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 12.0136 | 12.0214 | 0.0078
GEN-2018-088 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 19.328 | 19.3541 | 0.0261
GEN-2018-088 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.3588 | 21.4248 | 0.066
GEN-2018-088 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.4941 | 7.4979 | 0.0038
GEN-2018-088 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.6034 | 7.6071 | 0.0037
GEN-2018-088 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.6368 | 6.639 | 0.0022
GEN-2018-088 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 11.5329 | 11.5465 | 0.0136
GEN-2018-088 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.0997 | 25.1977 | 0.098
GEN-2018-088 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.1196 | 26.2274 | 0.1078
GEN-2018-088 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.7484 | 13.8466 | 0.0982
GEN-2018-088 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.6094 | 14.6381 | 0.0287
GEN-2018-088 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.2711 | 11.2861 | 0.015
GEN-2018-088 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.1341 | 17.1529 | 0.0188
GEN-2018-088 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6129 | 12.6325 | 0.0196
GEN-2018-088 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 16.4544 | 16.4716 | 0.0172
GEN-2018-088 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 16.4164 | 16.4338 | 0.0174
GEN-2018-088 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.0705 | 8.0726 | 0.0021
GEN-2018-088 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8383 | 7.8425 | 0.0042
GEN-2018-088 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.0217 | 18.0696 | 0.0479
GEN-2018-088 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.7417 | 9.7512 | 0.0095
GEN-2018-088 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.8175 | 7.8218 | 0.0043
GEN-2018-088 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 9.7944 | 9.7963 | 0.0019
GEN-2018-088 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.0942 | 18.105 | 0.0108
GEN-2018-088 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.038 | 13.3059 | 0.2679
GEN-2018-088 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.3605 | 9.3631 | 0.0026
GEN-2018-088 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.8471 | 7.8489 | 0.0018
GEN-2018-088 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.5659 | 13.568 | 0.0021
GEN-2018-088 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 11.0301 | 11.033 | 0.0029
GEN-2018-088 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.8219 | 7.8236 | 0.0017
GEN-2018-088 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3631 | 21.487 | 0.1239
GEN-2018-088 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.9437 | 6.9448 | 0.0011
GEN-2018-088 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.3421 | 7.3436 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.3523 | 17.3566 | 0.0043
GEN-2018-088 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.887 | 9.8889 | 0.0019
GEN-2018-088 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.8821 | 42.9056 | 0.0235
GEN-2018-088 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.7978 | 17.813 | 0.0152
GEN-2018-088 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.6922 | 12.6962 | 0.004
GEN-2018-088 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 35.0361 | 35.0519 | 0.0158
GEN-2018-088 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.5858 | 12.5878 | 0.002
GEN-2018-088 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6625 | 8.665 | 0.0025
GEN-2018-088 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.5811 | 16.5931 | 0.012
GEN-2018-088 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.0811 | 8.0832 | 0.0021
GEN-2018-088 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4084 | 19.4132 | 0.0048
GEN-2018-088 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.44 | 17.4436 | 0.0036
GEN-2018-088 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 25.4167 | 25.4249 | 0.0082
GEN-2018-088 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2723 | 16.283 | 0.0107
GEN-2018-088 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.9981 | 20.0032 | 0.0051
GEN-2018-088 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.494 | 10.4975 | 0.0035
GEN-2018-088 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.704 | 29.7417 | 0.0377
GEN-2018-088 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.6405 | 19.6919 | 0.0514
GEN-2018-088 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.6856 | 12.6887 | 0.0031
GEN-2018-088 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 14.0026 | 14.0064 | 0.0038
GEN-2018-088 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.8933 | 13.8994 | 0.0061
GEN-2018-088 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.1113 | 31.1377 | 0.0264
GEN-2018-088 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.7451 | 15.7703 | 0.0252
GEN-2018-088 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.5794 | 25.5854 | 0.006
GEN-2018-088 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.469 | 7.4703 | 0.0013
GEN-2018-088 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.9821 | 11.9882 | 0.0061
GEN-2018-088 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.7288 | 7.7299 | 0.0011
GEN-2018-088 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.0656 | 6.0672 | 0.0016
GEN-2018-088 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4687 | 12.4753 | 0.0066
GEN-2018-088 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.3059 | 5.3078 | 0.0019
GEN-2018-088 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.4262 | 6.4295 | 0.0033
GEN-2018-088 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.7726 | 9.7849 | 0.0123
GEN-2018-088 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.6251 | 2.6256 | 0.0005
GEN-2018-088 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 4.0457 | 4.0467 | 0.001
GEN-2018-088 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.6899 | 6.6927 | 0.0028
GEN-2018-088 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.6049 | 3.6057 | 0.0008
GEN-2018-088 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 5.0958 | 5.0974 | 0.0016
GEN-2018-088 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.072 | 7.0768 | 0.0048
GEN-2018-088 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.47 | 7.4745 | 0.0045
GEN-2018-088 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 9.0334 | 9.0391 | 0.0057
GEN-2018-088 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.2933 | 5.2948 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.8377 | 2.838 | 0.0003
GEN-2018-088 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.6398 | 3.6413 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.8503 | 14.8617 | 0.0114
GEN-2018-088 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.6891 | 7.6927 | 0.0036
GEN-2018-088 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.5552 | 13.6363 | 0.0811
GEN-2018-088 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 3.9572 | 3.9581 | 0.0009
GEN-2018-088 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.0298 | 15.0591 | 0.0293
GEN-2018-088 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 4.0521 | 4.053 | 0.0009
GEN-2018-088 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.5797 | 14.5907 | 0.011
GEN-2018-088 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.0132 | 14.0149 | 0.0017
GEN-2018-088 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.1009 | 10.1016 | 0.0007
GEN-2018-088 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.589 | 10.5904 | 0.0014
GEN-2018-088 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.8239 | 15.8268 | 0.0029
GEN-2018-088 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.3112 | 10.3152 | 0.004
GEN-2018-088 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.6339 | 33.6344 | 0.0005
GEN-2018-088 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.6756 | 42.676 | 0.0004
GEN-2018-088 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.6881 | 27.6884 | 0.0003
GEN-2018-088 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.8182 | 26.8185 | 0.0003
GEN-2018-088 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.6441 | 42.6452 | 0.0011
GEN-2018-088 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.3482 | 26.3496 | 0.0014
GEN-2018-088 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 49.0064 | 49.0102 | 0.0038
GEN-2018-088 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8803 | 29.884 | 0.0037
GEN-2018-088 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.7948 | 21.7954 | 0.0006
GEN-2018-088 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.7936 | 10.7939 | 0.0003
GEN-2018-088 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.6643 | 11.6659 | 0.0016
GEN-2018-088 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.5056 | 11.5069 | 0.0013
GEN-2018-088 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 18.6736 | 18.6779 | 0.0043
GEN-2018-088 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.0936 | 11.0985 | 0.0049
GEN-2018-088 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.3907 | 9.3917 | 0.001
GEN-2018-088 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.2196 | 28.2205 | 0.0009
GEN-2018-088 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.5338 | 11.5368 | 0.003
GEN-2018-088 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.1572 | 14.1579 | 0.0007
GEN-2018-088 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 47.6885 | 47.6921 | 0.0036
GEN-2018-088 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.2225 | 7.2244 | 0.0019
GEN-2018-088 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.1969 | 27.1979 | 0.001
GEN-2018-088 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.7981 | 10.8056 | 0.0075
GEN-2018-088 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 6.205 | 6.2076 | 0.0026
GEN-2018-088 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.3334 | 22.3716 | 0.0382
GEN-2018-088 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.9114 | 10.9191 | 0.0077
GEN-2018-088 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.5989 | 22.6359 | 0.037
GEN-2018-088 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 7.0712 | 7.074 | 0.0028
GEN-2018-088 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.8708 | 8.8763 | 0.0055
GEN-2018-088 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.8003 | 6.8029 | 0.0026
GEN-2018-088 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3113 | 11.3519 | 0.0406
GEN-2018-088 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.2604 | 7.2664 | 0.006
GEN-2018-088 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.782 | 18.8078 | 0.0258
GEN-2018-088 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 18.7567 | 18.7582 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 18.7567 | 18.7582 | 0.0015
GEN-2018-088 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.2515 | 7.2575 | 0.006
GEN-2018-088 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.9143 | 5.9143 | 0
GEN-2018-088 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.803 | 3.8035 | 0.0005
GEN-2018-088 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.4156 | 11.4288 | 0.0132
GEN-2018-088 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.4156 | 11.4288 | 0.0132
GEN-2018-088 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 15.9306 | 15.9408 | 0.0102
GEN-2018-088 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.7053 | 9.71 | 0.0047
GEN-2018-088 | 04 SOUTHEAST | 763164 | GEN-2018-088 | 345 | 12.524 | 12.7922 | 0.2682
GEN-2018-106 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 5.026 | 5.026 | 0
GEN-2018-106 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 303302 | 3MINDEN_LG | 115 | 5.75 | 5.7515 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 337351 | 3SAILES! | 115 | 6.1543 | 6.1555 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 337360 | 3ADA_LA | 115 | 5.6631 | 5.6644 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! | 115 | 7.0087 | 7.0114 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 337362 | 3LA_ORD_PLNT | 115 | 4.565 | 4.5661 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.2772 | 20.3346 | 0.0574
GEN-2018-106 | 04 SOUTHEAST | 337364 | 3CULLEN | 115 | 8.6476 | 8.6583 | 0.0107
GEN-2018-106 | 04 SOUTHEAST | 337365 | 3SPRINGHILL | 115 | 9.9853 | 9.9963 | 0.011
GEN-2018-106 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE | 115 | 6.0614 | 6.0639 | 0.0025
GEN-2018-106 | 04 SOUTHEAST | 337367 | 3ARCADIA | 115 | 5.5884 | 5.5891 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 337368 | 8MT_OLIVE% | 500 | 12.077 | 12.0796 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 337369 | 6MT_OLIVE% | 230 | 14.3571 | 14.3589 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.0891 | 10.1423 | 0.0532
GEN-2018-106 | 04 SOUTHEAST | 337413 | 8STERLING2% | 500 | 20.1079 | 20.1092 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337415 | 3STERLING% | 115 | 37.033 | 37.034 | 0.001
GEN-2018-106 | 04 SOUTHEAST | 337420 | 8STERLING% | 500 | 20.1079 | 20.1092 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337427 | 8PERRYVILLE% | 500 | 19.7989 | 19.8002 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337500 | 3TAYLOR | 115 | 7.3024 | 7.3068 | 0.0044
GEN-2018-106 | 04 SOUTHEAST | 337514 | 3MACEDONA | 115 | 6.5945 | 6.597 | 0.0025
GEN-2018-106 | 04 SOUTHEAST | 337515 | 8MCNEIL% | 500 | 14.5204 | 14.5231 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 337516 | 3MCNEIL! | 115 | 25.202 | 25.2064 | 0.0044
GEN-2018-106 | 04 SOUTHEAST | 337524 | 3KERLIN+ | 115 | 7.3756 | 7.3769 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337526 | 3EMERSON! | 115 | 6.0115 | 6.013 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 337537 | 3SMACKOVER+ | 115 | 9.5332 | 9.5335 | 0.0003
GEN-2018-106 | 04 SOUTHEAST | 337539 | 3EL DORADO! | 115 | 29.3473 | 29.3499 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 337540 | 3ELD DONAN | 115 | 15.1675 | 15.1683 | 0.0008
GEN-2018-106 | 04 SOUTHEAST | 337553 | 3ELDORADO.E! | 115 | 13.8674 | 13.8679 | 0.0005
GEN-2018-106 | 04 SOUTHEAST | 337560 | 3ELD QUINN | 115 | 28.5725 | 28.575 | 0.0025
GEN-2018-106 | 04 SOUTHEAST | 337561 | 8EL DORADO% | 500 | 27.7949 | 27.806 | 0.0111
GEN-2018-106 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2501 | 14.2643 | 0.0142
GEN-2018-106 | 04 SOUTHEAST | 337643 | 8SHERIDAN% | 500 | 28.0095 | 28.0111 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 337651 | 8WHT BLUFF% | 500 | 27.8501 | 27.8509 | 0.0008
GEN-2018-106 | 04 SOUTHEAST | 337754 | 8ETTA% | 500 | 19.0664 | 19.0675 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337763 | 8MAGNETCOVE% | 500 | 22.5891 | 22.5902 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337808 | 8MABELVALE% | 500 | 27.7018 | 27.7027 | 0.0009
GEN-2018-106 | 04 SOUTHEAST | 338440 | 8PANDA% | 500 | 27.728 | 27.7391 | 0.0111
GEN-2018-106 | 04 SOUTHEAST | 500140 | CARROLL6 | 230 | 13.8531 | 13.8633 | 0.0102
GEN-2018-106 | 04 SOUTHEAST | 500150 | CARROLL4 | 138 | 13.4977 | 13.5038 | 0.0061
GEN-2018-106 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.648 | 12.6758 | 0.0278
GEN-2018-106 | 04 SOUTHEAST | 500255 | REDBAYOU_6 | 230 | 10.7668 | 10.7755 | 0.0087
GEN-2018-106 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.4634 | 15.4829 | 0.0195
GEN-2018-106 | 04 SOUTHEAST | 500430 | IPAPER 4 | 138 | 5.7081 | 5.7112 | 0.0031
GEN-2018-106 | 04 SOUTHEAST | 500465 | 6LAYFLD | 230 | 16.1289 | 16.1339 | 0.005
GEN-2018-106 | 04 SOUTHEAST | 500525 | MANCOMP 6 | 230 | 8.7621 | 8.7673 | 0.0052
GEN-2018-106 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.7228 | 13.725 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.1695 | 25.1746 | 0.0051
GEN-2018-106 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.4324 | 9.4351 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 507710 | ARSHILL2 | 69 | 28.6373 | 28.6909 | 0.0536
GEN-2018-106 | 04 SOUTHEAST | 507711 | ARSHILL4 | 138 | 26.0328 | 26.1164 | 0.0836
GEN-2018-106 | 04 SOUTHEAST | 507717 | BROOKS 2 | 69 | 20.8369 | 20.8657 | 0.0288
GEN-2018-106 | 04 SOUTHEAST | 507726 | FLOURNY2 | 69 | 14.3345 | 14.3527 | 0.0182
GEN-2018-106 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 17.3121 | 17.3729 | 0.0608
GEN-2018-106 | 04 SOUTHEAST | 507728 | FORBNGT2 | 69 | 17.8411 | 17.8648 | 0.0237
GEN-2018-106 | 04 SOUTHEAST | 507730 | FTHUMBG2 | 69 | 18.367 | 18.3898 | 0.0228
GEN-2018-106 | 04 SOUTHEAST | 507731 | FTHUMBG4 | 138 | 20.1617 | 20.2144 | 0.0527
GEN-2018-106 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.556 | 18.6252 | 0.0692
GEN-2018-106 | 04 SOUTHEAST | 507735 | HARTSIS4 | 138 | 16.9987 | 17.0391 | 0.0404
GEN-2018-106 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 23.3622 | 23.444 | 0.0818
GEN-2018-106 | 04 SOUTHEAST | 507742 | MCWILLI4 | 138 | 22.0972 | 22.1651 | 0.0679
GEN-2018-106 | 04 SOUTHEAST | 507745 | NMARKET2 | 69 | 16.466 | 16.4833 | 0.0173
GEN-2018-106 | 04 SOUTHEAST | 507746 | PIERMNT4 | 138 | 17.0395 | 17.0791 | 0.0396
GEN-2018-106 | 04 SOUTHEAST | 507747 | PINESRD2 | 69 | 10.953 | 10.9626 | 0.0096
GEN-2018-106 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.2933 | 20.3593 | 0.066
GEN-2018-106 | 04 SOUTHEAST | 507749 | RAINES 4 | 138 | 16.905 | 16.9529 | 0.0479
GEN-2018-106 | 04 SOUTHEAST | 507754 | S SHV 2 | 69 | 18.6106 | 18.6366 | 0.026
GEN-2018-106 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.1952 | 24.2849 | 0.0897
GEN-2018-106 | 04 SOUTHEAST | 507756 | SHEDRD 2 | 69 | 17.6745 | 17.6951 | 0.0206
GEN-2018-106 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.7656 | 11.786 | 0.0204
GEN-2018-106 | 04 SOUTHEAST | 507758 | SUMMERG2 | 69 | 11.6068 | 11.6185 | 0.0117
GEN-2018-106 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.3787 | 32.584 | 0.2053
GEN-2018-106 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.18 | 16.3509 | 0.1709
GEN-2018-106 | 04 SOUTHEAST | 507762 | T70THST2 | 69 | 12.9923 | 13.0046 | 0.0123
GEN-2018-106 | 04 SOUTHEAST | 507763 | TRICHEL4 | 138 | 16.8985 | 16.9357 | 0.0372
GEN-2018-106 | 04 SOUTHEAST | 507764 | WALLAKE2 | 69 | 8.9055 | 8.911 | 0.0055
GEN-2018-106 | 04 SOUTHEAST | 507765 | WALLAKE4 | 138 | 11.229 | 11.2451 | 0.0161
GEN-2018-106 | 04 SOUTHEAST | 507766 | WATERWK2 | 69 | 17.2271 | 17.2474 | 0.0203
GEN-2018-106 | 04 SOUTHEAST | 507767 | WESTELC4 | 138 | 21.4525 | 21.5308 | 0.0783
GEN-2018-106 | 04 SOUTHEAST | 507770 | WOOLWTP2 | 69 | 11.9719 | 11.9846 | 0.0127
GEN-2018-106 | 04 SOUTHEAST | 507771 | CEDARGR4 | 138 | 23.2365 | 23.3175 | 0.081
GEN-2018-106 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.6562 | 17.7221 | 0.0659
GEN-2018-106 | 04 SOUTHEAST | 507782 | PROBSON4 | 138 | 9.0402 | 9.0504 | 0.0102
GEN-2018-106 | 04 SOUTHEAST | 507788 | MINDEN-3 | 115 | 5.6692 | 5.671 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 507789 | STLGENS4 | 138 | 25.6318 | 25.7101 | 0.0783
GEN-2018-106 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.3083 | 23.4033 | 0.095
GEN-2018-106 | 04 SOUTHEAST | 507794 | LEASIDE 2 | 69 | 13.4375 | 13.4529 | 0.0154
GEN-2018-106 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.4484 | 20.4552 | 0.0068
GEN-2018-106 | 04 SOUTHEAST | 508050 | ANDRSNC4 | 138 | 8.0511 | 8.0526 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 508052 | ATLANTA2 | 69 | 5.5546 | 5.5552 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.4962 | 7.4979 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 508059 | IPC T 4 | 138 | 8.5302 | 8.5318 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508062 | LINDEN 2 | 69 | 5.8866 | 5.8873 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.6053 | 7.6071 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.1874 | 25.1977 | 0.0103
GEN-2018-106 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.2163 | 26.2274 | 0.0111
GEN-2018-106 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.8385 | 13.8466 | 0.0081
GEN-2018-106 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6304 | 12.6325 | 0.0021
GEN-2018-106 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.0714 | 8.0726 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8405 | 7.8425 | 0.002
GEN-2018-106 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.8199 | 7.8218 | 0.0019
GEN-2018-106 | 04 SOUTHEAST | 508286 | CAMPCOR4 | 138 | 8.564 | 8.5669 | 0.0029
GEN-2018-106 | 04 SOUTHEAST | 508295 | LSREC 2 | 69 | 7.6517 | 7.6531 | 0.0014
GEN-2018-106 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 9.7941 | 9.7963 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.0899 | 18.105 | 0.0151
GEN-2018-106 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.2967 | 13.3059 | 0.0092
GEN-2018-106 | 04 SOUTHEAST | 508310 | PETTY 4 | 138 | 8.375 | 8.3778 | 0.0028
GEN-2018-106 | 04 SOUTHEAST | 508312 | PITTSB_2 | 69 | 8.6842 | 8.6857 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.3596 | 9.3631 | 0.0035
GEN-2018-106 | 04 SOUTHEAST | 508320 | LONSTAR2 | 69 | 8.2284 | 8.23 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.8463 | 7.8489 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.5651 | 13.568 | 0.0029
GEN-2018-106 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 11.0292 | 11.033 | 0.0038
GEN-2018-106 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.821 | 7.8236 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.4387 | 21.487 | 0.0483
GEN-2018-106 | 04 SOUTHEAST | 508368 | SCROGNSSW4 | 138 | 6.075 | 6.0763 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.9433 | 6.9448 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.3417 | 7.3436 | 0.0019
GEN-2018-106 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.3458 | 17.3566 | 0.0108
GEN-2018-106 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.8862 | 9.8889 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.8589 | 42.9056 | 0.0467
GEN-2018-106 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.7928 | 17.813 | 0.0202
GEN-2018-106 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.691 | 12.6962 | 0.0052
GEN-2018-106 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 35.0171 | 35.0519 | 0.0348
GEN-2018-106 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.5699 | 12.5878 | 0.0179
GEN-2018-106 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 13.9427 | 13.9574 | 0.0147
GEN-2018-106 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6621 | 8.665 | 0.0029
GEN-2018-106 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.577 | 16.5931 | 0.0161
GEN-2018-106 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 18.1671 | 18.1739 | 0.0068
GEN-2018-106 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 23.1424 | 23.1578 | 0.0154
GEN-2018-106 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.0803 | 8.0832 | 0.0029
GEN-2018-106 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4044 | 19.4132 | 0.0088
GEN-2018-106 | 04 SOUTHEAST | 508801 | BLANCH-2 | 69 | 7.0698 | 7.073 | 0.0032
GEN-2018-106 | 04 SOUTHEAST | 508802 | BLANCHR2 | 69 | 7.9211 | 7.9252 | 0.0041
GEN-2018-106 | 04 SOUTHEAST | 508805 | LIEBERM2 | 69 | 9.3807 | 9.3865 | 0.0058
GEN-2018-106 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.3899 | 17.4436 | 0.0537
GEN-2018-106 | 04 SOUTHEAST | 508807 | LINTNRD4 | 138 | 9.2859 | 9.2989 | 0.013
GEN-2018-106 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 25.2654 | 25.4249 | 0.1595
GEN-2018-106 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 15.9356 | 16.283 | 0.3474
GEN-2018-106 | 04 SOUTHEAST | 508810 | NBENTON2 | 69 | 4.2121 | 4.2133 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 508811 | NBENTON4 | 138 | 9.6104 | 9.6245 | 0.0141
GEN-2018-106 | 04 SOUTHEAST | 508812 | OILCITY2 | 69 | 7.5386 | 7.542 | 0.0034
GEN-2018-106 | 04 SOUTHEAST | 508815 | SUPEROR2 | 69 | 7.0155 | 7.0179 | 0.0024
GEN-2018-106 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.9071 | 20.0032 | 0.0961
GEN-2018-106 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.4934 | 10.4975 | 0.0041
GEN-2018-106 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.702 | 29.7417 | 0.0397
GEN-2018-106 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.6446 | 19.6919 | 0.0473
GEN-2018-106 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.678 | 12.6887 | 0.0107
GEN-2018-106 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.9942 | 14.0064 | 0.0122
GEN-2018-106 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.8921 | 13.8994 | 0.0073
GEN-2018-106 | 04 SOUTHEAST | 508839 | WASKOM 2 | 69 | 4.653 | 4.6546 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.0868 | 31.1377 | 0.0509
GEN-2018-106 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.6903 | 15.7703 | 0.08
GEN-2018-106 | 04 SOUTHEAST | 509050 | KEATCHI4 | 138 | 8.2581 | 8.2667 | 0.0086
GEN-2018-106 | 04 SOUTHEAST | 509052 | STONWAL4 | 138 | 10.8237 | 10.8408 | 0.0171
GEN-2018-106 | 04 SOUTHEAST | 509083 | ROKHILL4 | 138 | 11.9151 | 11.9229 | 0.0078
GEN-2018-106 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.5718 | 25.5854 | 0.0136
GEN-2018-106 | 04 SOUTHEAST | 509103 | WLNTSPRINGS4 | 138 | 9.4274 | 9.4339 | 0.0065
GEN-2018-106 | 04 SOUTHEAST | 509366 | LAYFLD8 | 500 | 10.4618 | 10.4638 | 0.002
GEN-2018-106 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.4686 | 7.4703 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.9817 | 11.9882 | 0.0065
GEN-2018-106 | 04 SOUTHEAST | 509623 | LAKEPIN2 | 69 | 7.6743 | 7.6761 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.7262 | 7.7299 | 0.0037
GEN-2018-106 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.0655 | 6.0672 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4684 | 12.4753 | 0.0069
GEN-2018-106 | 04 SOUTHEAST | 509645 | DUGLASV2 | 69 | 6.6073 | 6.608 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 509664 | CHAPLHL4 | 138 | 7.5926 | 7.595 | 0.0024
GEN-2018-106 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.3069 | 5.3078 | 0.0009
GEN-2018-106 | 04 SOUTHEAST | 509668 | ROACH 2 | 69 | 6.1949 | 6.1955 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.8612 | 14.8617 | 0.0005
GEN-2018-106 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.6326 | 13.6363 | 0.0037
GEN-2018-106 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.0578 | 15.0591 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.35 | 11.3519 | 0.0019
GEN-2018-106 | 04 SOUTHEAST | 588400 | GEN-2016-167 | 138 | 10.1946 | 10.2112 | 0.0166
GEN-2018-106 | 04 SOUTHEAST | 588404 | G16-167-TAP | 138 | 10.2994 | 10.3163 | 0.0169
GEN-2018-106 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 15.5933 | 15.9408 | 0.3475
GEN-2018-106 | 04 SOUTHEAST | 763164 | GEN-2018-088 | 345 | 12.7837 | 12.7922 | 0.0085
GEN-2018-115 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 14.856 | 14.8617 | 0.0057
GEN-2018-115 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.2081 | 10.2119 | 0.0038
GEN-2018-115 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.3004 | 8.3103 | 0.0099
GEN-2018-115 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0796 | 9.0915 | 0.0119
GEN-2018-115 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.6051 | 12.6482 | 0.0431
GEN-2018-115 | 04 SOUTHEAST | 511429 | L AIRGS4 | 138 | 12.1541 | 12.1939 | 0.0398
GEN-2018-115 | 04 SOUTHEAST | 511430 | LWS N4 | 138 | 10.9414 | 10.976 | 0.0346
GEN-2018-115 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.6873 | 11.7262 | 0.0389
GEN-2018-115 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.4895 | 9.497 | 0.0075
GEN-2018-115 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.9607 | 19.0628 | 0.1021
GEN-2018-115 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.1897 | 12.232 | 0.0423
GEN-2018-115 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.0971 | 8.0995 | 0.0024
GEN-2018-115 | 04 SOUTHEAST | 511450 | CORNVIL2 | 69 | 6.7706 | 6.7718 | 0.0012
GEN-2018-115 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.8915 | 4.893 | 0.0015
GEN-2018-115 | 04 SOUTHEAST | 511452 | DUNCAN-2 | 69 | 7.0306 | 7.0333 | 0.0027
GEN-2018-115 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.7556 | 6.7625 | 0.0069
GEN-2018-115 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.3359 | 5.3615 | 0.0256
GEN-2018-115 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.0858 | 6.09 | 0.0042
GEN-2018-115 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.4549 | 16.4903 | 0.0354
GEN-2018-115 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.9569 | 26.1825 | 0.2256
GEN-2018-115 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 14.0269 | 14.3397 | 0.3128
GEN-2018-115 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.1921 | 8.2004 | 0.0083
GEN-2018-115 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.1648 | 7.1715 | 0.0067
GEN-2018-115 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 12.2805 | 12.3239 | 0.0434
GEN-2018-115 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 6.0481 | 6.0515 | 0.0034
GEN-2018-115 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.9658 | 13.0164 | 0.0506
GEN-2018-115 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.3986 | 4.399 | 0.0004
GEN-2018-115 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 33.603 | 33.6469 | 0.0439
GEN-2018-115 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.693 | 11.6979 | 0.0049
GEN-2018-115 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.442 | 10.4605 | 0.0185
GEN-2018-115 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.9153 | 8.9218 | 0.0065
GEN-2018-115 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 13.4372 | 13.4863 | 0.0491
GEN-2018-115 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 22.6247 | 22.7882 | 0.1635
GEN-2018-115 | 04 SOUTHEAST | 511500 | CACHE4 | 138 | 8.7591 | 8.7757 | 0.0166
GEN-2018-115 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.7123 | 4.7152 | 0.0029
GEN-2018-115 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 12.3098 | 12.3541 | 0.0443
GEN-2018-115 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 13.0065 | 13.052 | 0.0455
GEN-2018-115 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.648 | 12.6924 | 0.0444
GEN-2018-115 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.8148 | 8.8212 | 0.0064
GEN-2018-115 | 04 SOUTHEAST | 511525 | LDISPOS2 | 69 | 5.0942 | 5.0964 | 0.0022
GEN-2018-115 | 04 SOUTHEAST | 511526 | L-RLITP2 | 69 | 7.4993 | 7.5037 | 0.0044
GEN-2018-115 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 12.3269 | 12.3714 | 0.0445
GEN-2018-115 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 8.8753 | 8.8983 | 0.023
GEN-2018-115 | 04 SOUTHEAST | 511552 | DUNCHERTP4 | 138 | 6.5348 | 6.5409 | 0.0061
GEN-2018-115 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.8298 | 10.8358 | 0.006
GEN-2018-115 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.6659 | 11.6695 | 0.0036
GEN-2018-115 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.3639 | 10.3817 | 0.0178
GEN-2018-115 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.3212 | 5.3467 | 0.0255
GEN-2018-115 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.5023 | 10.5904 | 0.0881
GEN-2018-115 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.7106 | 6.7422 | 0.0316
GEN-2018-115 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.0719 | 23.1128 | 0.0409
GEN-2018-115 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.8179 | 15.8268 | 0.0089
GEN-2018-115 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.3031 | 10.3152 | 0.0121
GEN-2018-115 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.622 | 33.6344 | 0.0124
GEN-2018-115 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.835 | 45.849 | 0.014
GEN-2018-115 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.8823 | 34.9065 | 0.0242
GEN-2018-115 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.336 | 26.3496 | 0.0136
GEN-2018-115 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 18.6552 | 18.6779 | 0.0227
GEN-2018-115 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.0706 | 11.0985 | 0.0279
GEN-2018-115 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 12.9006 | 12.9094 | 0.0088
GEN-2018-115 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 13.418 | 13.4295 | 0.0115
GEN-2018-115 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.0666 | 12.0739 | 0.0073
GEN-2018-115 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 22.9836 | 23.0241 | 0.0405
GEN-2018-115 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.6698 | 7.6727 | 0.0029
GEN-2018-115 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.1728 | 33.1877 | 0.0149
GEN-2018-115 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.2907 | 14.3057 | 0.015
GEN-2018-115 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 7.7196 | 7.7224 | 0.0028
GEN-2018-115 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.5849 | 16.5901 | 0.0052
GEN-2018-115 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8063 | 18.9019 | 0.0956
GEN-2018-115 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.114 | 33.1612 | 0.0472
GEN-2018-115 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.0668 | 10.074 | 0.0072
GEN-2018-115 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.2187 | 7.2244 | 0.0057
GEN-2018-115 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.1805 | 27.1979 | 0.0174
GEN-2018-115 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 43.3501 | 43.3629 | 0.0128
GEN-2018-115 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 25.7811 | 25.8019 | 0.0208
GEN-2018-115 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.0927 | 13.0961 | 0.0034
GEN-2018-115 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.9405 | 14.944 | 0.0035
GEN-2018-115 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 35.5258 | 35.5649 | 0.0391
GEN-2018-115 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.7378 | 18.749 | 0.0112
GEN-2018-115 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.3758 | 11.3804 | 0.0046
GEN-2018-115 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.4338 | 8.4354 | 0.0016
GEN-2018-115 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.4431 | 9.4445 | 0.0014
GEN-2018-115 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 29.8392 | 29.8734 | 0.0342
GEN-2018-115 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 6.6694 | 6.6705 | 0.0011
GEN-2018-115 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 5.8884 | 5.89 | 0.0016
GEN-2018-115 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.3488 | 11.3519 | 0.0031
GEN-2018-115 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.0661 | 21.0701 | 0.004
GEN-2018-115 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 13.231 | 13.2359 | 0.0049
GEN-2018-115 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 13.1443 | 13.1491 | 0.0048
GEN-2018-115 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.7262 | 9.7266 | 0.0004
GEN-2018-115 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.9756 | 6.9843 | 0.0087
GEN-2018-115 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.7429 | 9.7544 | 0.0115
GEN-2018-115 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.2604 | 7.2664 | 0.006
GEN-2018-115 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.3233 | 9.3338 | 0.0105
GEN-2018-115 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 10.9405 | 10.9982 | 0.0577
GEN-2018-115 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.5805 | 15.7013 | 0.1208
GEN-2018-115 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.2075 | 11.2689 | 0.0614
GEN-2018-115 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.3461 | 9.353 | 0.0069
GEN-2018-115 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.5432 | 11.5539 | 0.0107
GEN-2018-115 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 3.8115 | 3.8247 | 0.0132
GEN-2018-115 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.2515 | 7.2575 | 0.006
GEN-2018-115 | 04 SOUTHEAST | 590001 | OKLEHV24 | 138 | 5.1705 | 5.1705 | 0
GEN-2018-115 | 04 SOUTHEAST | 590003 | OKLEHV14 | 138 | 5.2556 | 5.2556 | 0
GEN-2018-115 | 04 SOUTHEAST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
GEN-2018-115 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.8125 | 10.8184 | 0.0059
GEN-2018-115 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.8021 | 3.8035 | 0.0014
GEN-2018-115 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.545 | 11.6957 | 0.1507
GEN-2018-115 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.4814 | 11.6304 | 0.149
GEN-2018-115 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.3113 | 22.3494 | 0.0381
GEN-2018-115 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.3527 | 22.391 | 0.0383
GEN-2018-115 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.759 | 7.764 | 0.005
GEN-2018-115 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6249 | 5.6275 | 0.0026
GEN-2018-115 | 04 SOUTHEAST | 762460 | GEN-2018-015 | 345 | 4.6555 | 4.6653 | 0.0098
GEN-2018-115 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 4.6645 | 4.6743 | 0.0098
GEN-2018-115 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 6.2664 | 6.2937 | 0.0273
GEN-2018-115 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 13.7646 | 14.0778 | 0.3132
GEN-2019-002 | 04 SOUTHEAST | 300069 | 5CHOTEAU1 | 161 | 42.9297 | 43.0266 | 0.0969
GEN-2019-002 | 04 SOUTHEAST | 300146 | 4SKIAETP | 138 | 7.2571 | 7.2581 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7137 | 15.7161 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 24.8163 | 24.8788 | 0.0625
GEN-2019-002 | 04 SOUTHEAST | 300741 | 5SPORTSMAN | 161 | 41.2645 | 41.3518 | 0.0873
GEN-2019-002 | 04 SOUTHEAST | 300767 | 5BRIGGS | 161 | 7.6333 | 7.6361 | 0.0028
GEN-2019-002 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.8075 | 12.8088 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 300955 | 2COWETA | 69 | 2.6128 | 2.613 | 0.0002
GEN-2019-002 | 04 SOUTHEAST | 300960 | 2LOWERY | 69 | 4.9022 | 4.903 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 300962 | 2PEGGS | 69 | 6.263 | 6.2644 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 300968 | 2SLEEPYH | 69 | 5.0545 | 5.0552 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 300972 | 2WAGNERW | 69 | 4.805 | 4.8056 | 0.0006
GEN-2019-002 | 04 SOUTHEAST | 300973 | 2WHITETP | 69 | 6.8698 | 6.8709 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 300975 | 2HULBERT | 69 | 6.676 | 6.6772 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 300992 | 2COLINS | 69 | 10.4085 | 10.4098 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 300993 | 5ELMCRK | 161 | 13.681 | 13.6887 | 0.0077
GEN-2019-002 | 04 SOUTHEAST | 300997 | 5KETONVL | 161 | 11.1213 | 11.127 | 0.0057
GEN-2019-002 | 04 SOUTHEAST | 300998 | 2OWASSO | 69 | 6.9661 | 6.9666 | 0.0005
GEN-2019-002 | 04 SOUTHEAST | 301006 | 2VERA | 69 | 6.4149 | 6.4154 | 0.0005
GEN-2019-002 | 04 SOUTHEAST | 301307 | 5PARK | 161 | 9.5945 | 9.599 | 0.0045
GEN-2019-002 | 04 SOUTHEAST | 301344 | 5CDRCRST | 161 | 11.2525 | 11.2666 | 0.0141
GEN-2019-002 | 04 SOUTHEAST | 301345 | 2CDRCRST | 69 | 8.1304 | 8.1329 | 0.0025
GEN-2019-002 | 04 SOUTHEAST | 301348 | 5CHOTEAU2 | 161 | 42.9297 | 43.0266 | 0.0969
GEN-2019-002 | 04 SOUTHEAST | 301451 | 2GRAY TP | 69 | 7.8366 | 7.8381 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 301452 | 2GRAY | 69 | 6.4184 | 6.4194 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 301453 | 2ZENA TP | 69 | 5.9793 | 5.9801 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 301460 | 2CLEORA | 69 | 4.052 | 4.0523 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 301472 | 2PARK | 69 | 9.4094 | 9.4111 | 0.0017
GEN-2019-002 | 04 SOUTHEAST | 504191 | HWY59 5 | 161 | 16.2098 | 16.2106 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 505558 | MUSKTAP5 | 161 | 14.6104 | 14.6148 | 0.0044
GEN-2019-002 | 04 SOUTHEAST | 505560 | FT GIB 5 | 161 | 10.9527 | 10.957 | 0.0043
GEN-2019-002 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 34.8717 | 34.8857 | 0.014
GEN-2019-002 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.8751 | 15.884 | 0.0089
GEN-2019-002 | 04 SOUTHEAST | 506979 | SHIPERD7 | 345 | 10.6683 | 10.672 | 0.0037
GEN-2019-002 | 04 SOUTHEAST | 509714 | CIP 4 | 138 | 14.1628 | 14.1648 | 0.002
GEN-2019-002 | 04 SOUTHEAST | 509720 | LLANE-W4 | 138 | 20.4565 | 20.4634 | 0.0069
GEN-2019-002 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.6498 | 12.6509 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 509722 | SPNKY CK4 | 138 | 31.3363 | 31.3547 | 0.0184
GEN-2019-002 | 04 SOUTHEAST | 509723 | TER-NIT4 | 138 | 13.6699 | 13.6728 | 0.0029
GEN-2019-002 | 04 SOUTHEAST | 509725 | PCATOSA4 | 138 | 11.826 | 11.8283 | 0.0023
GEN-2019-002 | 04 SOUTHEAST | 509728 | LLANE-E4 | 138 | 20.5563 | 20.5625 | 0.0062
GEN-2019-002 | 04 SOUTHEAST | 509736 | INOLA 4 | 138 | 8.4017 | 8.4034 | 0.0017
GEN-2019-002 | 04 SOUTHEAST | 509752 | INOLATP4 | 138 | 9.8796 | 9.882 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 509770 | LLAN WT4 | 138 | 25.2492 | 25.2598 | 0.0106
GEN-2019-002 | 04 SOUTHEAST | 509771 | LLAN ET4 | 138 | 25.2301 | 25.2395 | 0.0094
GEN-2019-002 | 04 SOUTHEAST | 509779 | MAYO--N4 | 138 | 24.1536 | 24.1577 | 0.0041
GEN-2019-002 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 24.5899 | 24.5941 | 0.0042
GEN-2019-002 | 04 SOUTHEAST | 509787 | DAWSN-N4 | 138 | 18.3433 | 18.3482 | 0.0049
GEN-2019-002 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 37.0537 | 37.0804 | 0.0267
GEN-2019-002 | 04 SOUTHEAST | 509791 | DAWSON-2 | 69 | 10.4761 | 10.4772 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 509794 | BCIRCLE2 | 69 | 9.4903 | 9.4912 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 509799 | CATOOSA2 | 69 | 10.6056 | 10.6066 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 509803 | DAWSONT4 | 138 | 12.6252 | 12.6279 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 28.1805 | 28.1935 | 0.013
GEN-2019-002 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.1459 | 50.1538 | 0.0079
GEN-2019-002 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.8081 | 36.8184 | 0.0103
GEN-2019-002 | 04 SOUTHEAST | 509835 | TERNITP4 | 138 | 16.5296 | 16.5339 | 0.0043
GEN-2019-002 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 19.6851 | 19.6891 | 0.004
GEN-2019-002 | 04 SOUTHEAST | 509841 | PCATSAT4 | 138 | 18.4817 | 18.4873 | 0.0056
GEN-2019-002 | 04 SOUTHEAST | 509843 | OWASO2_4 | 138 | 14.5369 | 14.5398 | 0.0029
GEN-2019-002 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.8086 | 24.8173 | 0.0087
GEN-2019-002 | 04 SOUTHEAST | 509854 | VERDIGS4 | 138 | 14.2294 | 14.232 | 0.0026
GEN-2019-002 | 04 SOUTHEAST | 509864 | CLARTOK4 | 138 | 14.224 | 14.2266 | 0.0026
GEN-2019-002 | 04 SOUTHEAST | 509886 | E41ST_W4 | 138 | 22.2982 | 22.3031 | 0.0049
GEN-2019-002 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 17.4937 | 17.4973 | 0.0036
GEN-2019-002 | 04 SOUTHEAST | 509892 | 141PINE4 | 138 | 21.1627 | 21.1699 | 0.0072
GEN-2019-002 | 04 SOUTHEAST | 509899 | BIRDCREE-4 | 138 | 17.8976 | 17.9029 | 0.0053
GEN-2019-002 | 04 SOUTHEAST | 510373 | CHOUTEA4 | 138 | 7.3523 | 7.3542 | 0.0019
GEN-2019-002 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 35.8791 | 35.8883 | 0.0092
GEN-2019-002 | 04 SOUTHEAST | 510399 | LSTAR--3 | 115 | 11.2664 | 11.276 | 0.0096
GEN-2019-002 | 04 SOUTHEAST | 510416 | HUNTAP-2 | 69 | 9.268 | 9.2725 | 0.0045
GEN-2019-002 | 04 SOUTHEAST | 510423 | L GROVE3 | 115 | 17.2018 | 17.2286 | 0.0268
GEN-2019-002 | 04 SOUTHEAST | 510437 | ROCKPT-4 | 138 | 8.7651 | 8.7671 | 0.002
GEN-2019-002 | 04 SOUTHEAST | 512624 | CENTLFT2 | 69 | 11.8388 | 11.842 | 0.0032
GEN-2019-002 | 04 SOUTHEAST | 512625 | MAIDTP2 | 69 | 12.22 | 12.2296 | 0.0096
GEN-2019-002 | 04 SOUTHEAST | 512626 | MAID 2 | 69 | 14.9985 | 15.0147 | 0.0162
GEN-2019-002 | 04 SOUTHEAST | 512627 | COLINS 5 | 161 | 12.5224 | 12.5285 | 0.0061
GEN-2019-002 | 04 SOUTHEAST | 512628 | PENSA 2 | 69 | 13.8116 | 13.8166 | 0.005
GEN-2019-002 | 04 SOUTHEAST | 512629 | DRYGULCH5 | 161 | 16.1885 | 16.2311 | 0.0426
GEN-2019-002 | 04 SOUTHEAST | 512631 | MIAMI 5 | 161 | 9.7765 | 9.7787 | 0.0022
GEN-2019-002 | 04 SOUTHEAST | 512632 | AFTON 5 | 161 | 8.6397 | 8.6433 | 0.0036
GEN-2019-002 | 04 SOUTHEAST | 512633 | AFTON 2 | 69 | 10.7853 | 10.787 | 0.0017
GEN-2019-002 | 04 SOUTHEAST | 512634 | KERR GR3 | 115 | 18.3285 | 18.3593 | 0.0308
GEN-2019-002 | 04 SOUTHEAST | 512635 | KERR GR5 | 161 | 30.147 | 30.2897 | 0.1427
GEN-2019-002 | 04 SOUTHEAST | 512637 | 412SUB 5 | 161 | 12.2433 | 12.2567 | 0.0134
GEN-2019-002 | 04 SOUTHEAST | 512638 | CATSAGR5 | 161 | 24.754 | 24.7805 | 0.0265
GEN-2019-002 | 04 SOUTHEAST | 512639 | PRY0RC22 | 69 | 10.2685 | 10.274 | 0.0055
GEN-2019-002 | 04 SOUTHEAST | 512640 | OKAYGR 5 | 161 | 10.2968 | 10.3022 | 0.0054
GEN-2019-002 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 15.3595 | 15.3663 | 0.0068
GEN-2019-002 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 20.6959 | 20.7044 | 0.0085
GEN-2019-002 | 04 SOUTHEAST | 512646 | OKAYGR 2 | 69 | 12.4876 | 12.4908 | 0.0032
GEN-2019-002 | 04 SOUTHEAST | 512647 | TAHLQH 2 | 69 | 12.3331 | 12.336 | 0.0029
GEN-2019-002 | 04 SOUTHEAST | 512648 | MAID 5 | 161 | 46.1315 | 46.5904 | 0.4589
GEN-2019-002 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 27.2745 | 27.3522 | 0.0777
GEN-2019-002 | 04 SOUTHEAST | 512651 | CLARMR 5 | 161 | 13.3986 | 13.4086 | 0.01
GEN-2019-002 | 04 SOUTHEAST | 512654 | PENSA 5 | 161 | 13.515 | 13.5338 | 0.0188
GEN-2019-002 | 04 SOUTHEAST | 512655 | TAHLQH 5 | 161 | 10.7986 | 10.8042 | 0.0056
GEN-2019-002 | 04 SOUTHEAST | 512656 | GRDA1 5 | 161 | 45.6462 | 46.0394 | 0.3932
GEN-2019-002 | 04 SOUTHEAST | 512661 | CPPTAP 2 | 69 | 13.3665 | 13.3783 | 0.0118
GEN-2019-002 | 04 SOUTHEAST | 512669 | KETCHUM5 | 161 | 10.9323 | 10.943 | 0.0107
GEN-2019-002 | 04 SOUTHEAST | 512671 | HUNT 2 | 69 | 13.8287 | 13.8399 | 0.0112
GEN-2019-002 | 04 SOUTHEAST | 512679 | CLARMR 2 | 69 | 13.2443 | 13.2484 | 0.0041
GEN-2019-002 | 04 SOUTHEAST | 512681 | AMERCAST S2 | 69 | 13.7131 | 13.7259 | 0.0128
GEN-2019-002 | 04 SOUTHEAST | 512683 | AMERCAST N2 | 69 | 8.6434 | 8.6488 | 0.0054
GEN-2019-002 | 04 SOUTHEAST | 512685 | CASTING TAP2 | 69 | 9.6335 | 9.6402 | 0.0067
GEN-2019-002 | 04 SOUTHEAST | 512686 | SALINA 5 | 161 | 18.5813 | 18.6292 | 0.0479
GEN-2019-002 | 04 SOUTHEAST | 512687 | AIRPROD2 | 69 | 13.2661 | 13.2771 | 0.011
GEN-2019-002 | 04 SOUTHEAST | 512690 | WAGNRTP2 | 69 | 7.5724 | 7.5738 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 512692 | CLEORTP2 | 69 | 7.7421 | 7.7434 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 512695 | ADARNEO2 | 69 | 4.9616 | 4.9622 | 0.0006
GEN-2019-002 | 04 SOUTHEAST | 512696 | PARKER 2 | 69 | 4.5975 | 4.598 | 0.0005
GEN-2019-002 | 04 SOUTHEAST | 512697 | WAGNOR 2 | 69 | 7.4631 | 7.4645 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 512698 | REDDEN 2 | 69 | 11.0174 | 11.0261 | 0.0087
GEN-2019-002 | 04 SOUTHEAST | 512699 | PRYORCHEM2 | 69 | 13.2509 | 13.2621 | 0.0112
GEN-2019-002 | 04 SOUTHEAST | 512700 | WAGNOR 5 | 161 | 10.0241 | 10.0318 | 0.0077
GEN-2019-002 | 04 SOUTHEAST | 512703 | PARKMEDTP | 69 | 5.9779 | 5.9782 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 512704 | STIWEL5 | 161 | 5.0309 | 5.0321 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 512705 | COLLINS4 | 138 | 8.8451 | 8.8471 | 0.002
GEN-2019-002 | 04 SOUTHEAST | 512707 | CLARMR 4 | 138 | 13.8774 | 13.882 | 0.0046
GEN-2019-002 | 04 SOUTHEAST | 512714 | KANSATP5 | 161 | 12.107 | 12.1147 | 0.0077
GEN-2019-002 | 04 SOUTHEAST | 512715 | KANSAS 2 | 69 | 6.6579 | 6.6588 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 512716 | KANSAS 5 | 161 | 11.5016 | 11.5086 | 0.007
GEN-2019-002 | 04 SOUTHEAST | 512727 | GRDA1 2 | 69 | 12.6413 | 12.652 | 0.0107
GEN-2019-002 | 04 SOUTHEAST | 512742 | WMAIN ST5 | 161 | 28.9249 | 29.0894 | 0.1645
GEN-2019-002 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 15.6479 | 15.6574 | 0.0095
GEN-2019-002 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.9225 | 15.9272 | 0.0047
GEN-2019-002 | 04 SOUTHEAST | 512753 | TONNEC2 | 69 | 5.7107 | 5.7109 | 0.0002
GEN-2019-002 | 04 SOUTHEAST | 512757 | NWMAID5 | 161 | 28.6629 | 28.8265 | 0.1636
GEN-2019-002 | 04 SOUTHEAST | 512759 | WAGCTY22 | 69 | 6.0191 | 6.0199 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 512760 | GERALDGAY5 | 161 | 29.9954 | 30.1789 | 0.1835
GEN-2019-002 | 04 SOUTHEAST | 512770 | KERR BRK1 5 | 161 | 30.147 | 30.2897 | 0.1427
GEN-2019-002 | 04 SOUTHEAST | 512771 | KERR BRK4 5 | 161 | 30.147 | 30.2897 | 0.1427
GEN-2019-002 | 04 SOUTHEAST | 512801 | WAGCTY12 | 69 | 5.6323 | 5.6331 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 512804 | RDFRNTP2 | 69 | 9.5969 | 9.5988 | 0.0019
GEN-2019-002 | 04 SOUTHEAST | 512805 | SALNCRK5 | 161 | 19.2458 | 19.2979 | 0.0521
GEN-2019-002 | 04 SOUTHEAST | 512812 | ARMIN 2 | 69 | 11.3505 | 11.3581 | 0.0076
GEN-2019-002 | 04 SOUTHEAST | 512822 | TAH22CT2 | 69 | 10.8911 | 10.8935 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 512828 | UNARCO 2 | 69 | 7.5909 | 7.5923 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.059 | 26.1263 | 0.0673
GEN-2019-002 | 04 SOUTHEAST | 512870 | COLNSGR2 | 69 | 10.4086 | 10.4099 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 513008 | CLARMTP 2 | 69 | 10.9157 | 10.9184 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 513014 | CLARCTY4 2 | 69 | 6.2492 | 6.2501 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 513041 | TITANKM 2 | 69 | 6.6041 | 6.6048 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 513044 | BRIGSKM 5 | 161 | 8.7905 | 8.7943 | 0.0038
GEN-2019-002 | 04 SOUTHEAST | 513050 | LOCSTGVKM 5 | 161 | 14.2713 | 14.3018 | 0.0305
GEN-2019-002 | 04 SOUTHEAST | 513053 | FTGIBKM 2 | 69 | 8.3432 | 8.3447 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 513065 | SWAGONERKM 2 | 69 | 8.0237 | 8.0252 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 513074 | MUSKSWKM 2 | 69 | 6.3402 | 6.3406 | 0.0004
GEN-2019-002 | 04 SOUTHEAST | 513124 | OOLOGAHKM 4 | 138 | 21.1043 | 21.1093 | 0.005
GEN-2019-002 | 04 SOUTHEAST | 513129 | SEQUOYAKM 2 | 69 | 7.1922 | 7.1934 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 513570 | CHOUTEAUCRK5 | 161 | 21.377 | 21.4462 | 0.0692
GEN-2019-002 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5522 | 17.5645 | 0.0123
GEN-2019-002 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5522 | 17.5645 | 0.0123
GEN-2019-002 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.6808 | 20.7183 | 0.0375
GEN-2019-002 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 19.2465 | 19.2474 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 515527 | HWY59TP5 | 161 | 16.415 | 16.4158 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 515956 | 7CLANS 5 | 161 | 10.3 | 10.3048 | 0.0048
GEN-2019-002 | 04 SOUTHEAST | 516027 | KETOWAH5 | 161 | 13.0767 | 13.0801 | 0.0034
GEN-2019-002 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.6985 | 17.7001 | 0.0016
GEN-2019-002 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 17.7134 | 17.7137 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 549984 | BROOKLINE 7 | 345 | 12.2338 | 12.2346 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 588990 | GEN-2017-061 | 161 | 18.1198 | 18.1694 | 0.0496
GEN-2019-002 | 04 SOUTHEAST | 589110 | GEN-2017-073 | 161 | 15.0413 | 15.078 | 0.0367
GEN-2019-002 | 04 SOUTHEAST | 763472 | GEN-2019-002 | 161 | 42.6889 | 43.1471 | 0.4582
GEN-2019-012 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5632 | 10.5637 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.5361 | 11.5392 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.4684 | 7.4715 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.691 | 8.6952 | 0.0042
GEN-2019-012 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 6.4129 | 6.4152 | 0.0023
GEN-2019-012 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 5.3103 | 5.3118 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.8396 | 4.8409 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.8169 | 10.8358 | 0.0189
GEN-2019-012 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.6595 | 11.6695 | 0.01
GEN-2019-012 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.8089 | 19.811 | 0.0021
GEN-2019-012 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.0729 | 19.0785 | 0.0056
GEN-2019-012 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.6736 | 1.6738 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 5.3319 | 5.3336 | 0.0017
GEN-2019-012 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 6.0603 | 6.0625 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.5942 | 6.5948 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 5.3245 | 5.3262 | 0.0017
GEN-2019-012 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.355 | 6.3574 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 12.5024 | 12.5119 | 0.0095
GEN-2019-012 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 19.7749 | 19.8442 | 0.0693
GEN-2019-012 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 7.7128 | 7.7168 | 0.004
GEN-2019-012 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.3547 | 5.3555 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.715 | 7.7169 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.0437 | 9.0465 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.219 | 10.2279 | 0.0089
GEN-2019-012 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.6831 | 7.6915 | 0.0084
GEN-2019-012 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.1029 | 23.1128 | 0.0099
GEN-2019-012 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.4871 | 17.4894 | 0.0023
GEN-2019-012 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.9731 | 18.9757 | 0.0026
GEN-2019-012 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.0032 | 28.0064 | 0.0032
GEN-2019-012 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 32.9721 | 32.9784 | 0.0063
GEN-2019-012 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.6803 | 27.6847 | 0.0044
GEN-2019-012 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.4959 | 23.4992 | 0.0033
GEN-2019-012 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.3281 | 28.3327 | 0.0046
GEN-2019-012 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.0517 | 46.0655 | 0.0138
GEN-2019-012 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.6098 | 33.6344 | 0.0246
GEN-2019-012 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.9856 | 23.9957 | 0.0101
GEN-2019-012 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.899 | 29.903 | 0.004
GEN-2019-012 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.0455 | 20.0473 | 0.0018
GEN-2019-012 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.8348 | 45.849 | 0.0142
GEN-2019-012 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.8747 | 34.9065 | 0.0318
GEN-2019-012 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.6712 | 42.676 | 0.0048
GEN-2019-012 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 27.6837 | 27.6884 | 0.0047
GEN-2019-012 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.8146 | 26.8185 | 0.0039
GEN-2019-012 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.3434 | 26.3496 | 0.0062
GEN-2019-012 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8808 | 29.884 | 0.0032
GEN-2019-012 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4079 | 3.4094 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 20.6688 | 21.044 | 0.3752
GEN-2019-012 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.2649 | 26.42 | 0.1551
GEN-2019-012 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.7615 | 3.7622 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.2048 | 9.2222 | 0.0174
GEN-2019-012 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.0069 | 10.028 | 0.0211
GEN-2019-012 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.3373 | 17.4372 | 0.0999
GEN-2019-012 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.7846 | 19.8541 | 0.0695
GEN-2019-012 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.0143 | 23.0241 | 0.0098
GEN-2019-012 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.2142 | 12.2625 | 0.0483
GEN-2019-012 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.6643 | 7.6727 | 0.0084
GEN-2019-012 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.423 | 13.4257 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.1421 | 33.1877 | 0.0456
GEN-2019-012 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 6.941 | 6.9466 | 0.0056
GEN-2019-012 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.3021 | 14.3057 | 0.0036
GEN-2019-012 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 11.1675 | 11.2008 | 0.0333
GEN-2019-012 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.4105 | 3.4108 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.6011 | 8.6241 | 0.023
GEN-2019-012 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.5678 | 13.6283 | 0.0605
GEN-2019-012 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 9.8821 | 9.9079 | 0.0258
GEN-2019-012 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 10.9878 | 10.9906 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 12.0031 | 12.0065 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.5833 | 16.5901 | 0.0068
GEN-2019-012 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 9.7475 | 9.7725 | 0.025
GEN-2019-012 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 8.7772 | 8.7973 | 0.0201
GEN-2019-012 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.2696 | 11.3153 | 0.0457
GEN-2019-012 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 10.2983 | 10.3364 | 0.0381
GEN-2019-012 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 21.0665 | 21.0867 | 0.0202
GEN-2019-012 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 6.5136 | 6.5153 | 0.0017
GEN-2019-012 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8946 | 18.9019 | 0.0073
GEN-2019-012 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.1578 | 33.1612 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.6625 | 9.7358 | 0.0733
GEN-2019-012 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.4514 | 14.5366 | 0.0852
GEN-2019-012 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.8304 | 15.8565 | 0.0261
GEN-2019-012 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 6.9263 | 6.9318 | 0.0055
GEN-2019-012 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.1451 | 17.1527 | 0.0076
GEN-2019-012 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.1408 | 17.1484 | 0.0076
GEN-2019-012 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.5547 | 11.6634 | 0.1087
GEN-2019-012 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 13.1321 | 13.2737 | 0.1416
GEN-2019-012 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 4.9875 | 4.9886 | 0.0011
GEN-2019-012 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6563 | 4.6566 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.1115 | 17.1141 | 0.0026
GEN-2019-012 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.1892 | 27.1979 | 0.0087
GEN-2019-012 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 43.3564 | 43.3629 | 0.0065
GEN-2019-012 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 11.1356 | 11.2068 | 0.0712
GEN-2019-012 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 11.1249 | 11.1959 | 0.071
GEN-2019-012 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.4152 | 8.4179 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.2814 | 10.2903 | 0.0089
GEN-2019-012 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.9257 | 11.9398 | 0.0141
GEN-2019-012 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.5049 | 6.5074 | 0.0025
GEN-2019-012 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 20.7396 | 20.7586 | 0.019
GEN-2019-012 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 15.176 | 15.1859 | 0.0099
GEN-2019-012 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 6.9239 | 6.9267 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8623 | 6.867 | 0.0047
GEN-2019-012 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 5.9949 | 5.9959 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.619 | 5.6202 | 0.0012
GEN-2019-012 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.1909 | 8.1937 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.1249 | 9.1275 | 0.0026
GEN-2019-012 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 21.5173 | 21.5377 | 0.0204
GEN-2019-012 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 7.5084 | 7.512 | 0.0036
GEN-2019-012 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 4.0513 | 4.0519 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.8933 | 10.8989 | 0.0056
GEN-2019-012 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 8.1811 | 8.184 | 0.0029
GEN-2019-012 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.7212 | 8.7237 | 0.0025
GEN-2019-012 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 12.1724 | 12.1863 | 0.0139
GEN-2019-012 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 10.9385 | 10.9605 | 0.022
GEN-2019-012 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 10.9058 | 10.9277 | 0.0219
GEN-2019-012 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 10.7702 | 10.7916 | 0.0214
GEN-2019-012 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 6.2332 | 6.2348 | 0.0016
GEN-2019-012 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.2542 | 6.2577 | 0.0035
GEN-2019-012 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 10.684 | 10.6868 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 525213 | SWISHER 6 | 230 | 10.61 | 10.6103 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 28.613 | 28.6138 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 525828 | TUCO_INT 3 | 115 | 19.3628 | 19.3631 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.0692 | 21.0701 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 13.235 | 13.2359 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 525840 | ANTELOPE_1 6 | 230 | 20.9068 | 20.9077 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 13.1483 | 13.1491 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 525957 | HALE_WNDCL16 | 230 | 10.5181 | 10.5183 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 526161 | CARLISLE 6 | 230 | 10.5281 | 10.5282 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 526337 | JONES 6 | 230 | 16.8478 | 16.848 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 526935 | YOAKUM 6 | 230 | 19.4387 | 19.4389 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.7264 | 9.7266 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 527896 | HOBBS_INT 7 | 345 | 11.293 | 11.2932 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 11.1976 | 11.2029 | 0.0053
GEN-2019-012 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 10.6195 | 10.621 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 18.6504 | 18.6624 | 0.012
GEN-2019-012 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 6.835 | 6.8362 | 0.0012
GEN-2019-012 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.755 | 5.7558 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 17.9709 | 17.9751 | 0.0042
GEN-2019-012 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 21.317 | 21.3282 | 0.0112
GEN-2019-012 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.4303 | 13.4337 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 27.6915 | 27.6974 | 0.0059
GEN-2019-012 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.5552 | 10.5597 | 0.0045
GEN-2019-012 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.5832 | 15.5933 | 0.0101
GEN-2019-012 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.4149 | 7.4161 | 0.0012
GEN-2019-012 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.3987 | 8.4011 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.422 | 10.4287 | 0.0067
GEN-2019-012 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.3283 | 15.3616 | 0.0333
GEN-2019-012 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 10.7788 | 10.7838 | 0.005
GEN-2019-012 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.4684 | 17.482 | 0.0136
GEN-2019-012 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 9.0586 | 9.0637 | 0.0051
GEN-2019-012 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 8.6668 | 8.6715 | 0.0047
GEN-2019-012 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 8.6668 | 8.6715 | 0.0047
GEN-2019-012 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.4518 | 7.4552 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 6.9892 | 6.9922 | 0.003
GEN-2019-012 | 04 SOUTHEAST | 560071 | G16-003-TAP | 345 | 15.2253 | 15.372 | 0.1467
GEN-2019-012 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.7473 | 9.7544 | 0.0071
GEN-2019-012 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 9.3662 | 9.371 | 0.0048
GEN-2019-012 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 10.0046 | 10.0059 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 7.8689 | 7.8803 | 0.0114
GEN-2019-012 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 6.2298 | 6.2438 | 0.014
GEN-2019-012 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.6013 | 10.6923 | 0.091
GEN-2019-012 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 7.8387 | 7.8411 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.3273 | 9.3338 | 0.0065
GEN-2019-012 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 8.3096 | 8.3134 | 0.0038
GEN-2019-012 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 15.6974 | 15.7013 | 0.0039
GEN-2019-012 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.6427 | 15.6447 | 0.002
GEN-2019-012 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.3654 | 12.462 | 0.0966
GEN-2019-012 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 15.3283 | 15.3616 | 0.0333
GEN-2019-012 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.7991 | 10.8184 | 0.0193
GEN-2019-012 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.9142 | 5.9143 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 18.5573 | 18.5693 | 0.012
GEN-2019-012 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.3817 | 22.391 | 0.0093
GEN-2019-012 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.7637 | 7.764 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.6274 | 5.6275 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.5078 | 11.5098 | 0.002
GEN-2019-012 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 4.6741 | 4.6743 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.6961 | 6.7024 | 0.0063
GEN-2019-012 | 04 SOUTHEAST | 763516 | GEN-2019-011 | 345 | 9.1327 | 9.1328 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 18.114 | 18.4899 | 0.3759
GEN-2019-012 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 8.1971 | 8.2004 | 0.0033
GEN-2019-012 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.6059 | 9.6105 | 0.0046
GEN-2019-012 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.8304 | 15.8565 | 0.0261
GEN-2019-012 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.2476 | 10.2541 | 0.0065
GEN-2019-012 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0681 | 7.0695 | 0.0014
GEN-2019-012 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6639 | 5.6647 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3209 | 6.3219 | 0.001
GEN-2019-013 | 04 SOUTHEAST | 511446 | CL-AFTP4 | 138 | 6.6515 | 6.6567 | 0.0052
GEN-2019-013 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.5139 | 11.5392 | 0.0253
GEN-2019-013 | 04 SOUTHEAST | 511459 | ELKCTY-2 | 69 | 7.3268 | 7.3309 | 0.0041
GEN-2019-013 | 04 SOUTHEAST | 511485 | CLINTJC4 | 138 | 6.4905 | 6.4932 | 0.0027
GEN-2019-013 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.4405 | 7.4715 | 0.031
GEN-2019-013 | 04 SOUTHEAST | 511511 | FALCNRD4 | 138 | 8.064 | 8.0761 | 0.0121
GEN-2019-013 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.5281 | 8.6952 | 0.1671
GEN-2019-013 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 6.3259 | 6.4152 | 0.0893
GEN-2019-013 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 5.1333 | 5.3118 | 0.1785
GEN-2019-013 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.7917 | 4.8409 | 0.0492
GEN-2019-013 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.7837 | 10.8358 | 0.0521
GEN-2019-013 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.5473 | 11.6695 | 0.1222
GEN-2019-013 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 21.0328 | 21.044 | 0.0112
GEN-2019-013 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.6507 | 7.6727 | 0.022
GEN-2019-013 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8931 | 18.9019 | 0.0088
GEN-2019-013 | 04 SOUTHEAST | 521116 | REDHLSW4 | 138 | 7.2221 | 7.2289 | 0.0068
GEN-2019-013 | 04 SOUTHEAST | 523551 | HUTCHISON 6 | 230 | 7.7539 | 7.7546 | 0.0007
GEN-2019-013 | 04 SOUTHEAST | 523748 | BOWERS 3 | 115 | 7.0579 | 7.0687 | 0.0108
GEN-2019-013 | 04 SOUTHEAST | 523770 | GRAPEVINE 3 | 115 | 8.1703 | 8.1843 | 0.014
GEN-2019-013 | 04 SOUTHEAST | 523771 | GRAPEVINE 6 | 230 | 5.8938 | 5.9126 | 0.0188
GEN-2019-013 | 04 SOUTHEAST | 523772 | COBRN_CREEK3 | 115 | 3.6651 | 3.6738 | 0.0087
GEN-2019-013 | 04 SOUTHEAST | 523776 | WHEELER 3 | 115 | 6.7715 | 6.8007 | 0.0292
GEN-2019-013 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 6.1778 | 6.2348 | 0.057
GEN-2019-013 | 04 SOUTHEAST | 523796 | HOWARD 2 | 69 | 4.8624 | 4.8703 | 0.0079
GEN-2019-013 | 04 SOUTHEAST | 523797 | HOWARD 3 | 115 | 5.1983 | 5.2135 | 0.0152
GEN-2019-013 | 04 SOUTHEAST | 523977 | HARRNG_WST 6 | 230 | 27.2684 | 27.2776 | 0.0092
GEN-2019-013 | 04 SOUTHEAST | 523978 | HARRNG_MID 6 | 230 | 27.2684 | 27.2776 | 0.0092
GEN-2019-013 | 04 SOUTHEAST | 524043 | NICHOLS 3 | 115 | 30.5232 | 30.5298 | 0.0066
GEN-2019-013 | 04 SOUTHEAST | 524044 | NICHOLS 6 | 230 | 26.4111 | 26.4205 | 0.0094
GEN-2019-013 | 04 SOUTHEAST | 524088 | KIRBY 3 | 115 | 5.623 | 5.6273 | 0.0043
GEN-2019-013 | 04 SOUTHEAST | 524415 | AMA_SOUTH 6 | 230 | 13.9798 | 13.982 | 0.0022
GEN-2019-013 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.7377 | 9.7544 | 0.0167
GEN-2019-013 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.3187 | 9.3338 | 0.0151
GEN-2019-013 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.7677 | 10.8184 | 0.0507
GEN-2019-013 | 04 SOUTHEAST | 763538 | GEN-2019-013 | 230 | 3.5583 | 3.7392 | 0.1809
GEN-2019-045 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 10.8301 | 10.8358 | 0.0057
GEN-2019-045 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 11.6662 | 11.6695 | 0.0033
GEN-2019-045 | 04 SOUTHEAST | 514716 | SALINE 2 | 69 | 3.3184 | 3.3217 | 0.0033
GEN-2019-045 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 6.0609 | 6.0625 | 0.0016
GEN-2019-045 | 04 SOUTHEAST | 514777 | CLEOCOR2 | 69 | 8.5749 | 8.5815 | 0.0066
GEN-2019-045 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.5911 | 6.5948 | 0.0037
GEN-2019-045 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.3557 | 6.3574 | 0.0017
GEN-2019-045 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 12.5049 | 12.5119 | 0.007
GEN-2019-045 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 19.8096 | 19.8442 | 0.0346
GEN-2019-045 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 7.7134 | 7.7168 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.3527 | 5.3555 | 0.0028
GEN-2019-045 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.3542 | 7.3569 | 0.0027
GEN-2019-045 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.6701 | 7.7169 | 0.0468
GEN-2019-045 | 04 SOUTHEAST | 514793 | ALINE 2 | 69 | 3.6532 | 3.6555 | 0.0023
GEN-2019-045 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 8.9728 | 9.0465 | 0.0737
GEN-2019-045 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 9.9594 | 10.2279 | 0.2685
GEN-2019-045 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.6873 | 7.6915 | 0.0042
GEN-2019-045 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 33.6235 | 33.6344 | 0.0109
GEN-2019-045 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.8931 | 34.9065 | 0.0134
GEN-2019-045 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4087 | 3.4094 | 0.0007
GEN-2019-045 | 04 SOUTHEAST | 515371 | HELENAT2 | 69 | 3.3369 | 3.34 | 0.0031
GEN-2019-045 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 20.9402 | 21.044 | 0.1038
GEN-2019-045 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.3607 | 26.42 | 0.0593
GEN-2019-045 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.7616 | 3.7622 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.2156 | 9.2222 | 0.0066
GEN-2019-045 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.02 | 10.028 | 0.008
GEN-2019-045 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.408 | 17.4372 | 0.0292
GEN-2019-045 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.8195 | 19.8541 | 0.0346
GEN-2019-045 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.2484 | 12.2625 | 0.0141
GEN-2019-045 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.6701 | 7.6727 | 0.0026
GEN-2019-045 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.169 | 33.1877 | 0.0187
GEN-2019-045 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 6.9433 | 6.9466 | 0.0033
GEN-2019-045 | 04 SOUTHEAST | 515553 | CLEO PL4 | 138 | 5.5505 | 5.5531 | 0.0026
GEN-2019-045 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 11.191 | 11.2008 | 0.0098
GEN-2019-045 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.4059 | 3.4108 | 0.0049
GEN-2019-045 | 04 SOUTHEAST | 515562 | CLEOPLT4 | 138 | 6.5883 | 6.592 | 0.0037
GEN-2019-045 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.6174 | 8.6241 | 0.0067
GEN-2019-045 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.6106 | 13.6283 | 0.0177
GEN-2019-045 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.3022 | 11.3153 | 0.0131
GEN-2019-045 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 10.3255 | 10.3364 | 0.0109
GEN-2019-045 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 21.0368 | 21.0867 | 0.0499
GEN-2019-045 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 6.511 | 6.5153 | 0.0043
GEN-2019-045 | 04 SOUTHEAST | 515803 | ALINETP2 | 69 | 3.6582 | 3.6605 | 0.0023
GEN-2019-045 | 04 SOUTHEAST | 515804 | CLEOTP 2 | 69 | 7.4916 | 7.497 | 0.0054
GEN-2019-045 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.7156 | 9.7358 | 0.0202
GEN-2019-045 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.3421 | 14.5366 | 0.1945
GEN-2019-045 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.037 | 15.8565 | 0.8195
GEN-2019-045 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.1471 | 17.1527 | 0.0056
GEN-2019-045 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.6336 | 11.6634 | 0.0298
GEN-2019-045 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 13.2347 | 13.2737 | 0.039
GEN-2019-045 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 4.9877 | 4.9886 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 516025 | SUNDANC4 | 138 | 4.6488 | 4.6505 | 0.0017
GEN-2019-045 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 11.1871 | 11.2068 | 0.0197
GEN-2019-045 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 11.1763 | 11.1959 | 0.0196
GEN-2019-045 | 04 SOUTHEAST | 520407 | WINCHTP2 | 69 | 4.1422 | 4.153 | 0.0108
GEN-2019-045 | 04 SOUTHEAST | 520421 | STOCKHOLM2 | 69 | 4.1751 | 4.1767 | 0.0016
GEN-2019-045 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.4112 | 8.4179 | 0.0067
GEN-2019-045 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.0198 | 10.2903 | 0.2705
GEN-2019-045 | 04 SOUTHEAST | 520431 | CHRKCTY4 | 138 | 6.2746 | 6.3366 | 0.062
GEN-2019-045 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.4999 | 11.9398 | 0.4399
GEN-2019-045 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.437 | 6.5074 | 0.0704
GEN-2019-045 | 04 SOUTHEAST | 520454 | STALOGA2 | 69 | 4.645 | 4.6456 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 520456 | FTSPLY 2 | 69 | 6.8395 | 6.8422 | 0.0027
GEN-2019-045 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 20.7102 | 20.7586 | 0.0484
GEN-2019-045 | 04 SOUTHEAST | 520480 | CURTIS 2 | 69 | 4.1666 | 4.1674 | 0.0008
GEN-2019-045 | 04 SOUTHEAST | 520492 | NINMILE4 | 138 | 3.8359 | 3.8366 | 0.0007
GEN-2019-045 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 15.1611 | 15.1859 | 0.0248
GEN-2019-045 | 04 SOUTHEAST | 520507 | CEDRDAL4 | 138 | 4.8166 | 4.8184 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 520536 | WATNGSW4 | 138 | 7.2966 | 7.2975 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 6.9233 | 6.9267 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.7192 | 6.867 | 0.1478
GEN-2019-045 | 04 SOUTHEAST | 520806 | ALVA 2 | 69 | 6.7437 | 6.7768 | 0.0331
GEN-2019-045 | 04 SOUTHEAST | 520825 | BEAVERJ2 | 69 | 2.2924 | 2.2927 | 0.0003
GEN-2019-045 | 04 SOUTHEAST | 520843 | CANTON-2 | 69 | 4.9416 | 4.9423 | 0.0007
GEN-2019-045 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 5.9932 | 5.9959 | 0.0027
GEN-2019-045 | 04 SOUTHEAST | 520851 | CHEROKS2 | 69 | 5.4437 | 5.4587 | 0.015
GEN-2019-045 | 04 SOUTHEAST | 520855 | CLEOSW 2 | 69 | 8 | 8.0063 | 0.0063
GEN-2019-045 | 04 SOUTHEAST | 520882 | DOVERSW4 | 138 | 10.9126 | 10.914 | 0.0014
GEN-2019-045 | 04 SOUTHEAST | 520919 | FTSUPLY2 | 69 | 7.9661 | 7.9699 | 0.0038
GEN-2019-045 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.6171 | 5.6202 | 0.0031
GEN-2019-045 | 04 SOUTHEAST | 520922 | SLEEPBR4 | 138 | 4.4198 | 4.4215 | 0.0017
GEN-2019-045 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.1865 | 8.1937 | 0.0072
GEN-2019-045 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.1232 | 9.1275 | 0.0043
GEN-2019-045 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 21.4854 | 21.5377 | 0.0523
GEN-2019-045 | 04 SOUTHEAST | 521001 | MORWODS4 | 138 | 5.3609 | 5.3618 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 521015 | OKEENE 2 | 69 | 6.707 | 6.7084 | 0.0014
GEN-2019-045 | 04 SOUTHEAST | 521016 | OKEENE 4 | 138 | 7.352 | 7.3536 | 0.0016
GEN-2019-045 | 04 SOUTHEAST | 521064 | TALOGA 2 | 69 | 8.5367 | 8.5389 | 0.0022
GEN-2019-045 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 7.5084 | 7.512 | 0.0036
GEN-2019-045 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 4.0513 | 4.0519 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.8933 | 10.8989 | 0.0056
GEN-2019-045 | 04 SOUTHEAST | 521128 | NINMLTP4 | 138 | 4.9378 | 4.939 | 0.0012
GEN-2019-045 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 8.1808 | 8.184 | 0.0032
GEN-2019-045 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.7198 | 8.7237 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 521200 | DRIFTWD4 | 138 | 6.0788 | 6.1223 | 0.0435
GEN-2019-045 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 13.2356 | 13.2359 | 0.0003
GEN-2019-045 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 11.1935 | 11.2029 | 0.0094
GEN-2019-045 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 10.6176 | 10.621 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 18.6347 | 18.6624 | 0.0277
GEN-2019-045 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 6.8334 | 6.8362 | 0.0028
GEN-2019-045 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.754 | 5.7558 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 17.9656 | 17.9751 | 0.0095
GEN-2019-045 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 21.3022 | 21.3282 | 0.026
GEN-2019-045 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.4247 | 13.4337 | 0.009
GEN-2019-045 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 27.6837 | 27.6974 | 0.0137
GEN-2019-045 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.5497 | 10.5597 | 0.01
GEN-2019-045 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.5708 | 15.5933 | 0.0225
GEN-2019-045 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.4133 | 7.4161 | 0.0028
GEN-2019-045 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.3957 | 8.4011 | 0.0054
GEN-2019-045 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.4153 | 10.4287 | 0.0134
GEN-2019-045 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.287 | 15.3616 | 0.0746
GEN-2019-045 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 10.7748 | 10.7838 | 0.009
GEN-2019-045 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.4516 | 17.482 | 0.0304
GEN-2019-045 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 9.0537 | 9.0637 | 0.01
GEN-2019-045 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 8.6622 | 8.6715 | 0.0093
GEN-2019-045 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 8.6622 | 8.6715 | 0.0093
GEN-2019-045 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.4484 | 7.4552 | 0.0068
GEN-2019-045 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 6.9862 | 6.9922 | 0.006
GEN-2019-045 | 04 SOUTHEAST | 560071 | G16-003-TAP | 345 | 15.3312 | 15.372 | 0.0408
GEN-2019-045 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 9.7521 | 9.7544 | 0.0023
GEN-2019-045 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 9.3618 | 9.371 | 0.0092
GEN-2019-045 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 10.003 | 10.0059 | 0.0029
GEN-2019-045 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 6.2398 | 6.2438 | 0.004
GEN-2019-045 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.6673 | 10.6923 | 0.025
GEN-2019-045 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 7.8349 | 7.8411 | 0.0062
GEN-2019-045 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 8.3062 | 8.3134 | 0.0072
GEN-2019-045 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.4352 | 12.462 | 0.0268
GEN-2019-045 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 15.287 | 15.3616 | 0.0746
GEN-2019-045 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 10.8126 | 10.8184 | 0.0058
GEN-2019-045 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 18.5418 | 18.5693 | 0.0275
GEN-2019-045 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.6882 | 6.7024 | 0.0142
GEN-2019-045 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 18.4102 | 18.4899 | 0.0797
GEN-2019-045 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 8.1943 | 8.2004 | 0.0061
GEN-2019-045 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.6019 | 9.6105 | 0.0086
GEN-2019-045 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.037 | 15.8565 | 0.8195
GEN-2019-045 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.2412 | 10.2541 | 0.0129
GEN-2019-045 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.0689 | 7.0695 | 0.0006
GEN-2019-065 | 04 SOUTHEAST | 508545 | HOWELL 2 | 69 | 6.8737 | 6.9148 | 0.0411
GEN-2019-065 | 04 SOUTHEAST | 508546 | KILGORE2 | 69 | 7.4855 | 7.5487 | 0.0632
GEN-2019-065 | 04 SOUTHEAST | 508548 | KNOXLEE4 | 138 | 26.3572 | 27.0164 | 0.6592
GEN-2019-065 | 04 SOUTHEAST | 508558 | MONROCR2 | 69 | 7.1724 | 7.2068 | 0.0344
GEN-2019-065 | 04 SOUTHEAST | 508565 | SABINE 2 | 69 | 6.9576 | 6.9902 | 0.0326
GEN-2019-065 | 04 SOUTHEAST | 508574 | WHITNEY2 | 69 | 22.3951 | 22.5274 | 0.1323
GEN-2019-065 | 04 SOUTHEAST | 509062 | FRIARSW4 | 138 | 8.3277 | 8.9976 | 0.6699
GEN-2019-065 | 04 SOUTHEAST | 509063 | FRIRSWR4 | 138 | 8.5175 | 9.0879 | 0.5704
GEN-2019-065 | 04 SOUTHEAST | 509067 | KILGORR4 | 138 | 9.8333 | 10.2283 | 0.395
GEN-2019-065 | 04 SOUTHEAST | 509069 | LEVERET4 | 138 | 8.4163 | 8.9785 | 0.5622
GEN-2019-065 | 04 SOUTHEAST | 509072 | LONDON 4 | 138 | 8.3698 | 9.2448 | 0.875
GEN-2019-065 | 04 SOUTHEAST | 509073 | MONROER4 | 138 | 12.336 | 12.7176 | 0.3816
GEN-2019-065 | 04 SOUTHEAST | 509075 | NWHENDR2 | 69 | 9.0164 | 9.2546 | 0.2382
GEN-2019-065 | 04 SOUTHEAST | 509076 | NWHENDR4 | 138 | 8.8941 | 9.3974 | 0.5033
GEN-2019-065 | 04 SOUTHEAST | 509077 | OAK1HIL4 | 138 | 9.1315 | 9.59 | 0.4585
GEN-2019-065 | 04 SOUTHEAST | 509079 | OVERTON2 | 69 | 7.3794 | 7.5818 | 0.2024
GEN-2019-065 | 04 SOUTHEAST | 509080 | OVERTON4 | 138 | 8.5529 | 9.3794 | 0.8265
GEN-2019-065 | 04 SOUTHEAST | 509089 | TURNERT2 | 69 | 2.831 | 2.8618 | 0.0308
GEN-2019-065 | 04 SOUTHEAST | 509242 | JACKSNV4 | 138 | 3.5293 | 3.6078 | 0.0785
GEN-2019-065 | 04 SOUTHEAST | 509320 | ALTO 4 | 138 | 3.0792 | 3.1042 | 0.025
GEN-2019-065 | 04 SOUTHEAST | 509324 | PINEGRV4 | 138 | 3.1028 | 3.1461 | 0.0433
GEN-2019-065 | 04 SOUTHEAST | 509326 | SLOCUM 4 | 138 | 3.8654 | 3.8817 | 0.0163
GEN-2019-065 | 04 SOUTHEAST | 763010 | G19-065-TAP | 138 | 8.4038 | 9.3177 | 0.9139
GEN-2019-065 | 04 SOUTHEAST | 763934 | GEN-2019-065 | 138 | 8.2752 | 9.191 | 0.9158
GEN-2018-089 | 05 SOUTWEST | 515458 | BORDER 7 | 345 | 7.434 | 7.4346 | 0.0006
GEN-2018-089 | 05 SOUTWEST | 515554 | BVRCNTY7 | 345 | 12.8481 | 12.8495 | 0.0014
GEN-2018-089 | 05 SOUTWEST | 515590 | PALDR2W7 | 345 | 11.1679 | 11.1689 | 0.001
GEN-2018-089 | 05 SOUTWEST | 515618 | BALKOW 7 | 345 | 10.9813 | 10.9824 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 515677 | BADGER 7 | 345 | 12.4976 | 12.4986 | 0.001
GEN-2018-089 | 05 SOUTWEST | 522800 | MU-TULIA 3 | 115 | 5.459 | 5.4701 | 0.0111
GEN-2018-089 | 05 SOUTWEST | 523093 | HITCHLAND 3 | 115 | 17.518 | 17.5185 | 0.0005
GEN-2018-089 | 05 SOUTWEST | 523095 | HITCHLAND 6 | 230 | 14.0616 | 14.0634 | 0.0018
GEN-2018-089 | 05 SOUTWEST | 523097 | HITCHLAND 7 | 345 | 13.5603 | 13.5626 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 523101 | NOBLE_WND 7 | 345 | 13.513 | 13.5153 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 523103 | NOBLE_WND 3 | 115 | 10.8081 | 10.8085 | 0.0004
GEN-2018-089 | 05 SOUTWEST | 523111 | NOVUS1 3 | 115 | 8.0737 | 8.0739 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 523112 | NOVUS1 7 | 345 | 13.329 | 13.3313 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 523155 | OCHILTREE 6 | 230 | 4.3759 | 4.376 | 0.0001
GEN-2018-089 | 05 SOUTWEST | 523177 | RB-SPURLCK+3 | 115 | 5.7122 | 5.7129 | 0.0007
GEN-2018-089 | 05 SOUTWEST | 523186 | SPEARMAN 3 | 115 | 9.3096 | 9.3102 | 0.0006
GEN-2018-089 | 05 SOUTWEST | 523215 | GEN-2011-022 | 345 | 9.828 | 9.8291 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 523217 | RB-KEMP 3 | 115 | 4.0336 | 4.0341 | 0.0005
GEN-2018-089 | 05 SOUTWEST | 523220 | XIT_INTG 3 | 115 | 6.1243 | 6.1256 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 523221 | XIT_INTG 6 | 230 | 3.3268 | 3.3277 | 0.0009
GEN-2018-089 | 05 SOUTWEST | 523228 | DALLAM 3 | 115 | 6.1608 | 6.1621 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 523256 | ETTER 3 | 115 | 5.5724 | 5.5732 | 0.0008
GEN-2018-089 | 05 SOUTWEST | 523266 | PRINGLE 3 | 115 | 11.7211 | 11.7228 | 0.0017
GEN-2018-089 | 05 SOUTWEST | 523267 | PRINGLE 6 | 230 | 4.75 | 4.7509 | 0.0009
GEN-2018-089 | 05 SOUTWEST | 523277 | VALERO 3 | 115 | 9.5379 | 9.5403 | 0.0024
GEN-2018-089 | 05 SOUTWEST | 523304 | MOORE_W 3 | 115 | 10.4568 | 10.4597 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 523308 | MOORE_E 3 | 115 | 10.4568 | 10.4597 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 523309 | MOORE_CNTY 6 | 230 | 6.98 | 6.9826 | 0.0026
GEN-2018-089 | 05 SOUTWEST | 523318 | DUMAS_19ST 3 | 115 | 6.0772 | 6.0783 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8028 | 9.8065 | 0.0037
GEN-2018-089 | 05 SOUTWEST | 523323 | MCDWL_CREEK6 | 230 | 9.4034 | 9.4109 | 0.0075
GEN-2018-089 | 05 SOUTWEST | 523325 | EXELL 3 | 115 | 6.3271 | 6.3286 | 0.0015
GEN-2018-089 | 05 SOUTWEST | 523332 | EXELL_TP 3 | 115 | 7.7399 | 7.7422 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 523339 | FAIN 3 | 115 | 8.5999 | 8.6026 | 0.0027
GEN-2018-089 | 05 SOUTWEST | 523377 | RIVERVIEW 3 | 115 | 14.0828 | 14.0861 | 0.0033
GEN-2018-089 | 05 SOUTWEST | 523410 | CRMWA_#4 3 | 115 | 10.1552 | 10.1581 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 523478 | Q_RYTON_TP 3 | 115 | 12.4839 | 12.4851 | 0.0012
GEN-2018-089 | 05 SOUTWEST | 523544 | HUTCH_N 3 | 115 | 16.4937 | 16.4981 | 0.0044
GEN-2018-089 | 05 SOUTWEST | 523546 | HUTCH_S 3 | 115 | 16.4937 | 16.4981 | 0.0044
GEN-2018-089 | 05 SOUTWEST | 523551 | HUTCHISON 6 | 230 | 7.8567 | 7.8596 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 523770 | GRAPEVINE 3 | 115 | 8.2845 | 8.2855 | 0.001
GEN-2018-089 | 05 SOUTWEST | 523771 | GRAPEVINE 6 | 230 | 5.9348 | 5.9359 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 523777 | WHEELER 6 | 230 | 6.1626 | 6.1632 | 0.0006
GEN-2018-089 | 05 SOUTWEST | 523817 | MIDSTRM_TP 3 | 115 | 4.9464 | 4.9468 | 0.0004
GEN-2018-089 | 05 SOUTWEST | 523823 | CARPENTER 7 | 345 | 6.5515 | 6.5517 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 523853 | FINNEY 7 | 345 | 8.9671 | 8.9671 | 0
GEN-2018-089 | 05 SOUTWEST | 523869 | CHAN+TASCOS6 | 230 | 4.4541 | 4.4561 | 0.002
GEN-2018-089 | 05 SOUTWEST | 523959 | POTTER_CO 6 | 230 | 22.9918 | 23.0545 | 0.0627
GEN-2018-089 | 05 SOUTWEST | 523961 | POTTER_CO 7 | 345 | 11.0446 | 11.0581 | 0.0135
GEN-2018-089 | 05 SOUTWEST | 523977 | HARRNG_WST 6 | 230 | 28.0964 | 28.1552 | 0.0588
GEN-2018-089 | 05 SOUTWEST | 523978 | HARRNG_MID 6 | 230 | 28.0964 | 28.1552 | 0.0588
GEN-2018-089 | 05 SOUTWEST | 523979 | HARRNG_EST 6 | 230 | 28.0964 | 28.1552 | 0.0588
GEN-2018-089 | 05 SOUTWEST | 524007 | ROLLHILLS 3 | 115 | 20.2635 | 20.2803 | 0.0168
GEN-2018-089 | 05 SOUTWEST | 524009 | CHERRY 3 | 115 | 19.3819 | 19.3973 | 0.0154
GEN-2018-089 | 05 SOUTWEST | 524010 | ROLLHILLS 6 | 230 | 20.9864 | 21.0269 | 0.0405
GEN-2018-089 | 05 SOUTWEST | 524016 | ASARCO 3 | 115 | 27.1763 | 27.1991 | 0.0228
GEN-2018-089 | 05 SOUTWEST | 524018 | ASARCO_TP 3 | 115 | 29.4586 | 29.4848 | 0.0262
GEN-2018-089 | 05 SOUTWEST | 524043 | NICHOLS 3 | 115 | 31.4746 | 31.5046 | 0.03
GEN-2018-089 | 05 SOUTWEST | 524044 | NICHOLS 6 | 230 | 27.1949 | 27.2494 | 0.0545
GEN-2018-089 | 05 SOUTWEST | 524058 | WHITAKER 3 | 115 | 22.5684 | 22.5871 | 0.0187
GEN-2018-089 | 05 SOUTWEST | 524079 | CONWAY 3 | 115 | 5.249 | 5.2496 | 0.0006
GEN-2018-089 | 05 SOUTWEST | 524105 | NORTHWEST 2 | 69 | 6.4993 | 6.5006 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 524106 | NORTHWEST 3 | 115 | 12.0699 | 12.0769 | 0.007
GEN-2018-089 | 05 SOUTWEST | 524124 | BUSH 3 | 115 | 7.5173 | 7.52 | 0.0027
GEN-2018-089 | 05 SOUTWEST | 524136 | HASTINGS 3 | 115 | 14.8227 | 14.8321 | 0.0094
GEN-2018-089 | 05 SOUTWEST | 524162 | EAST_PLANT 3 | 115 | 23.4384 | 23.4629 | 0.0245
GEN-2018-089 | 05 SOUTWEST | 524163 | EAST_PLANT 6 | 230 | 14.8478 | 14.8642 | 0.0164
GEN-2018-089 | 05 SOUTWEST | 524224 | MANHATTAN 3 | 115 | 17.7075 | 17.7242 | 0.0167
GEN-2018-089 | 05 SOUTWEST | 524243 | OUTPOST 3 | 115 | 9.9132 | 9.9189 | 0.0057
GEN-2018-089 | 05 SOUTWEST | 524249 | SUNSET 3 | 115 | 12.2476 | 12.2553 | 0.0077
GEN-2018-089 | 05 SOUTWEST | 524266 | BUSHLAND 3 | 115 | 9.7415 | 9.747 | 0.0055
GEN-2018-089 | 05 SOUTWEST | 524267 | BUSHLAND 6 | 230 | 10.3964 | 10.4097 | 0.0133
GEN-2018-089 | 05 SOUTWEST | 524276 | WILDOR_WND 6 | 230 | 5.4118 | 5.4149 | 0.0031
GEN-2018-089 | 05 SOUTWEST | 524290 | WILDOR2_JUS6 | 230 | 7.1967 | 7.2026 | 0.0059
GEN-2018-089 | 05 SOUTWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3316 | 5.3342 | 0.0026
GEN-2018-089 | 05 SOUTWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3316 | 5.3342 | 0.0026
GEN-2018-089 | 05 SOUTWEST | 524322 | GEORGIA 3 | 115 | 17.4138 | 17.4315 | 0.0177
GEN-2018-089 | 05 SOUTWEST | 524338 | SOUTHEAST 3 | 115 | 11.5855 | 11.5942 | 0.0087
GEN-2018-089 | 05 SOUTWEST | 524341 | PRESTONWEST3 | 115 | 13.5605 | 13.571 | 0.0105
GEN-2018-089 | 05 SOUTWEST | 524345 | OSAGE 3 | 115 | 14.2824 | 14.2927 | 0.0103
GEN-2018-089 | 05 SOUTWEST | 524364 | RANDALL 3 | 115 | 21.3628 | 21.3922 | 0.0294
GEN-2018-089 | 05 SOUTWEST | 524365 | RANDALL 6 | 230 | 15.1164 | 15.143 | 0.0266
GEN-2018-089 | 05 SOUTWEST | 524377 | FARMERS 3 | 115 | 15.9489 | 15.9637 | 0.0148
GEN-2018-089 | 05 SOUTWEST | 524387 | CRSE_HINDTP3 | 115 | 15.9613 | 15.9762 | 0.0149
GEN-2018-089 | 05 SOUTWEST | 524397 | ARROWHEAD 3 | 115 | 14.1203 | 14.1311 | 0.0108
GEN-2018-089 | 05 SOUTWEST | 524404 | OWENSCORN 3 | 115 | 15.5111 | 15.525 | 0.0139
GEN-2018-089 | 05 SOUTWEST | 524414 | AMA_SOUTH 3 | 115 | 17.3693 | 17.3868 | 0.0175
GEN-2018-089 | 05 SOUTWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2119 | 14.2417 | 0.0298
GEN-2018-089 | 05 SOUTWEST | 524522 | CANYON_E_TP3 | 115 | 6.1152 | 6.1181 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 524530 | PALO_DURO 3 | 115 | 7.0404 | 7.0465 | 0.0061
GEN-2018-089 | 05 SOUTWEST | 524544 | SPRING_DRW 3 | 115 | 6.6692 | 6.6719 | 0.0027
GEN-2018-089 | 05 SOUTWEST | 524560 | ARNOT 3 | 115 | 10.8891 | 10.8958 | 0.0067
GEN-2018-089 | 05 SOUTWEST | 524567 | NE_HEREFORD3 | 115 | 9.8589 | 9.8695 | 0.0106
GEN-2018-089 | 05 SOUTWEST | 524575 | DS-#25+ 3 | 115 | 10.1461 | 10.1573 | 0.0112
GEN-2018-089 | 05 SOUTWEST | 524606 | HEREFORD 3 | 115 | 10.8934 | 10.9063 | 0.0129
GEN-2018-089 | 05 SOUTWEST | 524619 | DFSMTH_EST 3 | 115 | 11.7259 | 11.741 | 0.0151
GEN-2018-089 | 05 SOUTWEST | 524622 | DFSMTH_WST 3 | 115 | 11.7288 | 11.7439 | 0.0151
GEN-2018-089 | 05 SOUTWEST | 524623 | DEAFSMITH 6 | 230 | 8.4095 | 8.4216 | 0.0121
GEN-2018-089 | 05 SOUTWEST | 524630 | TIERABLANCA3 | 115 | 12.0502 | 12.0663 | 0.0161
GEN-2018-089 | 05 SOUTWEST | 524679 | DIMMIT_S_TP2 | 69 | 3.064 | 3.0658 | 0.0018
GEN-2018-089 | 05 SOUTWEST | 524688 | DS-#3 2 | 69 | 3.1074 | 3.1093 | 0.0019
GEN-2018-089 | 05 SOUTWEST | 524694 | DS-#22 3 | 115 | 4.8373 | 4.8446 | 0.0073
GEN-2018-089 | 05 SOUTWEST | 524721 | DS-#15&#19+2 | 69 | 3.7916 | 3.7943 | 0.0027
GEN-2018-089 | 05 SOUTWEST | 524728 | DS-CASTRO 2 | 69 | 4.4062 | 4.41 | 0.0038
GEN-2018-089 | 05 SOUTWEST | 524734 | DS-#21 3 | 115 | 9.6056 | 9.6335 | 0.0279
GEN-2018-089 | 05 SOUTWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7276 | 8.7426 | 0.015
GEN-2018-089 | 05 SOUTWEST | 524746 | CASTRO_CNTY3 | 115 | 10.1286 | 10.1608 | 0.0322
GEN-2018-089 | 05 SOUTWEST | 524757 | BETHEL_COL13 | 115 | 8.5125 | 8.533 | 0.0205
GEN-2018-089 | 05 SOUTWEST | 524768 | PLSNT_HILL 3 | 115 | 10.9203 | 10.9246 | 0.0043
GEN-2018-089 | 05 SOUTWEST | 524770 | PLSNT_HILL 6 | 230 | 6.6367 | 6.6398 | 0.0031
GEN-2018-089 | 05 SOUTWEST | 524822 | CURRY 3 | 115 | 11.3868 | 11.3923 | 0.0055
GEN-2018-089 | 05 SOUTWEST | 524874 | OASIS 3 | 115 | 9.9809 | 9.9847 | 0.0038
GEN-2018-089 | 05 SOUTWEST | 524875 | OASIS 6 | 230 | 8.081 | 8.0854 | 0.0044
GEN-2018-089 | 05 SOUTWEST | 524885 | SN_JUAN_TAP6 | 230 | 5.0159 | 5.0165 | 0.0006
GEN-2018-089 | 05 SOUTWEST | 524908 | ROOSEVELT 3 | 115 | 11.0158 | 11.0207 | 0.0049
GEN-2018-089 | 05 SOUTWEST | 524909 | ROOSEVELT 6 | 230 | 9.9332 | 9.9404 | 0.0072
GEN-2018-089 | 05 SOUTWEST | 524924 | PORTALES 3 | 115 | 7.6861 | 7.6884 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 525018 | MULESHVALLY3 | 115 | 5.1382 | 5.1411 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 525019 | MULSHVLY_TP3 | 115 | 5.468 | 5.4712 | 0.0032
GEN-2018-089 | 05 SOUTWEST | 525027 | BAILEYCO 2 | 69 | 4.878 | 4.8795 | 0.0015
GEN-2018-089 | 05 SOUTWEST | 525028 | BAILEYCO 3 | 115 | 5.3639 | 5.3669 | 0.003
GEN-2018-089 | 05 SOUTWEST | 525050 | BC-KELLEY +3 | 115 | 7.8546 | 7.8695 | 0.0149
GEN-2018-089 | 05 SOUTWEST | 525056 | BC-EARTH 3 | 115 | 8.1959 | 8.2104 | 0.0145
GEN-2018-089 | 05 SOUTWEST | 525116 | DS-#12 2 | 69 | 2.5625 | 2.5638 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 525124 | HART_INDUST3 | 115 | 7.7085 | 7.7574 | 0.0489
GEN-2018-089 | 05 SOUTWEST | 525132 | LC-N_OLTON 2 | 69 | 3.0771 | 3.0794 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 525153 | HAPPY_INT 2 | 69 | 5.165 | 5.1697 | 0.0047
GEN-2018-089 | 05 SOUTWEST | 525154 | HAPPY_INT 3 | 115 | 5.75 | 5.7597 | 0.0097
GEN-2018-089 | 05 SOUTWEST | 525179 | TULIA_TP 3 | 115 | 6.7767 | 6.7936 | 0.0169
GEN-2018-089 | 05 SOUTWEST | 525191 | KRESS_INT 2 | 69 | 4.4326 | 4.4382 | 0.0056
GEN-2018-089 | 05 SOUTWEST | 525192 | KRESS_INT 3 | 115 | 12.2619 | 12.3354 | 0.0735
GEN-2018-089 | 05 SOUTWEST | 525203 | SW-KRESS 2 | 69 | 4.4326 | 4.4382 | 0.0056
GEN-2018-089 | 05 SOUTWEST | 525212 | SWISHER 3 | 115 | 11.7109 | 11.7821 | 0.0712
GEN-2018-089 | 05 SOUTWEST | 525213 | SWISHER 6 | 230 | 10.7031 | 10.8441 | 0.141
GEN-2018-089 | 05 SOUTWEST | 525224 | KRESS_RURL 2 | 69 | 2.5668 | 2.5688 | 0.002
GEN-2018-089 | 05 SOUTWEST | 525225 | KRESS_RURAL3 | 115 | 6.2444 | 6.2603 | 0.0159
GEN-2018-089 | 05 SOUTWEST | 525226 | KRS_RURL_TP3 | 115 | 6.7315 | 6.7499 | 0.0184
GEN-2018-089 | 05 SOUTWEST | 525249 | LH-PLW&FNY+2 | 69 | 1.6684 | 1.6692 | 0.0008
GEN-2018-089 | 05 SOUTWEST | 525257 | N_PLAINVEW 3 | 115 | 5.5473 | 5.5568 | 0.0095
GEN-2018-089 | 05 SOUTWEST | 525272 | KISER 3 | 115 | 5.569 | 5.5782 | 0.0092
GEN-2018-089 | 05 SOUTWEST | 525291 | PLAINVW_TP 2 | 69 | 6.3695 | 6.3758 | 0.0063
GEN-2018-089 | 05 SOUTWEST | 525298 | S_PLAINVEW 2 | 69 | 2.6934 | 2.6946 | 0.0012
GEN-2018-089 | 05 SOUTWEST | 525325 | COX 2 | 69 | 3.2902 | 3.2917 | 0.0015
GEN-2018-089 | 05 SOUTWEST | 525326 | COX 3 | 115 | 6.6216 | 6.6317 | 0.0101
GEN-2018-089 | 05 SOUTWEST | 525393 | ROCKYFORD 3 | 115 | 8.5333 | 8.5483 | 0.015
GEN-2018-089 | 05 SOUTWEST | 525404 | LC-OLTON 2 | 69 | 4.2553 | 4.2597 | 0.0044
GEN-2018-089 | 05 SOUTWEST | 525413 | LAMTON 2 | 69 | 4.8245 | 4.8301 | 0.0056
GEN-2018-089 | 05 SOUTWEST | 525414 | LAMTON 3 | 115 | 7.8218 | 7.8453 | 0.0235
GEN-2018-089 | 05 SOUTWEST | 525425 | CORNER 2 | 69 | 3.663 | 3.6652 | 0.0022
GEN-2018-089 | 05 SOUTWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8037 | 5.8091 | 0.0054
GEN-2018-089 | 05 SOUTWEST | 525440 | LC-S_OLTON+3 | 115 | 7.2485 | 7.2647 | 0.0162
GEN-2018-089 | 05 SOUTWEST | 525446 | RKYFORD_TP 3 | 115 | 9.4415 | 9.4599 | 0.0184
GEN-2018-089 | 05 SOUTWEST | 525453 | HALE_CNTY 2 | 69 | 6.7547 | 6.7619 | 0.0072
GEN-2018-089 | 05 SOUTWEST | 525454 | HALE_CNTY 3 | 115 | 10.5309 | 10.5599 | 0.029
GEN-2018-089 | 05 SOUTWEST | 525460 | NEWHART 3 | 115 | 14.9415 | 15.1909 | 0.2494
GEN-2018-089 | 05 SOUTWEST | 525461 | NEWHART 6 | 230 | 11.027 | 11.4527 | 0.4257
GEN-2018-089 | 05 SOUTWEST | 525480 | PLANT_X 3 | 115 | 15.4689 | 15.507 | 0.0381
GEN-2018-089 | 05 SOUTWEST | 525481 | PLANT_X 6 | 230 | 23.7414 | 23.8515 | 0.1101
GEN-2018-089 | 05 SOUTWEST | 525531 | TOLK 6 | 230 | 30.6423 | 30.7299 | 0.0876
GEN-2018-089 | 05 SOUTWEST | 525549 | TOLK 7 | 345 | 13.448 | 13.4662 | 0.0182
GEN-2018-089 | 05 SOUTWEST | 525584 | BLUECLDCOL 6 | 230 | 10.7099 | 10.7184 | 0.0085
GEN-2018-089 | 05 SOUTWEST | 525585 | BLUECLDPOI 6 | 230 | 11.3046 | 11.3141 | 0.0095
GEN-2018-089 | 05 SOUTWEST | 525586 | NEEDMORE 6 | 230 | 11.3046 | 11.3141 | 0.0095
GEN-2018-089 | 05 SOUTWEST | 525613 | W_LITTLFLD 2 | 69 | 3.1708 | 3.1712 | 0.0004
GEN-2018-089 | 05 SOUTWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.327 | 4.3279 | 0.0009
GEN-2018-089 | 05 SOUTWEST | 525635 | LAMB_CNTY 2 | 69 | 6.1222 | 6.1238 | 0.0016
GEN-2018-089 | 05 SOUTWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4419 | 8.4473 | 0.0054
GEN-2018-089 | 05 SOUTWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9131 | 5.917 | 0.0039
GEN-2018-089 | 05 SOUTWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1531 | 5.1543 | 0.0012
GEN-2018-089 | 05 SOUTWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.7999 | 4.8009 | 0.001
GEN-2018-089 | 05 SOUTWEST | 525731 | SP-ABERNTHY2 | 69 | 3.172 | 3.1724 | 0.0004
GEN-2018-089 | 05 SOUTWEST | 525738 | HALECENTER 2 | 69 | 2.6084 | 2.6087 | 0.0003
GEN-2018-089 | 05 SOUTWEST | 525763 | CALLAHAN 3 | 115 | 5.8356 | 5.8402 | 0.0046
GEN-2018-089 | 05 SOUTWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4056 | 5.4075 | 0.0019
GEN-2018-089 | 05 SOUTWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.5076 | 6.5121 | 0.0045
GEN-2018-089 | 05 SOUTWEST | 525803 | BLANCO 3 | 115 | 5.2363 | 5.2385 | 0.0022
GEN-2018-089 | 05 SOUTWEST | 525816 | TUCO_INT2 2 | 69 | 4.7706 | 4.7714 | 0.0008
GEN-2018-089 | 05 SOUTWEST | 525826 | TUCO_INT 2 | 69 | 8.2018 | 8.2042 | 0.0024
GEN-2018-089 | 05 SOUTWEST | 525828 | TUCO_INT 3 | 115 | 19.7809 | 19.806 | 0.0251
GEN-2018-089 | 05 SOUTWEST | 525830 | TUCO_INT 6 | 230 | 21.8615 | 21.909 | 0.0475
GEN-2018-089 | 05 SOUTWEST | 525832 | TUCO_INT 7 | 345 | 13.9779 | 13.9936 | 0.0157
GEN-2018-089 | 05 SOUTWEST | 525840 | ANTELOPE_1 6 | 230 | 21.6858 | 21.7325 | 0.0467
GEN-2018-089 | 05 SOUTWEST | 525850 | ELK_CT1 | 345 | 13.8782 | 13.8937 | 0.0155
GEN-2018-089 | 05 SOUTWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7498 | 2.75 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5199 | 3.5204 | 0.0005
GEN-2018-089 | 05 SOUTWEST | 525926 | CROSBY 3 | 115 | 4.9194 | 4.9209 | 0.0015
GEN-2018-089 | 05 SOUTWEST | 525957 | HALE_WNDCL16 | 230 | 10.6908 | 10.701 | 0.0102
GEN-2018-089 | 05 SOUTWEST | 526019 | HOCKLEY 2 | 69 | 5.3924 | 5.3931 | 0.0007
GEN-2018-089 | 05 SOUTWEST | 526020 | HOCKLEY 3 | 115 | 5.6548 | 5.6562 | 0.0014
GEN-2018-089 | 05 SOUTWEST | 526036 | LC-OPDYKE 3 | 115 | 5.9368 | 5.9382 | 0.0014
GEN-2018-089 | 05 SOUTWEST | 526076 | STANTON_W 3 | 115 | 9.1722 | 9.1756 | 0.0034
GEN-2018-089 | 05 SOUTWEST | 526109 | SP-ERSKINE 3 | 115 | 11.1246 | 11.129 | 0.0044
GEN-2018-089 | 05 SOUTWEST | 526146 | INDIANA 3 | 115 | 9.5447 | 9.5483 | 0.0036
GEN-2018-089 | 05 SOUTWEST | 526159 | CARLISLE 2 | 69 | 2.7513 | 2.7515 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 526160 | CARLISLE 3 | 115 | 12.7973 | 12.8027 | 0.0054
GEN-2018-089 | 05 SOUTWEST | 526161 | CARLISLE 6 | 230 | 10.6882 | 10.6959 | 0.0077
GEN-2018-089 | 05 SOUTWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.4689 | 11.473 | 0.0041
GEN-2018-089 | 05 SOUTWEST | 526192 | MURPHY 3 | 115 | 10.5559 | 10.5593 | 0.0034
GEN-2018-089 | 05 SOUTWEST | 526268 | LUBBCK_STH 3 | 115 | 18.1166 | 18.1246 | 0.008
GEN-2018-089 | 05 SOUTWEST | 526269 | LUBBCK_STH 6 | 230 | 15.445 | 15.4547 | 0.0097
GEN-2018-089 | 05 SOUTWEST | 526297 | LUBBCK_EST 2 | 69 | 8.7358 | 8.7371 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 526298 | LUBBCK_EST 3 | 115 | 14.8816 | 14.8886 | 0.007
GEN-2018-089 | 05 SOUTWEST | 526299 | LUBBCK_EST 6 | 230 | 11.4684 | 11.4736 | 0.0052
GEN-2018-089 | 05 SOUTWEST | 526337 | JONES 6 | 230 | 17.0899 | 17.1008 | 0.0109
GEN-2018-089 | 05 SOUTWEST | 526361 | COCHRAN 3 | 115 | 6.5956 | 6.5964 | 0.0008
GEN-2018-089 | 05 SOUTWEST | 526424 | PACIFIC 3 | 115 | 9.2331 | 9.2352 | 0.0021
GEN-2018-089 | 05 SOUTWEST | 526434 | SUNDOWN 3 | 115 | 10.7972 | 10.8003 | 0.0031
GEN-2018-089 | 05 SOUTWEST | 526435 | SUNDOWN 6 | 230 | 11.5469 | 11.555 | 0.0081
GEN-2018-089 | 05 SOUTWEST | 526445 | AMOCO_TP 3 | 115 | 10.1926 | 10.1952 | 0.0026
GEN-2018-089 | 05 SOUTWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.4888 | 6.4899 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 526460 | AMOCO_SS 6 | 230 | 10.2653 | 10.2709 | 0.0056
GEN-2018-089 | 05 SOUTWEST | 526475 | YUMA_INT 3 | 115 | 10.8694 | 10.8729 | 0.0035
GEN-2018-089 | 05 SOUTWEST | 526484 | LG-LEVELAND3 | 115 | 9.2767 | 9.2788 | 0.0021
GEN-2018-089 | 05 SOUTWEST | 526524 | WOLFFORTH 3 | 115 | 11.3334 | 11.3369 | 0.0035
GEN-2018-089 | 05 SOUTWEST | 526525 | WOLFFORTH 6 | 230 | 13.0153 | 13.0245 | 0.0092
GEN-2018-089 | 05 SOUTWEST | 526676 | GRASSLAND 3 | 115 | 7.2496 | 7.2506 | 0.001
GEN-2018-089 | 05 SOUTWEST | 526677 | GRASSLAND 6 | 230 | 6.2441 | 6.2456 | 0.0015
GEN-2018-089 | 05 SOUTWEST | 526679 | CIRRUS_WND 6 | 230 | 4.894 | 4.8949 | 0.0009
GEN-2018-089 | 05 SOUTWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1235 | 11.1253 | 0.0018
GEN-2018-089 | 05 SOUTWEST | 526934 | YOAKUM 3 | 115 | 19.2963 | 19.2991 | 0.0028
GEN-2018-089 | 05 SOUTWEST | 526935 | YOAKUM 6 | 230 | 20.8125 | 20.8189 | 0.0064
GEN-2018-089 | 05 SOUTWEST | 526936 | YOAKUM_345 | 345 | 10.5017 | 10.5046 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 527009 | BRU_SUB 6 | 230 | 16.5439 | 16.5471 | 0.0032
GEN-2018-089 | 05 SOUTWEST | 527028 | INK_BASIN 6 | 230 | 11.7933 | 11.7946 | 0.0013
GEN-2018-089 | 05 SOUTWEST | 527149 | MUSTANG 6 | 230 | 19.0039 | 19.0068 | 0.0029
GEN-2018-089 | 05 SOUTWEST | 527610 | SAGA_SCOL 7 | 345 | 10.362 | 10.3648 | 0.0028
GEN-2018-089 | 05 SOUTWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.1088 | 10.1115 | 0.0027
GEN-2018-089 | 05 SOUTWEST | 527656 | CROSSROADS 7 | 345 | 11.6227 | 11.6265 | 0.0038
GEN-2018-089 | 05 SOUTWEST | 527802 | EDDY_CNTY 7 | 345 | 7.5969 | 7.5969 | 0
GEN-2018-089 | 05 SOUTWEST | 527896 | HOBBS_INT 7 | 345 | 12.3086 | 12.3104 | 0.0018
GEN-2018-089 | 05 SOUTWEST | 531512 | HARBNGR7 | 345 | 6.5324 | 6.5326 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 560577 | G06-44 | 115 | 7.7983 | 7.7985 | 0.0002
GEN-2018-089 | 05 SOUTWEST | 576395 | GEN-2010-014 | 345 | 9.828 | 9.8291 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 576397 | G10014G11022 | 345 | 9.828 | 9.8291 | 0.0011
GEN-2018-089 | 05 SOUTWEST | 599955 | PNM-DC6 | 230 | 9.9332 | 9.9404 | 0.0072
GEN-2018-089 | 05 SOUTWEST | 599956 | PNM-DC7 | 345 | 15.1757 | 15.1757 | 0
GEN-2018-089 | 05 SOUTWEST | 755000 | WWDBORDT | 345 | 10.2582 | 10.259 | 0.0008
GEN-2018-089 | 05 SOUTWEST | 760494 | GEN-2017-146 | 230 | 7.7674 | 7.7777 | 0.0103
GEN-2018-089 | 05 SOUTWEST | 760498 | G17-146-TAP | 230 | 8.0675 | 8.0786 | 0.0111
GEN-2018-089 | 05 SOUTWEST | 762132 | GEN-2017-158 | 230 | 14.0884 | 14.1047 | 0.0163
GEN-2018-089 | 05 SOUTWEST | 762216 | G17-151TAP | 345 | 8.531 | 8.5355 | 0.0045
GEN-2018-089 | 05 SOUTWEST | 762217 | GEN-2017-151 | 345 | 6.2731 | 6.2754 | 0.0023
GEN-2018-089 | 05 SOUTWEST | 762467 | G18-015-TAP | 345 | 5.3204 | 5.3211 | 0.0007
GEN-2018-089 | 05 SOUTWEST | 763186 | GEN-2018-089 | 230 | 10.7073 | 11.1335 | 0.4262
GEN-2018-089 | 05 SOUTWEST | 763483 | GEN-2019-003 | 230 | 8.9621 | 8.9679 | 0.0058
GEN-2018-089 | 05 SOUTWEST | 763516 | GEN-2019-011 | 345 | 9.8674 | 9.8699 | 0.0025
GEN-2018-099 | 05 SOUTWEST | 511456 | O.K.U.-7 | 345 | 5.8456 | 5.8457 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 511553 | CHISHOLM7 | 345 | 10.2667 | 10.2669 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 515375 | WWRDEHV7 | 345 | 19.0118 | 19.012 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 515458 | BORDER 7 | 345 | 7.4344 | 7.4346 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 515554 | BVRCNTY7 | 345 | 12.8492 | 12.8495 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 515590 | PALDR2W7 | 345 | 11.1687 | 11.1689 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 515618 | BALKOW 7 | 345 | 10.9821 | 10.9824 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 515677 | BADGER 7 | 345 | 12.4984 | 12.4986 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 523093 | HITCHLAND 3 | 115 | 17.5191 | 17.5185 | -0.0006
GEN-2018-099 | 05 SOUTWEST | 523095 | HITCHLAND 6 | 230 | 14.0633 | 14.0634 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 523097 | HITCHLAND 7 | 345 | 13.5621 | 13.5626 | 0.0005
GEN-2018-099 | 05 SOUTWEST | 523101 | NOBLE_WND 7 | 345 | 13.5147 | 13.5153 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 523103 | NOBLE_WND 3 | 115 | 10.8084 | 10.8085 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 523111 | NOVUS1 3 | 115 | 8.0739 | 8.0739 | 0
GEN-2018-099 | 05 SOUTWEST | 523112 | NOVUS1 7 | 345 | 13.3307 | 13.3313 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 523155 | OCHILTREE 6 | 230 | 4.3761 | 4.376 | -0.0001
GEN-2018-099 | 05 SOUTWEST | 523215 | GEN-2011-022 | 345 | 9.8288 | 9.8291 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 523221 | XIT_INTG 6 | 230 | 3.3275 | 3.3277 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 523267 | PRINGLE 6 | 230 | 4.7508 | 4.7509 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 523309 | MOORE_CNTY 6 | 230 | 6.9822 | 6.9826 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8059 | 9.8065 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 523323 | MCDWL_CREEK6 | 230 | 9.4097 | 9.4109 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 523551 | HUTCHISON 6 | 230 | 7.8592 | 7.8596 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 523771 | GRAPEVINE 6 | 230 | 5.9358 | 5.9359 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 523823 | CARPENTER 7 | 345 | 6.5517 | 6.5517 | 0
GEN-2018-099 | 05 SOUTWEST | 523853 | FINNEY 7 | 345 | 8.9671 | 8.9671 | 0
GEN-2018-099 | 05 SOUTWEST | 523869 | CHAN+TASCOS6 | 230 | 4.4558 | 4.4561 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 523959 | POTTER_CO 6 | 230 | 23.0447 | 23.0545 | 0.0098
GEN-2018-099 | 05 SOUTWEST | 523961 | POTTER_CO 7 | 345 | 11.0527 | 11.0581 | 0.0054
GEN-2018-099 | 05 SOUTWEST | 523977 | HARRNG_WST 6 | 230 | 28.1474 | 28.1552 | 0.0078
GEN-2018-099 | 05 SOUTWEST | 523978 | HARRNG_MID 6 | 230 | 28.1474 | 28.1552 | 0.0078
GEN-2018-099 | 05 SOUTWEST | 523979 | HARRNG_EST 6 | 230 | 28.1474 | 28.1552 | 0.0078
GEN-2018-099 | 05 SOUTWEST | 524007 | ROLLHILLS 3 | 115 | 20.278 | 20.2803 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 524010 | ROLLHILLS 6 | 230 | 21.0211 | 21.0269 | 0.0058
GEN-2018-099 | 05 SOUTWEST | 524043 | NICHOLS 3 | 115 | 31.5006 | 31.5046 | 0.004
GEN-2018-099 | 05 SOUTWEST | 524044 | NICHOLS 6 | 230 | 27.2422 | 27.2494 | 0.0072
GEN-2018-099 | 05 SOUTWEST | 524266 | BUSHLAND 3 | 115 | 9.746 | 9.747 | 0.001
GEN-2018-099 | 05 SOUTWEST | 524267 | BUSHLAND 6 | 230 | 10.4063 | 10.4097 | 0.0034
GEN-2018-099 | 05 SOUTWEST | 524290 | WILDOR2_JUS6 | 230 | 7.2011 | 7.2026 | 0.0015
GEN-2018-099 | 05 SOUTWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3332 | 5.3342 | 0.001
GEN-2018-099 | 05 SOUTWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3332 | 5.3342 | 0.001
GEN-2018-099 | 05 SOUTWEST | 524364 | RANDALL 3 | 115 | 21.3885 | 21.3922 | 0.0037
GEN-2018-099 | 05 SOUTWEST | 524365 | RANDALL 6 | 230 | 15.1401 | 15.143 | 0.0029
GEN-2018-099 | 05 SOUTWEST | 524377 | FARMERS 3 | 115 | 15.9619 | 15.9637 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 524397 | ARROWHEAD 3 | 115 | 14.1297 | 14.1311 | 0.0014
GEN-2018-099 | 05 SOUTWEST | 524404 | OWENSCORN 3 | 115 | 15.5232 | 15.525 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 524414 | AMA_SOUTH 3 | 115 | 17.3847 | 17.3868 | 0.0021
GEN-2018-099 | 05 SOUTWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2389 | 14.2417 | 0.0028
GEN-2018-099 | 05 SOUTWEST | 524486 | CAPROCK 3 | 115 | 2.7742 | 2.7743 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 524502 | NORTON 3 | 115 | 3.0741 | 3.0743 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5422 | 2.5423 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 524544 | SPRING_DRW 3 | 115 | 6.6715 | 6.6719 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 524619 | DFSMTH_EST 3 | 115 | 11.7351 | 11.741 | 0.0059
GEN-2018-099 | 05 SOUTWEST | 524622 | DFSMTH_WST 3 | 115 | 11.738 | 11.7439 | 0.0059
GEN-2018-099 | 05 SOUTWEST | 524623 | DEAFSMITH 6 | 230 | 8.4157 | 8.4216 | 0.0059
GEN-2018-099 | 05 SOUTWEST | 524630 | TIERABLANCA3 | 115 | 12.0601 | 12.0663 | 0.0062
GEN-2018-099 | 05 SOUTWEST | 524662 | PARMER_CO 3 | 115 | 4.5893 | 4.5909 | 0.0016
GEN-2018-099 | 05 SOUTWEST | 524669 | DS-#20 3 | 115 | 5.5105 | 5.513 | 0.0025
GEN-2018-099 | 05 SOUTWEST | 524694 | DS-#22 3 | 115 | 4.8437 | 4.8446 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 524734 | DS-#21 3 | 115 | 9.6299 | 9.6335 | 0.0036
GEN-2018-099 | 05 SOUTWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7407 | 8.7426 | 0.0019
GEN-2018-099 | 05 SOUTWEST | 524746 | CASTRO_CNTY3 | 115 | 10.1568 | 10.1608 | 0.004
GEN-2018-099 | 05 SOUTWEST | 524757 | BETHEL_COL13 | 115 | 8.5304 | 8.533 | 0.0026
GEN-2018-099 | 05 SOUTWEST | 524764 | NORRIS_TP 3 | 115 | 11.3493 | 11.3615 | 0.0122
GEN-2018-099 | 05 SOUTWEST | 524768 | PLSNT_HILL 3 | 115 | 10.9139 | 10.9246 | 0.0107
GEN-2018-099 | 05 SOUTWEST | 524770 | PLSNT_HILL 6 | 230 | 6.6306 | 6.6398 | 0.0092
GEN-2018-099 | 05 SOUTWEST | 524773 | E_CLOVIS 3 | 115 | 9.1728 | 9.1806 | 0.0078
GEN-2018-099 | 05 SOUTWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.7899 | 7.7953 | 0.0054
GEN-2018-099 | 05 SOUTWEST | 524777 | N_CLOVIS 3 | 115 | 7.0222 | 7.0266 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 524783 | W_CLOVIS 2 | 69 | 2.5521 | 2.5524 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 524790 | CANNON_TP 3 | 115 | 6.2343 | 6.2379 | 0.0036
GEN-2018-099 | 05 SOUTWEST | 524797 | PERIMETER 3 | 115 | 6.7035 | 6.7079 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 524801 | NORRIS 3 | 115 | 10.3903 | 10.4005 | 0.0102
GEN-2018-099 | 05 SOUTWEST | 524808 | FE-CLVS_INT3 | 115 | 7.2496 | 7.2542 | 0.0046
GEN-2018-099 | 05 SOUTWEST | 524821 | CURRY 2 | 69 | 4.5204 | 4.5215 | 0.0011
GEN-2018-099 | 05 SOUTWEST | 524822 | CURRY 3 | 115 | 11.3801 | 11.3923 | 0.0122
GEN-2018-099 | 05 SOUTWEST | 524831 | FE-HOLLAND 3 | 115 | 9.4835 | 9.4918 | 0.0083
GEN-2018-099 | 05 SOUTWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.8009 | 10.8119 | 0.011
GEN-2018-099 | 05 SOUTWEST | 524846 | FARWELL 2 | 69 | 2.2133 | 2.2136 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0979 | 8.1043 | 0.0064
GEN-2018-099 | 05 SOUTWEST | 524874 | OASIS 3 | 115 | 9.9746 | 9.9847 | 0.0101
GEN-2018-099 | 05 SOUTWEST | 524875 | OASIS 6 | 230 | 8.0722 | 8.0854 | 0.0132
GEN-2018-099 | 05 SOUTWEST | 524885 | SN_JUAN_TAP6 | 230 | 5.0144 | 5.0165 | 0.0021
GEN-2018-099 | 05 SOUTWEST | 524889 | SN_JUAN_WND6 | 230 | 4.7993 | 4.8012 | 0.0019
GEN-2018-099 | 05 SOUTWEST | 524908 | ROOSEVELT 3 | 115 | 11.0078 | 11.0207 | 0.0129
GEN-2018-099 | 05 SOUTWEST | 524909 | ROOSEVELT 6 | 230 | 9.9176 | 9.9404 | 0.0228
GEN-2018-099 | 05 SOUTWEST | 524923 | PORTALES 2 | 69 | 7.7373 | 7.7409 | 0.0036
GEN-2018-099 | 05 SOUTWEST | 524924 | PORTALES 3 | 115 | 7.6823 | 7.6884 | 0.0061
GEN-2018-099 | 05 SOUTWEST | 524929 | RO-PORT_MTR2 | 69 | 7.7373 | 7.7409 | 0.0036
GEN-2018-099 | 05 SOUTWEST | 524934 | ZODIAC 2 | 69 | 5.6812 | 5.6832 | 0.002
GEN-2018-099 | 05 SOUTWEST | 524935 | KILGORE 3 | 115 | 6.2989 | 6.3029 | 0.004
GEN-2018-099 | 05 SOUTWEST | 524941 | PORTALES#1 2 | 69 | 5.9325 | 5.9346 | 0.0021
GEN-2018-099 | 05 SOUTWEST | 524963 | S_PORTALES 3 | 115 | 5.9233 | 5.9269 | 0.0036
GEN-2018-099 | 05 SOUTWEST | 524977 | GREYHOUND 3 | 115 | 5.8398 | 5.8433 | 0.0035
GEN-2018-099 | 05 SOUTWEST | 525018 | MULESHVALLY3 | 115 | 5.1389 | 5.1411 | 0.0022
GEN-2018-099 | 05 SOUTWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4688 | 5.4712 | 0.0024
GEN-2018-099 | 05 SOUTWEST | 525027 | BAILEYCO 2 | 69 | 4.8783 | 4.8795 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 525028 | BAILEYCO 3 | 115 | 5.3645 | 5.3669 | 0.0024
GEN-2018-099 | 05 SOUTWEST | 525050 | BC-KELLEY +3 | 115 | 7.8661 | 7.8695 | 0.0034
GEN-2018-099 | 05 SOUTWEST | 525056 | BC-EARTH 3 | 115 | 8.2063 | 8.2104 | 0.0041
GEN-2018-099 | 05 SOUTWEST | 525124 | HART_INDUST3 | 115 | 7.7548 | 7.7574 | 0.0026
GEN-2018-099 | 05 SOUTWEST | 525179 | TULIA_TP 3 | 115 | 6.7926 | 6.7936 | 0.001
GEN-2018-099 | 05 SOUTWEST | 525191 | KRESS_INT 2 | 69 | 4.4379 | 4.4382 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 525192 | KRESS_INT 3 | 115 | 12.3313 | 12.3354 | 0.0041
GEN-2018-099 | 05 SOUTWEST | 525212 | SWISHER 3 | 115 | 11.7784 | 11.7821 | 0.0037
GEN-2018-099 | 05 SOUTWEST | 525213 | SWISHER 6 | 230 | 10.8383 | 10.8441 | 0.0058
GEN-2018-099 | 05 SOUTWEST | 525226 | KRS_RURL_TP3 | 115 | 6.7487 | 6.7499 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 525272 | KISER 3 | 115 | 5.5774 | 5.5782 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 525291 | PLAINVW_TP 2 | 69 | 6.375 | 6.3758 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 525298 | S_PLAINVEW 2 | 69 | 2.6944 | 2.6946 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 525325 | COX 2 | 69 | 3.2915 | 3.2917 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 525326 | COX 3 | 115 | 6.6306 | 6.6317 | 0.0011
GEN-2018-099 | 05 SOUTWEST | 525351 | LH-AIKEN 2 | 69 | 2.2461 | 2.2461 | 0
GEN-2018-099 | 05 SOUTWEST | 525393 | ROCKYFORD 3 | 115 | 8.543 | 8.5483 | 0.0053
GEN-2018-099 | 05 SOUTWEST | 525413 | LAMTON 2 | 69 | 4.8294 | 4.8301 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 525414 | LAMTON 3 | 115 | 7.8423 | 7.8453 | 0.003
GEN-2018-099 | 05 SOUTWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8084 | 5.8091 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 525440 | LC-S_OLTON+3 | 115 | 7.2617 | 7.2647 | 0.003
GEN-2018-099 | 05 SOUTWEST | 525446 | RKYFORD_TP 3 | 115 | 9.4534 | 9.4599 | 0.0065
GEN-2018-099 | 05 SOUTWEST | 525453 | HALE_CNTY 2 | 69 | 6.7609 | 6.7619 | 0.001
GEN-2018-099 | 05 SOUTWEST | 525454 | HALE_CNTY 3 | 115 | 10.5562 | 10.5599 | 0.0037
GEN-2018-099 | 05 SOUTWEST | 525460 | NEWHART 3 | 115 | 15.182 | 15.1909 | 0.0089
GEN-2018-099 | 05 SOUTWEST | 525461 | NEWHART 6 | 230 | 11.4426 | 11.4527 | 0.0101
GEN-2018-099 | 05 SOUTWEST | 525480 | PLANT_X 3 | 115 | 15.4875 | 15.507 | 0.0195
GEN-2018-099 | 05 SOUTWEST | 525481 | PLANT_X 6 | 230 | 23.71 | 23.8515 | 0.1415
GEN-2018-099 | 05 SOUTWEST | 525531 | TOLK 6 | 230 | 30.3691 | 30.7299 | 0.3608
GEN-2018-099 | 05 SOUTWEST | 525549 | TOLK 7 | 345 | 13.4061 | 13.4662 | 0.0601
GEN-2018-099 | 05 SOUTWEST | 525584 | BLUECLDCOL 6 | 230 | 10.6854 | 10.7184 | 0.033
GEN-2018-099 | 05 SOUTWEST | 525585 | BLUECLDPOI 6 | 230 | 11.2771 | 11.3141 | 0.037
GEN-2018-099 | 05 SOUTWEST | 525586 | NEEDMORE 6 | 230 | 11.2771 | 11.3141 | 0.037
GEN-2018-099 | 05 SOUTWEST | 525606 | AMHERST 2 | 69 | 2.5333 | 2.5337 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 525613 | W_LITTLFLD 2 | 69 | 3.1706 | 3.1712 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3266 | 4.3279 | 0.0013
GEN-2018-099 | 05 SOUTWEST | 525635 | LAMB_CNTY 2 | 69 | 6.1214 | 6.1238 | 0.0024
GEN-2018-099 | 05 SOUTWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4392 | 8.4473 | 0.0081
GEN-2018-099 | 05 SOUTWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9073 | 5.917 | 0.0097
GEN-2018-099 | 05 SOUTWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1525 | 5.1543 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 525657 | W_ANTON_TP 2 | 69 | 4.3103 | 4.3115 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.7994 | 4.8009 | 0.0015
GEN-2018-099 | 05 SOUTWEST | 525694 | HOBGOOD 2 | 69 | 3.5934 | 3.5943 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 525723 | CNTYLINE_TP2 | 69 | 2.3202 | 2.3202 | 0
GEN-2018-099 | 05 SOUTWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1723 | 3.1724 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 525738 | HALECENTER 2 | 69 | 2.6086 | 2.6087 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 525745 | LH-HALECTR 2 | 69 | 2.5795 | 2.5796 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 525763 | CALLAHAN 3 | 115 | 5.8395 | 5.8402 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4071 | 5.4075 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.5114 | 6.5121 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 525790 | FLOYDADA_TP2 | 69 | 2.6851 | 2.6852 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 525801 | LRNZ_MPT 3 | 115 | 5.2371 | 5.2375 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 525803 | BLANCO 3 | 115 | 5.2381 | 5.2385 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 525811 | LH-HARMONY 2 | 69 | 4.3615 | 4.3617 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 525816 | TUCO_INT2 2 | 69 | 4.7712 | 4.7714 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 525826 | TUCO_INT 2 | 69 | 8.2036 | 8.2042 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 525828 | TUCO_INT 3 | 115 | 19.7995 | 19.806 | 0.0065
GEN-2018-099 | 05 SOUTWEST | 525830 | TUCO_INT 6 | 230 | 21.8938 | 21.909 | 0.0152
GEN-2018-099 | 05 SOUTWEST | 525832 | TUCO_INT 7 | 345 | 13.9879 | 13.9936 | 0.0057
GEN-2018-099 | 05 SOUTWEST | 525840 | ANTELOPE_1 6 | 230 | 21.7175 | 21.7325 | 0.015
GEN-2018-099 | 05 SOUTWEST | 525850 | ELK_CT1 | 345 | 13.8881 | 13.8937 | 0.0056
GEN-2018-099 | 05 SOUTWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.75 | 2.75 | 0
GEN-2018-099 | 05 SOUTWEST | 525860 | SP-BECTON +2 | 69 | 2.4449 | 2.4449 | 0
GEN-2018-099 | 05 SOUTWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5203 | 3.5204 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 525892 | MONROE 2 | 69 | 2.8331 | 2.8331 | 0
GEN-2018-099 | 05 SOUTWEST | 525925 | CROSBY 2 | 69 | 4.898 | 4.8982 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 525926 | CROSBY 3 | 115 | 4.9206 | 4.9209 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 525957 | HALE_WNDCL16 | 230 | 10.6977 | 10.701 | 0.0033
GEN-2018-099 | 05 SOUTWEST | 526009 | LC-LEVLND#22 | 69 | 4.5106 | 4.5113 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 526019 | HOCKLEY 2 | 69 | 5.3921 | 5.3931 | 0.001
GEN-2018-099 | 05 SOUTWEST | 526020 | HOCKLEY 3 | 115 | 5.6544 | 5.6562 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 526036 | LC-OPDYKE 3 | 115 | 5.9364 | 5.9382 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 526042 | COBLE 2 | 69 | 2.4265 | 2.4267 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.5065 | 4.5072 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 526076 | STANTON_W 3 | 115 | 9.1743 | 9.1756 | 0.0013
GEN-2018-099 | 05 SOUTWEST | 526109 | SP-ERSKINE 3 | 115 | 11.1272 | 11.129 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 526130 | SP-CARLISLE2 | 69 | 2.2447 | 2.2448 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 526146 | INDIANA 3 | 115 | 9.547 | 9.5483 | 0.0013
GEN-2018-099 | 05 SOUTWEST | 526159 | CARLISLE 2 | 69 | 2.7514 | 2.7515 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 526160 | CARLISLE 3 | 115 | 12.8004 | 12.8027 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 526161 | CARLISLE 6 | 230 | 10.6925 | 10.6959 | 0.0034
GEN-2018-099 | 05 SOUTWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.4712 | 11.473 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 526176 | LP-DOUD 3 | 115 | 9.0399 | 9.041 | 0.0011
GEN-2018-099 | 05 SOUTWEST | 526184 | SW_6878 2 | 69 | 2.32 | 2.3201 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 526192 | MURPHY 3 | 115 | 10.5579 | 10.5593 | 0.0014
GEN-2018-099 | 05 SOUTWEST | 526195 | QUINCY 3 | 115 | 10.0143 | 10.0155 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 526213 | ALLEN 3 | 115 | 10.8972 | 10.8985 | 0.0013
GEN-2018-099 | 05 SOUTWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3122 | 4.3123 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 526268 | LUBBCK_STH 3 | 115 | 18.1215 | 18.1246 | 0.0031
GEN-2018-099 | 05 SOUTWEST | 526269 | LUBBCK_STH 6 | 230 | 15.4506 | 15.4547 | 0.0041
GEN-2018-099 | 05 SOUTWEST | 526284 | PLANTERS 2 | 69 | 6.3026 | 6.3028 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 526297 | LUBBCK_EST 2 | 69 | 8.7367 | 8.7371 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 526298 | LUBBCK_EST 3 | 115 | 14.8863 | 14.8886 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 526299 | LUBBCK_EST 6 | 230 | 11.4716 | 11.4736 | 0.002
GEN-2018-099 | 05 SOUTWEST | 526310 | CLUTTER 2 | 69 | 5.8402 | 5.8404 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 526337 | JONES 6 | 230 | 17.0964 | 17.1008 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 526361 | COCHRAN 3 | 115 | 6.5954 | 6.5964 | 0.001
GEN-2018-099 | 05 SOUTWEST | 526424 | PACIFIC 3 | 115 | 9.2328 | 9.2352 | 0.0024
GEN-2018-099 | 05 SOUTWEST | 526434 | SUNDOWN 3 | 115 | 10.7968 | 10.8003 | 0.0035
GEN-2018-099 | 05 SOUTWEST | 526435 | SUNDOWN 6 | 230 | 11.5471 | 11.555 | 0.0079
GEN-2018-099 | 05 SOUTWEST | 526445 | AMOCO_TP 3 | 115 | 10.1923 | 10.1952 | 0.0029
GEN-2018-099 | 05 SOUTWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.4887 | 6.4899 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 526460 | AMOCO_SS 6 | 230 | 10.2653 | 10.2709 | 0.0056
GEN-2018-099 | 05 SOUTWEST | 526475 | YUMA_INT 3 | 115 | 10.8713 | 10.8729 | 0.0016
GEN-2018-099 | 05 SOUTWEST | 526481 | SP-WOLF_TP 3 | 115 | 11.0315 | 11.0331 | 0.0016
GEN-2018-099 | 05 SOUTWEST | 526484 | LG-LEVELAND3 | 115 | 9.2765 | 9.2788 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 526524 | WOLFFORTH 3 | 115 | 11.3351 | 11.3369 | 0.0018
GEN-2018-099 | 05 SOUTWEST | 526525 | WOLFFORTH 6 | 230 | 13.0196 | 13.0245 | 0.0049
GEN-2018-099 | 05 SOUTWEST | 526562 | SLATON 2 | 69 | 2.6775 | 2.6775 | 0
GEN-2018-099 | 05 SOUTWEST | 526602 | WOODROW 3 | 115 | 9.5468 | 9.5476 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 526656 | LYNN_CNTY 3 | 115 | 6.2835 | 6.2838 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 526676 | GRASSLAND 3 | 115 | 7.2502 | 7.2506 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 526677 | GRASSLAND 6 | 230 | 6.245 | 6.2456 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 526679 | CIRRUS_WND 6 | 230 | 4.8946 | 4.8949 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 526694 | GRAHAM 3 | 115 | 3.0307 | 3.0307 | 0
GEN-2018-099 | 05 SOUTWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1236 | 11.1253 | 0.0017
GEN-2018-099 | 05 SOUTWEST | 526784 | AMOCOWASSON6 | 230 | 16.5544 | 16.5582 | 0.0038
GEN-2018-099 | 05 SOUTWEST | 526792 | PRENTICE 3 | 115 | 6.3124 | 6.3129 | 0.0005
GEN-2018-099 | 05 SOUTWEST | 526928 | PLAINS_INT 3 | 115 | 10.2935 | 10.2947 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 526934 | YOAKUM 3 | 115 | 19.2952 | 19.2991 | 0.0039
GEN-2018-099 | 05 SOUTWEST | 526935 | YOAKUM 6 | 230 | 20.8091 | 20.8189 | 0.0098
GEN-2018-099 | 05 SOUTWEST | 526936 | YOAKUM_345 | 345 | 10.5011 | 10.5046 | 0.0035
GEN-2018-099 | 05 SOUTWEST | 526944 | LG-PLAINS 3 | 115 | 8.1533 | 8.1541 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 527009 | BRU_SUB 6 | 230 | 16.5422 | 16.5471 | 0.0049
GEN-2018-099 | 05 SOUTWEST | 527010 | OXYBRU 6 | 230 | 16.3867 | 16.3916 | 0.0049
GEN-2018-099 | 05 SOUTWEST | 527011 | XTO_MAHONEY6 | 230 | 16.238 | 16.2424 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 527018 | BENNETT 3 | 115 | 14.4077 | 14.4091 | 0.0014
GEN-2018-099 | 05 SOUTWEST | 527027 | INK_BASIN 3 | 115 | 13.7042 | 13.7053 | 0.0011
GEN-2018-099 | 05 SOUTWEST | 527028 | INK_BASIN 6 | 230 | 11.7923 | 11.7946 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.8521 | 12.853 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 527041 | ARCO_TP 3 | 115 | 14.3056 | 14.3071 | 0.0015
GEN-2018-099 | 05 SOUTWEST | 527047 | OXY_WILRD1 3 | 115 | 11.4323 | 11.4332 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 527062 | SHELL_CO2 3 | 115 | 17.4519 | 17.4538 | 0.0019
GEN-2018-099 | 05 SOUTWEST | 527130 | DENVER_N 3 | 115 | 23.3387 | 23.3418 | 0.0031
GEN-2018-099 | 05 SOUTWEST | 527136 | DENVER_S 3 | 115 | 23.3387 | 23.3418 | 0.0031
GEN-2018-099 | 05 SOUTWEST | 527146 | MUSTANG 3 | 115 | 24.9068 | 24.9101 | 0.0033
GEN-2018-099 | 05 SOUTWEST | 527149 | MUSTANG 6 | 230 | 19.0024 | 19.0068 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 527151 | GS-MUSTANG 6 | 230 | 19.0024 | 19.0068 | 0.0044
GEN-2018-099 | 05 SOUTWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3301 | 8.3307 | 0.0006
GEN-2018-099 | 05 SOUTWEST | 527202 | SEAGRAVES 3 | 115 | 9.6117 | 9.6124 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 527275 | SEMINOLE 3 | 115 | 14.7976 | 14.7988 | 0.0012
GEN-2018-099 | 05 SOUTWEST | 527276 | SEMINOLE 6 | 230 | 8.8907 | 8.8916 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 527482 | CHAVES_CNTY3 | 115 | 7.4888 | 7.4897 | 0.0009
GEN-2018-099 | 05 SOUTWEST | 527483 | CHAVES_CNTY6 | 230 | 4.5765 | 4.5773 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.3561 | 10.3648 | 0.0087
GEN-2018-099 | 05 SOUTWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.3561 | 10.3648 | 0.0087
GEN-2018-099 | 05 SOUTWEST | 527610 | SAGA_SCOL 7 | 345 | 10.3561 | 10.3648 | 0.0087
GEN-2018-099 | 05 SOUTWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.8142 | 8.8205 | 0.0063
GEN-2018-099 | 05 SOUTWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.103 | 10.1115 | 0.0085
GEN-2018-099 | 05 SOUTWEST | 527656 | CROSSROADS 7 | 345 | 11.6149 | 11.6265 | 0.0116
GEN-2018-099 | 05 SOUTWEST | 527666 | RSVLT_COL1 7 | 345 | 8.8142 | 8.8205 | 0.0063
GEN-2018-099 | 05 SOUTWEST | 527667 | RSVLT_COL2 7 | 345 | 8.8142 | 8.8205 | 0.0063
GEN-2018-099 | 05 SOUTWEST | 527793 | EDDY_STH 3 | 115 | 12.3626 | 12.363 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 527798 | EDDY_NTH 3 | 115 | 12.3626 | 12.363 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 527799 | EDDY_NORTH 6 | 230 | 9.9051 | 9.9052 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 527802 | EDDY_CNTY 7 | 345 | 7.5952 | 7.5969 | 0.0017
GEN-2018-099 | 05 SOUTWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.2956 | 18.2985 | 0.0029
GEN-2018-099 | 05 SOUTWEST | 527867 | CUNNIGHM_S 6 | 230 | 18.2956 | 18.2985 | 0.0029
GEN-2018-099 | 05 SOUTWEST | 527891 | HOBBS_INT 3 | 115 | 32.3275 | 32.3305 | 0.003
GEN-2018-099 | 05 SOUTWEST | 527894 | HOBBS_INT 6 | 230 | 20.3358 | 20.34 | 0.0042
GEN-2018-099 | 05 SOUTWEST | 527896 | HOBBS_INT 7 | 345 | 12.305 | 12.3104 | 0.0054
GEN-2018-099 | 05 SOUTWEST | 527965 | KIOWA 7 | 345 | 9.199 | 9.2013 | 0.0023
GEN-2018-099 | 05 SOUTWEST | 527966 | KIOWA 3 | 115 | 17.983 | 17.9851 | 0.0021
GEN-2018-099 | 05 SOUTWEST | 528015 | PHANTOM 7 | 345 | 6.1673 | 6.168 | 0.0007
GEN-2018-099 | 05 SOUTWEST | 528025 | RDRUNNER 3 | 115 | 14.5254 | 14.5271 | 0.0017
GEN-2018-099 | 05 SOUTWEST | 528027 | RDRUNNER 7 | 345 | 9.1953 | 9.1978 | 0.0025
GEN-2018-099 | 05 SOUTWEST | 528095 | 7-RIVERS 6 | 230 | 6.7591 | 6.7594 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 528185 | N_LOVING 7 | 345 | 6.9934 | 6.9944 | 0.001
GEN-2018-099 | 05 SOUTWEST | 528325 | LE-WAITS 3 | 115 | 9.4355 | 9.436 | 0.0005
GEN-2018-099 | 05 SOUTWEST | 528604 | ANDREWS 6 | 230 | 6.3543 | 6.3547 | 0.0004
GEN-2018-099 | 05 SOUTWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6621 | 3.6622 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 531512 | HARBNGR7 | 345 | 6.5325 | 6.5326 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 560577 | G06-44 | 115 | 7.7984 | 7.7985 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 576395 | GEN-2010-014 | 345 | 9.8288 | 9.8291 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 576397 | G10014G11022 | 345 | 9.8288 | 9.8291 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 588460 | A16-008SUB | 115 | 13.7042 | 13.7053 | 0.0011
GEN-2018-099 | 05 SOUTWEST | 599950 | LAMAR7 | 345 | 2.3488 | 2.3488 | 0
GEN-2018-099 | 05 SOUTWEST | 599951 | LAMAR 6 | 345 | 13.4752 | 13.4752 | 0
GEN-2018-099 | 05 SOUTWEST | 599955 | PNM-DC6 | 230 | 9.9176 | 9.9404 | 0.0228
GEN-2018-099 | 05 SOUTWEST | 599956 | PNM-DC7 | 345 | 15.1757 | 15.1757 | 0
GEN-2018-099 | 05 SOUTWEST | 599960 | EPTNP-D6 | 230 | 9.9051 | 9.9052 | 0.0001
GEN-2018-099 | 05 SOUTWEST | 599961 | EPTNP 7 | 345 | 13.486 | 13.486 | 0
GEN-2018-099 | 05 SOUTWEST | 755000 | WWDBORDT | 345 | 10.2588 | 10.259 | 0.0002
GEN-2018-099 | 05 SOUTWEST | 760494 | GEN-2017-146 | 230 | 7.771 | 7.7777 | 0.0067
GEN-2018-099 | 05 SOUTWEST | 760498 | G17-146-TAP | 230 | 8.0713 | 8.0786 | 0.0073
GEN-2018-099 | 05 SOUTWEST | 761355 | GEN-2017-239 | 230 | 14.5789 | 14.5824 | 0.0035
GEN-2018-099 | 05 SOUTWEST | 762132 | GEN-2017-158 | 230 | 13.6999 | 14.1047 | 0.4048
GEN-2018-099 | 05 SOUTWEST | 762216 | G17-151TAP | 345 | 8.5339 | 8.5355 | 0.0016
GEN-2018-099 | 05 SOUTWEST | 762217 | GEN-2017-151 | 345 | 6.2746 | 6.2754 | 0.0008
GEN-2018-099 | 05 SOUTWEST | 762460 | GEN-2018-015 | 345 | 5.3113 | 5.3116 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 762467 | G18-015-TAP | 345 | 5.3208 | 5.3211 | 0.0003
GEN-2018-099 | 05 SOUTWEST | 763186 | GEN-2018-089 | 230 | 11.124 | 11.1335 | 0.0095
GEN-2018-099 | 05 SOUTWEST | 763483 | GEN-2019-003 | 230 | 8.9496 | 8.9679 | 0.0183
GEN-2018-099 | 05 SOUTWEST | 763516 | GEN-2019-011 | 345 | 9.8668 | 9.8699 | 0.0031
GEN-2019-003 | 05 SOUTWEST | 515458 | BORDER 7 | 345 | 7.4345 | 7.4346 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 515554 | BVRCNTY7 | 345 | 12.8493 | 12.8495 | 0.0002
GEN-2019-003 | 05 SOUTWEST | 523095 | HITCHLAND 6 | 230 | 14.0633 | 14.0634 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 523097 | HITCHLAND 7 | 345 | 13.5622 | 13.5626 | 0.0004
GEN-2019-003 | 05 SOUTWEST | 523101 | NOBLE_WND 7 | 345 | 13.5148 | 13.5153 | 0.0005
GEN-2019-003 | 05 SOUTWEST | 523112 | NOVUS1 7 | 345 | 13.3308 | 13.3313 | 0.0005
GEN-2019-003 | 05 SOUTWEST | 523323 | MCDWL_CREEK6 | 230 | 9.4097 | 9.4109 | 0.0012
GEN-2019-003 | 05 SOUTWEST | 523823 | CARPENTER 7 | 345 | 6.5517 | 6.5517 | 0
GEN-2019-003 | 05 SOUTWEST | 523853 | FINNEY 7 | 345 | 8.9671 | 8.9671 | 0
GEN-2019-003 | 05 SOUTWEST | 523869 | CHAN+TASCOS6 | 230 | 4.4558 | 4.4561 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 523959 | POTTER_CO 6 | 230 | 23.0449 | 23.0545 | 0.0096
GEN-2019-003 | 05 SOUTWEST | 523961 | POTTER_CO 7 | 345 | 11.0534 | 11.0581 | 0.0047
GEN-2019-003 | 05 SOUTWEST | 523979 | HARRNG_EST 6 | 230 | 28.1473 | 28.1552 | 0.0079
GEN-2019-003 | 05 SOUTWEST | 524010 | ROLLHILLS 6 | 230 | 21.0211 | 21.0269 | 0.0058
GEN-2019-003 | 05 SOUTWEST | 524044 | NICHOLS 6 | 230 | 27.2421 | 27.2494 | 0.0073
GEN-2019-003 | 05 SOUTWEST | 524267 | BUSHLAND 6 | 230 | 10.4057 | 10.4097 | 0.004
GEN-2019-003 | 05 SOUTWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3333 | 5.3342 | 0.0009
GEN-2019-003 | 05 SOUTWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3333 | 5.3342 | 0.0009
GEN-2019-003 | 05 SOUTWEST | 524365 | RANDALL 6 | 230 | 15.1399 | 15.143 | 0.0031
GEN-2019-003 | 05 SOUTWEST | 524414 | AMA_SOUTH 3 | 115 | 17.3845 | 17.3868 | 0.0023
GEN-2019-003 | 05 SOUTWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2388 | 14.2417 | 0.0029
GEN-2019-003 | 05 SOUTWEST | 524472 | LOPEZ 3 | 115 | 2.4039 | 2.4055 | 0.0016
GEN-2019-003 | 05 SOUTWEST | 524486 | CAPROCK 3 | 115 | 2.7722 | 2.7743 | 0.0021
GEN-2019-003 | 05 SOUTWEST | 524502 | NORTON 3 | 115 | 3.0709 | 3.0743 | 0.0034
GEN-2019-003 | 05 SOUTWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5404 | 2.5423 | 0.0019
GEN-2019-003 | 05 SOUTWEST | 524619 | DFSMTH_EST 3 | 115 | 11.7294 | 11.741 | 0.0116
GEN-2019-003 | 05 SOUTWEST | 524622 | DFSMTH_WST 3 | 115 | 11.7323 | 11.7439 | 0.0116
GEN-2019-003 | 05 SOUTWEST | 524623 | DEAFSMITH 6 | 230 | 8.4133 | 8.4216 | 0.0083
GEN-2019-003 | 05 SOUTWEST | 524662 | PARMER_CO 3 | 115 | 4.5739 | 4.5909 | 0.017
GEN-2019-003 | 05 SOUTWEST | 524664 | DS-#24 +3 | 115 | 4.5114 | 4.5271 | 0.0157
GEN-2019-003 | 05 SOUTWEST | 524669 | DS-#20 3 | 115 | 5.4811 | 5.513 | 0.0319
GEN-2019-003 | 05 SOUTWEST | 524746 | CASTRO_CNTY3 | 115 | 10.1552 | 10.1608 | 0.0056
GEN-2019-003 | 05 SOUTWEST | 524764 | NORRIS_TP 3 | 115 | 11.1732 | 11.3615 | 0.1883
GEN-2019-003 | 05 SOUTWEST | 524768 | PLSNT_HILL 3 | 115 | 10.7474 | 10.9246 | 0.1772
GEN-2019-003 | 05 SOUTWEST | 524770 | PLSNT_HILL 6 | 230 | 6.4731 | 6.6398 | 0.1667
GEN-2019-003 | 05 SOUTWEST | 524773 | E_CLOVIS 3 | 115 | 9.056 | 9.1806 | 0.1246
GEN-2019-003 | 05 SOUTWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.7051 | 7.7953 | 0.0902
GEN-2019-003 | 05 SOUTWEST | 524777 | N_CLOVIS 3 | 115 | 6.9527 | 7.0266 | 0.0739
GEN-2019-003 | 05 SOUTWEST | 524783 | W_CLOVIS 2 | 69 | 2.5467 | 2.5524 | 0.0057
GEN-2019-003 | 05 SOUTWEST | 524784 | W_CLOVIS 3 | 115 | 6.532 | 6.5979 | 0.0659
GEN-2019-003 | 05 SOUTWEST | 524790 | CANNON_TP 3 | 115 | 6.1772 | 6.2379 | 0.0607
GEN-2019-003 | 05 SOUTWEST | 524794 | CANNONAFB 3 | 115 | 5.8059 | 5.8594 | 0.0535
GEN-2019-003 | 05 SOUTWEST | 524797 | PERIMETER 3 | 115 | 6.6338 | 6.7079 | 0.0741
GEN-2019-003 | 05 SOUTWEST | 524801 | NORRIS 3 | 115 | 10.2419 | 10.4005 | 0.1586
GEN-2019-003 | 05 SOUTWEST | 524808 | FE-CLVS_INT3 | 115 | 7.1763 | 7.2542 | 0.0779
GEN-2019-003 | 05 SOUTWEST | 524821 | CURRY 2 | 69 | 4.5042 | 4.5215 | 0.0173
GEN-2019-003 | 05 SOUTWEST | 524822 | CURRY 3 | 115 | 11.2031 | 11.3923 | 0.1892
GEN-2019-003 | 05 SOUTWEST | 524831 | FE-HOLLAND 3 | 115 | 9.3587 | 9.4918 | 0.1331
GEN-2019-003 | 05 SOUTWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.6412 | 10.8119 | 0.1707
GEN-2019-003 | 05 SOUTWEST | 524846 | FARWELL 2 | 69 | 2.2092 | 2.2136 | 0.0044
GEN-2019-003 | 05 SOUTWEST | 524853 | DS-#10 +2 | 69 | 1.7986 | 1.7994 | 0.0008
GEN-2019-003 | 05 SOUTWEST | 524863 | FE-CHZPLT 3 | 115 | 7.9997 | 8.1043 | 0.1046
GEN-2019-003 | 05 SOUTWEST | 524874 | OASIS 3 | 115 | 9.8126 | 9.9847 | 0.1721
GEN-2019-003 | 05 SOUTWEST | 524875 | OASIS 6 | 230 | 7.8492 | 8.0854 | 0.2362
GEN-2019-003 | 05 SOUTWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.9835 | 5.0165 | 0.033
GEN-2019-003 | 05 SOUTWEST | 524889 | SN_JUAN_WND6 | 230 | 4.7721 | 4.8012 | 0.0291
GEN-2019-003 | 05 SOUTWEST | 524908 | ROOSEVELT 3 | 115 | 10.8029 | 11.0207 | 0.2178
GEN-2019-003 | 05 SOUTWEST | 524909 | ROOSEVELT 6 | 230 | 9.5201 | 9.9404 | 0.4203
GEN-2019-003 | 05 SOUTWEST | 524923 | PORTALES 2 | 69 | 7.6791 | 7.7409 | 0.0618
GEN-2019-003 | 05 SOUTWEST | 524924 | PORTALES 3 | 115 | 7.585 | 7.6884 | 0.1034
GEN-2019-003 | 05 SOUTWEST | 524929 | RO-PORT_MTR2 | 69 | 7.6791 | 7.7409 | 0.0618
GEN-2019-003 | 05 SOUTWEST | 524934 | ZODIAC 2 | 69 | 5.649 | 5.6832 | 0.0342
GEN-2019-003 | 05 SOUTWEST | 524935 | KILGORE 3 | 115 | 6.2334 | 6.3029 | 0.0695
GEN-2019-003 | 05 SOUTWEST | 524941 | PORTALES#1 2 | 69 | 5.8977 | 5.9346 | 0.0369
GEN-2019-003 | 05 SOUTWEST | 524948 | PORTALES#2 2 | 69 | 5.0056 | 5.0326 | 0.027
GEN-2019-003 | 05 SOUTWEST | 524962 | S_PORTALES 2 | 69 | 4.4134 | 4.4346 | 0.0212
GEN-2019-003 | 05 SOUTWEST | 524963 | S_PORTALES 3 | 115 | 5.8654 | 5.9269 | 0.0615
GEN-2019-003 | 05 SOUTWEST | 524977 | GREYHOUND 3 | 115 | 5.7835 | 5.8433 | 0.0598
GEN-2019-003 | 05 SOUTWEST | 525008 | MULESH_CTY 2 | 69 | 4.037 | 4.0409 | 0.0039
GEN-2019-003 | 05 SOUTWEST | 525017 | EMULESH&VLY2 | 69 | 4.0135 | 4.0174 | 0.0039
GEN-2019-003 | 05 SOUTWEST | 525018 | MULESHVALLY3 | 115 | 5.1311 | 5.1411 | 0.01
GEN-2019-003 | 05 SOUTWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4599 | 5.4712 | 0.0113
GEN-2019-003 | 05 SOUTWEST | 525023 | BC-BAIL_MTR2 | 69 | 4.8738 | 4.8795 | 0.0057
GEN-2019-003 | 05 SOUTWEST | 525027 | BAILEYCO 2 | 69 | 4.8738 | 4.8795 | 0.0057
GEN-2019-003 | 05 SOUTWEST | 525028 | BAILEYCO 3 | 115 | 5.3554 | 5.3669 | 0.0115
GEN-2019-003 | 05 SOUTWEST | 525050 | BC-KELLEY +3 | 115 | 7.8648 | 7.8695 | 0.0047
GEN-2019-003 | 05 SOUTWEST | 525056 | BC-EARTH 3 | 115 | 8.2047 | 8.2104 | 0.0057
GEN-2019-003 | 05 SOUTWEST | 525124 | HART_INDUST3 | 115 | 7.7546 | 7.7574 | 0.0028
GEN-2019-003 | 05 SOUTWEST | 525192 | KRESS_INT 3 | 115 | 12.3312 | 12.3354 | 0.0042
GEN-2019-003 | 05 SOUTWEST | 525212 | SWISHER 3 | 115 | 11.7784 | 11.7821 | 0.0037
GEN-2019-003 | 05 SOUTWEST | 525213 | SWISHER 6 | 230 | 10.8387 | 10.8441 | 0.0054
GEN-2019-003 | 05 SOUTWEST | 525326 | COX 3 | 115 | 6.6306 | 6.6317 | 0.0011
GEN-2019-003 | 05 SOUTWEST | 525393 | ROCKYFORD 3 | 115 | 8.5411 | 8.5483 | 0.0072
GEN-2019-003 | 05 SOUTWEST | 525414 | LAMTON 3 | 115 | 7.8417 | 7.8453 | 0.0036
GEN-2019-003 | 05 SOUTWEST | 525440 | LC-S_OLTON+3 | 115 | 7.2609 | 7.2647 | 0.0038
GEN-2019-003 | 05 SOUTWEST | 525446 | RKYFORD_TP 3 | 115 | 9.4511 | 9.4599 | 0.0088
GEN-2019-003 | 05 SOUTWEST | 525453 | HALE_CNTY 2 | 69 | 6.7608 | 6.7619 | 0.0011
GEN-2019-003 | 05 SOUTWEST | 525454 | HALE_CNTY 3 | 115 | 10.5558 | 10.5599 | 0.0041
GEN-2019-003 | 05 SOUTWEST | 525460 | NEWHART 3 | 115 | 15.1817 | 15.1909 | 0.0092
GEN-2019-003 | 05 SOUTWEST | 525461 | NEWHART 6 | 230 | 11.4433 | 11.4527 | 0.0094
GEN-2019-003 | 05 SOUTWEST | 525480 | PLANT_X 3 | 115 | 15.4802 | 15.507 | 0.0268
GEN-2019-003 | 05 SOUTWEST | 525481 | PLANT_X 6 | 230 | 23.7399 | 23.8515 | 0.1116
GEN-2019-003 | 05 SOUTWEST | 525531 | TOLK 6 | 230 | 30.4711 | 30.7299 | 0.2588
GEN-2019-003 | 05 SOUTWEST | 525549 | TOLK 7 | 345 | 13.4212 | 13.4662 | 0.045
GEN-2019-003 | 05 SOUTWEST | 525584 | BLUECLDCOL 6 | 230 | 10.6944 | 10.7184 | 0.024
GEN-2019-003 | 05 SOUTWEST | 525585 | BLUECLDPOI 6 | 230 | 11.2872 | 11.3141 | 0.0269
GEN-2019-003 | 05 SOUTWEST | 525586 | NEEDMORE 6 | 230 | 11.2872 | 11.3141 | 0.0269
GEN-2019-003 | 05 SOUTWEST | 525613 | W_LITTLFLD 2 | 69 | 3.1706 | 3.1712 | 0.0006
GEN-2019-003 | 05 SOUTWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3267 | 4.3279 | 0.0012
GEN-2019-003 | 05 SOUTWEST | 525635 | LAMB_CNTY 2 | 69 | 6.1216 | 6.1238 | 0.0022
GEN-2019-003 | 05 SOUTWEST | 525636 | LAMB_CNTY 3 | 115 | 8.44 | 8.4473 | 0.0073
GEN-2019-003 | 05 SOUTWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9093 | 5.917 | 0.0077
GEN-2019-003 | 05 SOUTWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1527 | 5.1543 | 0.0016
GEN-2019-003 | 05 SOUTWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.7996 | 4.8009 | 0.0013
GEN-2019-003 | 05 SOUTWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1723 | 3.1724 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 525738 | HALECENTER 2 | 69 | 2.6086 | 2.6087 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 525763 | CALLAHAN 3 | 115 | 5.8395 | 5.8402 | 0.0007
GEN-2019-003 | 05 SOUTWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4072 | 5.4075 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.5114 | 6.5121 | 0.0007
GEN-2019-003 | 05 SOUTWEST | 525803 | BLANCO 3 | 115 | 5.2381 | 5.2385 | 0.0004
GEN-2019-003 | 05 SOUTWEST | 525816 | TUCO_INT2 2 | 69 | 4.7712 | 4.7714 | 0.0002
GEN-2019-003 | 05 SOUTWEST | 525826 | TUCO_INT 2 | 69 | 8.2036 | 8.2042 | 0.0006
GEN-2019-003 | 05 SOUTWEST | 525828 | TUCO_INT 3 | 115 | 19.8002 | 19.806 | 0.0058
GEN-2019-003 | 05 SOUTWEST | 525830 | TUCO_INT 6 | 230 | 21.8961 | 21.909 | 0.0129
GEN-2019-003 | 05 SOUTWEST | 525832 | TUCO_INT 7 | 345 | 13.9887 | 13.9936 | 0.0049
GEN-2019-003 | 05 SOUTWEST | 525840 | ANTELOPE_1 6 | 230 | 21.7198 | 21.7325 | 0.0127
GEN-2019-003 | 05 SOUTWEST | 525850 | ELK_CT1 | 345 | 13.8888 | 13.8937 | 0.0049
GEN-2019-003 | 05 SOUTWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.75 | 2.75 | 0
GEN-2019-003 | 05 SOUTWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5203 | 3.5204 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 525926 | CROSBY 3 | 115 | 4.9206 | 4.9209 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 525957 | HALE_WNDCL16 | 230 | 10.6982 | 10.701 | 0.0028
GEN-2019-003 | 05 SOUTWEST | 526019 | HOCKLEY 2 | 69 | 5.3923 | 5.3931 | 0.0008
GEN-2019-003 | 05 SOUTWEST | 526020 | HOCKLEY 3 | 115 | 5.6546 | 5.6562 | 0.0016
GEN-2019-003 | 05 SOUTWEST | 526036 | LC-OPDYKE 3 | 115 | 5.9366 | 5.9382 | 0.0016
GEN-2019-003 | 05 SOUTWEST | 526076 | STANTON_W 3 | 115 | 9.1745 | 9.1756 | 0.0011
GEN-2019-003 | 05 SOUTWEST | 526109 | SP-ERSKINE 3 | 115 | 11.1275 | 11.129 | 0.0015
GEN-2019-003 | 05 SOUTWEST | 526146 | INDIANA 3 | 115 | 9.5471 | 9.5483 | 0.0012
GEN-2019-003 | 05 SOUTWEST | 526159 | CARLISLE 2 | 69 | 2.7514 | 2.7515 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 526160 | CARLISLE 3 | 115 | 12.8007 | 12.8027 | 0.002
GEN-2019-003 | 05 SOUTWEST | 526161 | CARLISLE 6 | 230 | 10.693 | 10.6959 | 0.0029
GEN-2019-003 | 05 SOUTWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.4715 | 11.473 | 0.0015
GEN-2019-003 | 05 SOUTWEST | 526192 | MURPHY 3 | 115 | 10.5581 | 10.5593 | 0.0012
GEN-2019-003 | 05 SOUTWEST | 526268 | LUBBCK_STH 3 | 115 | 18.122 | 18.1246 | 0.0026
GEN-2019-003 | 05 SOUTWEST | 526269 | LUBBCK_STH 6 | 230 | 15.4512 | 15.4547 | 0.0035
GEN-2019-003 | 05 SOUTWEST | 526297 | LUBBCK_EST 2 | 69 | 8.7368 | 8.7371 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 526298 | LUBBCK_EST 3 | 115 | 14.8866 | 14.8886 | 0.002
GEN-2019-003 | 05 SOUTWEST | 526299 | LUBBCK_EST 6 | 230 | 11.4719 | 11.4736 | 0.0017
GEN-2019-003 | 05 SOUTWEST | 526337 | JONES 6 | 230 | 17.0971 | 17.1008 | 0.0037
GEN-2019-003 | 05 SOUTWEST | 526424 | PACIFIC 3 | 115 | 9.2332 | 9.2352 | 0.002
GEN-2019-003 | 05 SOUTWEST | 526434 | SUNDOWN 3 | 115 | 10.7973 | 10.8003 | 0.003
GEN-2019-003 | 05 SOUTWEST | 526435 | SUNDOWN 6 | 230 | 11.5484 | 11.555 | 0.0066
GEN-2019-003 | 05 SOUTWEST | 526445 | AMOCO_TP 3 | 115 | 10.1927 | 10.1952 | 0.0025
GEN-2019-003 | 05 SOUTWEST | 526460 | AMOCO_SS 6 | 230 | 10.2662 | 10.2709 | 0.0047
GEN-2019-003 | 05 SOUTWEST | 526524 | WOLFFORTH 3 | 115 | 11.3353 | 11.3369 | 0.0016
GEN-2019-003 | 05 SOUTWEST | 526525 | WOLFFORTH 6 | 230 | 13.0204 | 13.0245 | 0.0041
GEN-2019-003 | 05 SOUTWEST | 526676 | GRASSLAND 3 | 115 | 7.2503 | 7.2506 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 526677 | GRASSLAND 6 | 230 | 6.2451 | 6.2456 | 0.0005
GEN-2019-003 | 05 SOUTWEST | 526679 | CIRRUS_WND 6 | 230 | 4.8946 | 4.8949 | 0.0003
GEN-2019-003 | 05 SOUTWEST | 526784 | AMOCOWASSON6 | 230 | 16.5546 | 16.5582 | 0.0036
GEN-2019-003 | 05 SOUTWEST | 526792 | PRENTICE 3 | 115 | 6.3125 | 6.3129 | 0.0004
GEN-2019-003 | 05 SOUTWEST | 526928 | PLAINS_INT 3 | 115 | 10.2936 | 10.2947 | 0.0011
GEN-2019-003 | 05 SOUTWEST | 526934 | YOAKUM 3 | 115 | 19.2955 | 19.2991 | 0.0036
GEN-2019-003 | 05 SOUTWEST | 526935 | YOAKUM 6 | 230 | 20.8098 | 20.8189 | 0.0091
GEN-2019-003 | 05 SOUTWEST | 526936 | YOAKUM_345 | 345 | 10.501 | 10.5046 | 0.0036
GEN-2019-003 | 05 SOUTWEST | 527009 | BRU_SUB 6 | 230 | 16.5425 | 16.5471 | 0.0046
GEN-2019-003 | 05 SOUTWEST | 527010 | OXYBRU 6 | 230 | 16.387 | 16.3916 | 0.0046
GEN-2019-003 | 05 SOUTWEST | 527011 | XTO_MAHONEY6 | 230 | 16.2383 | 16.2424 | 0.0041
GEN-2019-003 | 05 SOUTWEST | 527027 | INK_BASIN 3 | 115 | 13.7041 | 13.7053 | 0.0012
GEN-2019-003 | 05 SOUTWEST | 527028 | INK_BASIN 6 | 230 | 11.7921 | 11.7946 | 0.0025
GEN-2019-003 | 05 SOUTWEST | 527041 | ARCO_TP 3 | 115 | 14.3057 | 14.3071 | 0.0014
GEN-2019-003 | 05 SOUTWEST | 527146 | MUSTANG 3 | 115 | 24.9069 | 24.9101 | 0.0032
GEN-2019-003 | 05 SOUTWEST | 527149 | MUSTANG 6 | 230 | 19.0027 | 19.0068 | 0.0041
GEN-2019-003 | 05 SOUTWEST | 527151 | GS-MUSTANG 6 | 230 | 19.0027 | 19.0068 | 0.0041
GEN-2019-003 | 05 SOUTWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3302 | 8.3307 | 0.0005
GEN-2019-003 | 05 SOUTWEST | 527276 | SEMINOLE 6 | 230 | 8.8907 | 8.8916 | 0.0009
GEN-2019-003 | 05 SOUTWEST | 527455 | RSWL_SLRCOL3 | 115 | 7.4051 | 7.4148 | 0.0097
GEN-2019-003 | 05 SOUTWEST | 527470 | CHVS_SLRCOL3 | 115 | 7.2299 | 7.2391 | 0.0092
GEN-2019-003 | 05 SOUTWEST | 527482 | CHAVES_CNTY3 | 115 | 7.4798 | 7.4897 | 0.0099
GEN-2019-003 | 05 SOUTWEST | 527483 | CHAVES_CNTY6 | 230 | 4.5682 | 4.5773 | 0.0091
GEN-2019-003 | 05 SOUTWEST | 527501 | URTON 3 | 115 | 6.2456 | 6.2523 | 0.0067
GEN-2019-003 | 05 SOUTWEST | 527509 | PRICE_TAP 3 | 115 | 5.7922 | 5.798 | 0.0058
GEN-2019-003 | 05 SOUTWEST | 527546 | SAMSON 3 | 115 | 5.8682 | 5.8738 | 0.0056
GEN-2019-003 | 05 SOUTWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.3561 | 10.3648 | 0.0087
GEN-2019-003 | 05 SOUTWEST | 527610 | SAGA_SCOL 7 | 345 | 10.3561 | 10.3648 | 0.0087
GEN-2019-003 | 05 SOUTWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.8142 | 8.8205 | 0.0063
GEN-2019-003 | 05 SOUTWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.103 | 10.1115 | 0.0085
GEN-2019-003 | 05 SOUTWEST | 527656 | CROSSROADS 7 | 345 | 11.6149 | 11.6265 | 0.0116
GEN-2019-003 | 05 SOUTWEST | 527793 | EDDY_STH 3 | 115 | 12.3575 | 12.363 | 0.0055
GEN-2019-003 | 05 SOUTWEST | 527798 | EDDY_NTH 3 | 115 | 12.3575 | 12.363 | 0.0055
GEN-2019-003 | 05 SOUTWEST | 527799 | EDDY_NORTH 6 | 230 | 9.8986 | 9.9052 | 0.0066
GEN-2019-003 | 05 SOUTWEST | 527802 | EDDY_CNTY 7 | 345 | 7.5924 | 7.5969 | 0.0045
GEN-2019-003 | 05 SOUTWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.2928 | 18.2985 | 0.0057
GEN-2019-003 | 05 SOUTWEST | 527894 | HOBBS_INT 6 | 230 | 20.333 | 20.34 | 0.007
GEN-2019-003 | 05 SOUTWEST | 527896 | HOBBS_INT 7 | 345 | 12.3026 | 12.3104 | 0.0078
GEN-2019-003 | 05 SOUTWEST | 527965 | KIOWA 7 | 345 | 9.1963 | 9.2013 | 0.005
GEN-2019-003 | 05 SOUTWEST | 528027 | RDRUNNER 7 | 345 | 9.1934 | 9.1978 | 0.0044
GEN-2019-003 | 05 SOUTWEST | 528095 | 7-RIVERS 6 | 230 | 6.757 | 6.7594 | 0.0024
GEN-2019-003 | 05 SOUTWEST | 560756 | CEILO-TAP-N | 115 | 0.4779 | 0.478 | 0.0001
GEN-2019-003 | 05 SOUTWEST | 576397 | G10014G11022 | 345 | 9.8289 | 9.8291 | 0.0002
GEN-2019-003 | 05 SOUTWEST | 583280 | A12-02&13-05 | 115 | 1.0766 | 1.0773 | 0.0007
GEN-2019-003 | 05 SOUTWEST | 599950 | LAMAR7 | 345 | 2.3488 | 2.3488 | 0
GEN-2019-003 | 05 SOUTWEST | 599951 | LAMAR 6 | 345 | 13.4752 | 13.4752 | 0
GEN-2019-003 | 05 SOUTWEST | 599955 | PNM-DC6 | 230 | 9.5201 | 9.9404 | 0.4203
GEN-2019-003 | 05 SOUTWEST | 599956 | PNM-DC7 | 345 | 15.1757 | 15.1757 | 0
GEN-2019-003 | 05 SOUTWEST | 599960 | EPTNP-D6 | 230 | 9.8986 | 9.9052 | 0.0066
GEN-2019-003 | 05 SOUTWEST | 599961 | EPTNP 7 | 345 | 13.486 | 13.486 | 0
GEN-2019-003 | 05 SOUTWEST | 755000 | WWDBORDT | 345 | 10.2588 | 10.259 | 0.0002
GEN-2019-003 | 05 SOUTWEST | 760494 | GEN-2017-146 | 230 | 7.7699 | 7.7777 | 0.0078
GEN-2019-003 | 05 SOUTWEST | 760498 | G17-146-TAP | 230 | 8.0701 | 8.0786 | 0.0085
GEN-2019-003 | 05 SOUTWEST | 762132 | GEN-2017-158 | 230 | 14.0566 | 14.1047 | 0.0481
GEN-2019-003 | 05 SOUTWEST | 762216 | G17-151TAP | 345 | 8.5341 | 8.5355 | 0.0014
GEN-2019-003 | 05 SOUTWEST | 762217 | GEN-2017-151 | 345 | 6.2747 | 6.2754 | 0.0007
GEN-2019-003 | 05 SOUTWEST | 762467 | G18-015-TAP | 345 | 5.3209 | 5.3211 | 0.0002
GEN-2019-003 | 05 SOUTWEST | 763186 | GEN-2018-089 | 230 | 11.1246 | 11.1335 | 0.0089
GEN-2019-003 | 05 SOUTWEST | 763483 | GEN-2019-003 | 230 | 8.544 | 8.9679 | 0.4239
GEN-2019-003 | 05 SOUTWEST | 763516 | GEN-2019-011 | 345 | 9.8667 | 9.8699 | 0.0032
GEN-2019-011 | 05 SOUTWEST | 511456 | O.K.U.-7 | 345 | 5.8447 | 5.8457 | 0.001
GEN-2019-011 | 05 SOUTWEST | 511468 | L.E.S.-7 | 345 | 12.9346 | 12.9352 | 0.0006
GEN-2019-011 | 05 SOUTWEST | 511553 | CHISHOLM7 | 345 | 10.266 | 10.2669 | 0.0009
GEN-2019-011 | 05 SOUTWEST | 511557 | CHISHOLM6 | 230 | 11.2592 | 11.2597 | 0.0005
GEN-2019-011 | 05 SOUTWEST | 511565 | OKLAUN HVDC7 | 345 | 5.8271 | 5.828 | 0.0009
GEN-2019-011 | 05 SOUTWEST | 515375 | WWRDEHV7 | 345 | 19.0117 | 19.012 | 0.0003
GEN-2019-011 | 05 SOUTWEST | 515376 | WWRDEHV4 | 138 | 25.3838 | 25.384 | 0.0002
GEN-2019-011 | 05 SOUTWEST | 515407 | TATONGA7 | 345 | 16.4722 | 16.4723 | 0.0001
GEN-2019-011 | 05 SOUTWEST | 515458 | BORDER 7 | 345 | 7.4337 | 7.4346 | 0.0009
GEN-2019-011 | 05 SOUTWEST | 515852 | DGRASSE7 | 345 | 13.9913 | 13.9914 | 0.0001
GEN-2019-011 | 05 SOUTWEST | 515961 | GUTHRIE7 | 345 | 11.8591 | 11.8592 | 0.0001
GEN-2019-011 | 05 SOUTWEST | 523097 | HITCHLAND 7 | 345 | 13.5626 | 13.5626 | 0
GEN-2019-011 | 05 SOUTWEST | 523959 | POTTER_CO 6 | 230 | 23.0513 | 23.0545 | 0.0032
GEN-2019-011 | 05 SOUTWEST | 523961 | POTTER_CO 7 | 345 | 11.0565 | 11.0581 | 0.0016
GEN-2019-011 | 05 SOUTWEST | 524044 | NICHOLS 6 | 230 | 27.2467 | 27.2494 | 0.0027
GEN-2019-011 | 05 SOUTWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3339 | 5.3342 | 0.0003
GEN-2019-011 | 05 SOUTWEST | 524365 | RANDALL 6 | 230 | 15.1418 | 15.143 | 0.0012
GEN-2019-011 | 05 SOUTWEST | 524414 | AMA_SOUTH 3 | 115 | 17.386 | 17.3868 | 0.0008
GEN-2019-011 | 05 SOUTWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2405 | 14.2417 | 0.0012
GEN-2019-011 | 05 SOUTWEST | 524770 | PLSNT_HILL 6 | 230 | 6.6383 | 6.6398 | 0.0015
GEN-2019-011 | 05 SOUTWEST | 524875 | OASIS 6 | 230 | 8.083 | 8.0854 | 0.0024
GEN-2019-011 | 05 SOUTWEST | 524908 | ROOSEVELT 3 | 115 | 11.0186 | 11.0207 | 0.0021
GEN-2019-011 | 05 SOUTWEST | 524909 | ROOSEVELT 6 | 230 | 9.9369 | 9.9404 | 0.0035
GEN-2019-011 | 05 SOUTWEST | 525192 | KRESS_INT 3 | 115 | 12.3328 | 12.3354 | 0.0026
GEN-2019-011 | 05 SOUTWEST | 525212 | SWISHER 3 | 115 | 11.7797 | 11.7821 | 0.0024
GEN-2019-011 | 05 SOUTWEST | 525213 | SWISHER 6 | 230 | 10.8398 | 10.8441 | 0.0043
GEN-2019-011 | 05 SOUTWEST | 525326 | COX 3 | 115 | 6.6307 | 6.6317 | 0.001
GEN-2019-011 | 05 SOUTWEST | 525414 | LAMTON 3 | 115 | 7.8441 | 7.8453 | 0.0012
GEN-2019-011 | 05 SOUTWEST | 525453 | HALE_CNTY 2 | 69 | 6.7612 | 6.7619 | 0.0007
GEN-2019-011 | 05 SOUTWEST | 525454 | HALE_CNTY 3 | 115 | 10.5574 | 10.5599 | 0.0025
GEN-2019-011 | 05 SOUTWEST | 525460 | NEWHART 3 | 115 | 15.1875 | 15.1909 | 0.0034
GEN-2019-011 | 05 SOUTWEST | 525461 | NEWHART 6 | 230 | 11.449 | 11.4527 | 0.0037
GEN-2019-011 | 05 SOUTWEST | 525480 | PLANT_X 3 | 115 | 15.5025 | 15.507 | 0.0045
GEN-2019-011 | 05 SOUTWEST | 525481 | PLANT_X 6 | 230 | 23.8295 | 23.8515 | 0.022
GEN-2019-011 | 05 SOUTWEST | 525531 | TOLK 6 | 230 | 30.6915 | 30.7299 | 0.0384
GEN-2019-011 | 05 SOUTWEST | 525549 | TOLK 7 | 345 | 13.4498 | 13.4662 | 0.0164
GEN-2019-011 | 05 SOUTWEST | 525584 | BLUECLDCOL 6 | 230 | 10.7095 | 10.7184 | 0.0089
GEN-2019-011 | 05 SOUTWEST | 525585 | BLUECLDPOI 6 | 230 | 11.3041 | 11.3141 | 0.01
GEN-2019-011 | 05 SOUTWEST | 525586 | NEEDMORE 6 | 230 | 11.3041 | 11.3141 | 0.01
GEN-2019-011 | 05 SOUTWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4453 | 8.4473 | 0.002
GEN-2019-011 | 05 SOUTWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9154 | 5.917 | 0.0016
GEN-2019-011 | 05 SOUTWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1721 | 3.1724 | 0.0003
GEN-2019-011 | 05 SOUTWEST | 525738 | HALECENTER 2 | 69 | 2.6085 | 2.6087 | 0.0002
GEN-2019-011 | 05 SOUTWEST | 525763 | CALLAHAN 3 | 115 | 5.8393 | 5.8402 | 0.0009
GEN-2019-011 | 05 SOUTWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.407 | 5.4075 | 0.0005
GEN-2019-011 | 05 SOUTWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.511 | 6.5121 | 0.0011
GEN-2019-011 | 05 SOUTWEST | 525803 | BLANCO 3 | 115 | 5.2378 | 5.2385 | 0.0007
GEN-2019-011 | 05 SOUTWEST | 525816 | TUCO_INT2 2 | 69 | 4.7709 | 4.7714 | 0.0005
GEN-2019-011 | 05 SOUTWEST | 525826 | TUCO_INT 2 | 69 | 8.2027 | 8.2042 | 0.0015
GEN-2019-011 | 05 SOUTWEST | 525828 | TUCO_INT 3 | 115 | 19.7902 | 19.806 | 0.0158
GEN-2019-011 | 05 SOUTWEST | 525830 | TUCO_INT 6 | 230 | 21.8609 | 21.909 | 0.0481
GEN-2019-011 | 05 SOUTWEST | 525832 | TUCO_INT 7 | 345 | 13.9452 | 13.9936 | 0.0484
GEN-2019-011 | 05 SOUTWEST | 525840 | ANTELOPE_1 6 | 230 | 21.6852 | 21.7325 | 0.0473
GEN-2019-011 | 05 SOUTWEST | 525850 | ELK_CT1 | 345 | 13.8461 | 13.8937 | 0.0476
GEN-2019-011 | 05 SOUTWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7499 | 2.75 | 0.0001
GEN-2019-011 | 05 SOUTWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5201 | 3.5204 | 0.0003
GEN-2019-011 | 05 SOUTWEST | 525926 | CROSBY 3 | 115 | 4.9203 | 4.9209 | 0.0006
GEN-2019-011 | 05 SOUTWEST | 525957 | HALE_WNDCL16 | 230 | 10.6907 | 10.701 | 0.0103
GEN-2019-011 | 05 SOUTWEST | 526036 | LC-OPDYKE 3 | 115 | 5.9362 | 5.9382 | 0.002
GEN-2019-011 | 05 SOUTWEST | 526076 | STANTON_W 3 | 115 | 9.172 | 9.1756 | 0.0036
GEN-2019-011 | 05 SOUTWEST | 526109 | SP-ERSKINE 3 | 115 | 11.1237 | 11.129 | 0.0053
GEN-2019-011 | 05 SOUTWEST | 526146 | INDIANA 3 | 115 | 9.5444 | 9.5483 | 0.0039
GEN-2019-011 | 05 SOUTWEST | 526159 | CARLISLE 2 | 69 | 2.7513 | 2.7515 | 0.0002
GEN-2019-011 | 05 SOUTWEST | 526160 | CARLISLE 3 | 115 | 12.7957 | 12.8027 | 0.007
GEN-2019-011 | 05 SOUTWEST | 526161 | CARLISLE 6 | 230 | 10.6859 | 10.6959 | 0.01
GEN-2019-011 | 05 SOUTWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.4672 | 11.473 | 0.0058
GEN-2019-011 | 05 SOUTWEST | 526192 | MURPHY 3 | 115 | 10.555 | 10.5593 | 0.0043
GEN-2019-011 | 05 SOUTWEST | 526268 | LUBBCK_STH 3 | 115 | 18.1159 | 18.1246 | 0.0087
GEN-2019-011 | 05 SOUTWEST | 526269 | LUBBCK_STH 6 | 230 | 15.4431 | 15.4547 | 0.0116
GEN-2019-011 | 05 SOUTWEST | 526297 | LUBBCK_EST 2 | 69 | 8.736 | 8.7371 | 0.0011
GEN-2019-011 | 05 SOUTWEST | 526298 | LUBBCK_EST 3 | 115 | 14.8826 | 14.8886 | 0.006
GEN-2019-011 | 05 SOUTWEST | 526299 | LUBBCK_EST 6 | 230 | 11.4679 | 11.4736 | 0.0057
GEN-2019-011 | 05 SOUTWEST | 526337 | JONES 6 | 230 | 17.0883 | 17.1008 | 0.0125
GEN-2019-011 | 05 SOUTWEST | 526350 | LEHMAN_TP 3 | 115 | 5.5839 | 5.5869 | 0.003
GEN-2019-011 | 05 SOUTWEST | 526424 | PACIFIC 3 | 115 | 9.2287 | 9.2352 | 0.0065
GEN-2019-011 | 05 SOUTWEST | 526434 | SUNDOWN 3 | 115 | 10.7916 | 10.8003 | 0.0087
GEN-2019-011 | 05 SOUTWEST | 526435 | SUNDOWN 6 | 230 | 11.5355 | 11.555 | 0.0195
GEN-2019-011 | 05 SOUTWEST | 526445 | AMOCO_TP 3 | 115 | 10.1874 | 10.1952 | 0.0078
GEN-2019-011 | 05 SOUTWEST | 526460 | AMOCO_SS 6 | 230 | 10.252 | 10.2709 | 0.0189
GEN-2019-011 | 05 SOUTWEST | 526491 | LG-CLAUENE 3 | 115 | 8.1582 | 8.1635 | 0.0053
GEN-2019-011 | 05 SOUTWEST | 526524 | WOLFFORTH 3 | 115 | 11.3304 | 11.3369 | 0.0065
GEN-2019-011 | 05 SOUTWEST | 526525 | WOLFFORTH 6 | 230 | 13.0105 | 13.0245 | 0.014
GEN-2019-011 | 05 SOUTWEST | 526676 | GRASSLAND 3 | 115 | 7.2495 | 7.2506 | 0.0011
GEN-2019-011 | 05 SOUTWEST | 526677 | GRASSLAND 6 | 230 | 6.2439 | 6.2456 | 0.0017
GEN-2019-011 | 05 SOUTWEST | 526679 | CIRRUS_WND 6 | 230 | 4.8939 | 4.8949 | 0.001
GEN-2019-011 | 05 SOUTWEST | 526735 | TERRY_CNTY 2 | 69 | 7.1337 | 7.1362 | 0.0025
GEN-2019-011 | 05 SOUTWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1147 | 11.1253 | 0.0106
GEN-2019-011 | 05 SOUTWEST | 526784 | AMOCOWASSON6 | 230 | 16.4694 | 16.5582 | 0.0888
GEN-2019-011 | 05 SOUTWEST | 526792 | PRENTICE 3 | 115 | 6.3079 | 6.3129 | 0.005
GEN-2019-011 | 05 SOUTWEST | 526928 | PLAINS_INT 3 | 115 | 10.2762 | 10.2947 | 0.0185
GEN-2019-011 | 05 SOUTWEST | 526934 | YOAKUM 3 | 115 | 19.2289 | 19.2991 | 0.0702
GEN-2019-011 | 05 SOUTWEST | 526935 | YOAKUM 6 | 230 | 20.5865 | 20.8189 | 0.2324
GEN-2019-011 | 05 SOUTWEST | 526936 | YOAKUM_345 | 345 | 10.077 | 10.5046 | 0.4276
GEN-2019-011 | 05 SOUTWEST | 526944 | LG-PLAINS 3 | 115 | 8.1433 | 8.1541 | 0.0108
GEN-2019-011 | 05 SOUTWEST | 527009 | BRU_SUB 6 | 230 | 16.4308 | 16.5471 | 0.1163
GEN-2019-011 | 05 SOUTWEST | 527010 | OXYBRU 6 | 230 | 16.2774 | 16.3916 | 0.1142
GEN-2019-011 | 05 SOUTWEST | 527011 | XTO_MAHONEY6 | 230 | 16.1392 | 16.2424 | 0.1032
GEN-2019-011 | 05 SOUTWEST | 527018 | BENNETT 3 | 115 | 14.383 | 14.4091 | 0.0261
GEN-2019-011 | 05 SOUTWEST | 527024 | ALLRED_SUB 3 | 115 | 11.2717 | 11.2858 | 0.0141
GEN-2019-011 | 05 SOUTWEST | 527027 | INK_BASIN 3 | 115 | 13.6833 | 13.7053 | 0.022
GEN-2019-011 | 05 SOUTWEST | 527028 | INK_BASIN 6 | 230 | 11.7457 | 11.7946 | 0.0489
GEN-2019-011 | 05 SOUTWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.8347 | 12.853 | 0.0183
GEN-2019-011 | 05 SOUTWEST | 527033 | XTO_CORNEL+3 | 115 | 12.9876 | 13.006 | 0.0184
GEN-2019-011 | 05 SOUTWEST | 527036 | SHELL_C2 3 | 115 | 15.4654 | 15.49 | 0.0246
GEN-2019-011 | 05 SOUTWEST | 527041 | ARCO_TP 3 | 115 | 14.281 | 14.3071 | 0.0261
GEN-2019-011 | 05 SOUTWEST | 527047 | OXY_WILRD1 3 | 115 | 11.4166 | 11.4332 | 0.0166
GEN-2019-011 | 05 SOUTWEST | 527051 | ODC_TP 3 | 115 | 14.4002 | 14.4264 | 0.0262
GEN-2019-011 | 05 SOUTWEST | 527062 | SHELL_CO2 3 | 115 | 17.4205 | 17.4538 | 0.0333
GEN-2019-011 | 05 SOUTWEST | 527080 | EL_PASO 3 | 115 | 17.1498 | 17.1816 | 0.0318
GEN-2019-011 | 05 SOUTWEST | 527105 | SAN_ANDS_TP3 | 115 | 17.9957 | 18.0278 | 0.0321
GEN-2019-011 | 05 SOUTWEST | 527125 | DENVER_CTY 2 | 69 | 8.8501 | 8.8546 | 0.0045
GEN-2019-011 | 05 SOUTWEST | 527130 | DENVER_N 3 | 115 | 23.2888 | 23.3418 | 0.053
GEN-2019-011 | 05 SOUTWEST | 527136 | DENVER_S 3 | 115 | 23.2888 | 23.3418 | 0.053
GEN-2019-011 | 05 SOUTWEST | 527146 | MUSTANG 3 | 115 | 24.8526 | 24.9101 | 0.0575
GEN-2019-011 | 05 SOUTWEST | 527149 | MUSTANG 6 | 230 | 18.9074 | 19.0068 | 0.0994
GEN-2019-011 | 05 SOUTWEST | 527151 | GS-MUSTANG 6 | 230 | 18.9074 | 19.0068 | 0.0994
GEN-2019-011 | 05 SOUTWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3223 | 8.3307 | 0.0084
GEN-2019-011 | 05 SOUTWEST | 527201 | SEAGRAVES 2 | 69 | 5.6157 | 5.6177 | 0.002
GEN-2019-011 | 05 SOUTWEST | 527202 | SEAGRAVES 3 | 115 | 9.6025 | 9.6124 | 0.0099
GEN-2019-011 | 05 SOUTWEST | 527238 | ROZ 3 | 115 | 11.5136 | 11.5281 | 0.0145
GEN-2019-011 | 05 SOUTWEST | 527242 | AMERADA 3 | 115 | 11.6728 | 11.6877 | 0.0149
GEN-2019-011 | 05 SOUTWEST | 527257 | FLATLAND 3 | 115 | 7.0454 | 7.0496 | 0.0042
GEN-2019-011 | 05 SOUTWEST | 527275 | SEMINOLE 3 | 115 | 14.7748 | 14.7988 | 0.024
GEN-2019-011 | 05 SOUTWEST | 527276 | SEMINOLE 6 | 230 | 8.8733 | 8.8916 | 0.0183
GEN-2019-011 | 05 SOUTWEST | 527286 | HIGGEAST 3 | 115 | 10.6955 | 10.7046 | 0.0091
GEN-2019-011 | 05 SOUTWEST | 527322 | GAINES 3 | 115 | 9.8252 | 9.8345 | 0.0093
GEN-2019-011 | 05 SOUTWEST | 527340 | DOSS 3 | 115 | 8.3262 | 8.3334 | 0.0072
GEN-2019-011 | 05 SOUTWEST | 527363 | HIGG 3 | 115 | 10.8853 | 10.8946 | 0.0093
GEN-2019-011 | 05 SOUTWEST | 527483 | CHAVES_CNTY6 | 230 | 4.5749 | 4.5773 | 0.0024
GEN-2019-011 | 05 SOUTWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.3385 | 10.3648 | 0.0263
GEN-2019-011 | 05 SOUTWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.3385 | 10.3648 | 0.0263
GEN-2019-011 | 05 SOUTWEST | 527610 | SAGA_SCOL 7 | 345 | 10.3385 | 10.3648 | 0.0263
GEN-2019-011 | 05 SOUTWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.8016 | 8.8205 | 0.0189
GEN-2019-011 | 05 SOUTWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0859 | 10.1115 | 0.0256
GEN-2019-011 | 05 SOUTWEST | 527656 | CROSSROADS 7 | 345 | 11.5913 | 11.6265 | 0.0352
GEN-2019-011 | 05 SOUTWEST | 527666 | RSVLT_COL1 7 | 345 | 8.8016 | 8.8205 | 0.0189
GEN-2019-011 | 05 SOUTWEST | 527667 | RSVLT_COL2 7 | 345 | 8.8016 | 8.8205 | 0.0189
GEN-2019-011 | 05 SOUTWEST | 527793 | EDDY_STH 3 | 115 | 12.3481 | 12.363 | 0.0149
GEN-2019-011 | 05 SOUTWEST | 527798 | EDDY_NTH 3 | 115 | 12.3481 | 12.363 | 0.0149
GEN-2019-011 | 05 SOUTWEST | 527799 | EDDY_NORTH 6 | 230 | 9.8857 | 9.9052 | 0.0195
GEN-2019-011 | 05 SOUTWEST | 527802 | EDDY_CNTY 7 | 345 | 7.5755 | 7.5969 | 0.0214
GEN-2019-011 | 05 SOUTWEST | 527864 | CUNNINHAM 3 | 115 | 28.4302 | 28.4729 | 0.0427
GEN-2019-011 | 05 SOUTWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.2452 | 18.2985 | 0.0533
GEN-2019-011 | 05 SOUTWEST | 527867 | CUNNIGHM_S 6 | 230 | 18.2452 | 18.2985 | 0.0533
GEN-2019-011 | 05 SOUTWEST | 527891 | HOBBS_INT 3 | 115 | 32.2757 | 32.3305 | 0.0548
GEN-2019-011 | 05 SOUTWEST | 527894 | HOBBS_INT 6 | 230 | 20.2628 | 20.34 | 0.0772
GEN-2019-011 | 05 SOUTWEST | 527896 | HOBBS_INT 7 | 345 | 12.2099 | 12.3104 | 0.1005
GEN-2019-011 | 05 SOUTWEST | 527930 | PCA 3 | 115 | 12.6117 | 12.629 | 0.0173
GEN-2019-011 | 05 SOUTWEST | 527961 | POTASH_JCT 2 | 69 | 9.8979 | 9.9047 | 0.0068
GEN-2019-011 | 05 SOUTWEST | 527962 | POTASH_JCT 3 | 115 | 17.9364 | 17.9754 | 0.039
GEN-2019-011 | 05 SOUTWEST | 527963 | POTASH_JCT 6 | 230 | 7.9895 | 8.0017 | 0.0122
GEN-2019-011 | 05 SOUTWEST | 527965 | KIOWA 7 | 345 | 9.1613 | 9.2013 | 0.04
GEN-2019-011 | 05 SOUTWEST | 527966 | KIOWA 3 | 115 | 17.9458 | 17.9851 | 0.0393
GEN-2019-011 | 05 SOUTWEST | 527999 | INTREPDW_TP3 | 115 | 14.6162 | 14.6421 | 0.0259
GEN-2019-011 | 05 SOUTWEST | 528013 | PHANTOM 3 | 115 | 13.538 | 13.5646 | 0.0266
GEN-2019-011 | 05 SOUTWEST | 528015 | PHANTOM 7 | 345 | 6.1511 | 6.168 | 0.0169
GEN-2019-011 | 05 SOUTWEST | 528016 | SAND_DUNES 3 | 115 | 7.816 | 7.8242 | 0.0082
GEN-2019-011 | 05 SOUTWEST | 528018 | RED_BLUFF 3 | 115 | 10.6957 | 10.7121 | 0.0164
GEN-2019-011 | 05 SOUTWEST | 528020 | BOPCO_PKRLK3 | 115 | 13.3418 | 13.3676 | 0.0258
GEN-2019-011 | 05 SOUTWEST | 528024 | RR_SVC_HV 3 | 115 | 14.4943 | 14.5271 | 0.0328
GEN-2019-011 | 05 SOUTWEST | 528025 | RDRUNNER 3 | 115 | 14.4943 | 14.5271 | 0.0328
GEN-2019-011 | 05 SOUTWEST | 528027 | RDRUNNER 7 | 345 | 9.1508 | 9.1978 | 0.047
GEN-2019-011 | 05 SOUTWEST | 528040 | BATTLE_AXE 3 | 115 | 3.4697 | 3.4714 | 0.0017
GEN-2019-011 | 05 SOUTWEST | 528095 | 7-RIVERS 6 | 230 | 6.7504 | 6.7594 | 0.009
GEN-2019-011 | 05 SOUTWEST | 528160 | CARLSBAD 3 | 115 | 11.906 | 11.9215 | 0.0155
GEN-2019-011 | 05 SOUTWEST | 528182 | NORTH_LOVNG3 | 115 | 12.8414 | 12.8639 | 0.0225
GEN-2019-011 | 05 SOUTWEST | 528185 | N_LOVING 7 | 345 | 6.9728 | 6.9944 | 0.0216
GEN-2019-011 | 05 SOUTWEST | 528192 | SOUTH_LOVNG3 | 115 | 9.7429 | 9.7559 | 0.013
GEN-2019-011 | 05 SOUTWEST | 528193 | BLACKRIVER 3 | 115 | 10.7892 | 10.8047 | 0.0155
GEN-2019-011 | 05 SOUTWEST | 528194 | MALAGABEND 3 | 115 | 8.228 | 8.2376 | 0.0096
GEN-2019-011 | 05 SOUTWEST | 528195 | AGAVE_PDURO3 | 115 | 8.366 | 8.3755 | 0.0095
GEN-2019-011 | 05 SOUTWEST | 528222 | CHINA_DRAW 3 | 115 | 11.5437 | 11.558 | 0.0143
GEN-2019-011 | 05 SOUTWEST | 528223 | CHINA_DRAW 7 | 345 | 6.2264 | 6.2432 | 0.0168
GEN-2019-011 | 05 SOUTWEST | 528226 | HOPI_SUB 3 | 115 | 7.631 | 7.6376 | 0.0066
GEN-2019-011 | 05 SOUTWEST | 528228 | WOOD_DRAW 3 | 115 | 8.5622 | 8.5719 | 0.0097
GEN-2019-011 | 05 SOUTWEST | 528230 | AGAVE_RHILL3 | 115 | 12.9782 | 13.0045 | 0.0263
GEN-2019-011 | 05 SOUTWEST | 528231 | AGAVE_RHIL23 | 115 | 12.28 | 12.3034 | 0.0234
GEN-2019-011 | 05 SOUTWEST | 528232 | OCHOA 3 | 115 | 12.2608 | 12.2843 | 0.0235
GEN-2019-011 | 05 SOUTWEST | 528235 | WOLFCAMP_TP3 | 115 | 12.6566 | 12.6796 | 0.023
GEN-2019-011 | 05 SOUTWEST | 528239 | CUSTERMTN 3 | 115 | 8.0789 | 8.0863 | 0.0074
GEN-2019-011 | 05 SOUTWEST | 528240 | PONDEROSA 3 | 115 | 4.275 | 4.2771 | 0.0021
GEN-2019-011 | 05 SOUTWEST | 528325 | LE-WAITS 3 | 115 | 9.4273 | 9.436 | 0.0087
GEN-2019-011 | 05 SOUTWEST | 528333 | LE-WEST_SUB3 | 115 | 9.373 | 9.3783 | 0.0053
GEN-2019-011 | 05 SOUTWEST | 528334 | LE-NRTH_INT3 | 115 | 9.318 | 9.3233 | 0.0053
GEN-2019-011 | 05 SOUTWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.6536 | 8.6574 | 0.0038
GEN-2019-011 | 05 SOUTWEST | 528353 | MADDOXG23 3 | 115 | 27.1482 | 27.1853 | 0.0371
GEN-2019-011 | 05 SOUTWEST | 528355 | MADDOX 3 | 115 | 27.1482 | 27.1853 | 0.0371
GEN-2019-011 | 05 SOUTWEST | 528392 | PEARLE 3 | 115 | 6.6661 | 6.6688 | 0.0027
GEN-2019-011 | 05 SOUTWEST | 528394 | QUAHADA 3 | 115 | 8.5916 | 8.5974 | 0.0058
GEN-2019-011 | 05 SOUTWEST | 528433 | BENSING 3 | 115 | 8.399 | 8.4036 | 0.0046
GEN-2019-011 | 05 SOUTWEST | 528434 | MILLEN_TPW 3 | 115 | 12.1794 | 12.188 | 0.0086
GEN-2019-011 | 05 SOUTWEST | 528435 | MILLEN 3 | 115 | 12.1794 | 12.188 | 0.0086
GEN-2019-011 | 05 SOUTWEST | 528436 | MILLEN_TPE 3 | 115 | 12.1794 | 12.188 | 0.0086
GEN-2019-011 | 05 SOUTWEST | 528491 | MONUMENT 3 | 115 | 16.0729 | 16.0865 | 0.0136
GEN-2019-011 | 05 SOUTWEST | 528540 | WHITTEN 3 | 115 | 8.0324 | 8.0389 | 0.0065
GEN-2019-011 | 05 SOUTWEST | 528568 | MONUMNT_TP 3 | 115 | 10.7606 | 10.7673 | 0.0067
GEN-2019-011 | 05 SOUTWEST | 528602 | ANDREWS 3 | 115 | 9.8767 | 9.8853 | 0.0086
GEN-2019-011 | 05 SOUTWEST | 528603 | NA_ENRICH 3 | 115 | 9.8011 | 9.8096 | 0.0085
GEN-2019-011 | 05 SOUTWEST | 528604 | ANDREWS 6 | 230 | 6.3476 | 6.3547 | 0.0071
GEN-2019-011 | 05 SOUTWEST | 528617 | LE-WAITS 2 | 69 | 3.4229 | 3.4236 | 0.0007
GEN-2019-011 | 05 SOUTWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6609 | 3.6622 | 0.0013
GEN-2019-011 | 05 SOUTWEST | 528709 | LE-PLNSGOAB2 | 69 | 2.9032 | 2.904 | 0.0008
GEN-2019-011 | 05 SOUTWEST | 560071 | G16-003-TAP | 345 | 14.3008 | 14.301 | 0.0002
GEN-2019-011 | 05 SOUTWEST | 560078 | G16-037-TAP | 345 | 8.7443 | 8.7447 | 0.0004
GEN-2019-011 | 05 SOUTWEST | 587990 | GEN-2016-121 | 115 | 13.3542 | 13.3822 | 0.028
GEN-2019-011 | 05 SOUTWEST | 588460 | A16-008SUB | 115 | 13.6833 | 13.7053 | 0.022
GEN-2019-011 | 05 SOUTWEST | 588760 | GEN-2017-033 | 345 | 4.2676 | 4.2681 | 0.0005
GEN-2019-011 | 05 SOUTWEST | 599955 | PNM-DC6 | 230 | 9.9369 | 9.9404 | 0.0035
GEN-2019-011 | 05 SOUTWEST | 599960 | EPTNP-D6 | 230 | 9.8857 | 9.9052 | 0.0195
GEN-2019-011 | 05 SOUTWEST | 755000 | WWDBORDT | 345 | 10.2581 | 10.259 | 0.0009
GEN-2019-011 | 05 SOUTWEST | 760498 | G17-146-TAP | 230 | 8.0773 | 8.0786 | 0.0013
GEN-2019-011 | 05 SOUTWEST | 761355 | GEN-2017-239 | 230 | 14.5002 | 14.5824 | 0.0822
GEN-2019-011 | 05 SOUTWEST | 762132 | GEN-2017-158 | 230 | 14.0976 | 14.1047 | 0.0071
GEN-2019-011 | 05 SOUTWEST | 762216 | G17-151TAP | 345 | 8.5217 | 8.5355 | 0.0138
GEN-2019-011 | 05 SOUTWEST | 762217 | GEN-2017-151 | 345 | 6.2683 | 6.2754 | 0.0071
GEN-2019-011 | 05 SOUTWEST | 762442 | G18-004-TAP | 115 | 23.4421 | 23.4702 | 0.0281
GEN-2019-011 | 05 SOUTWEST | 762460 | GEN-2018-015 | 345 | 5.3095 | 5.3116 | 0.0021
GEN-2019-011 | 05 SOUTWEST | 762467 | G18-015-TAP | 345 | 5.319 | 5.3211 | 0.0021
GEN-2019-011 | 05 SOUTWEST | 762866 | GEN-2018-052 | 115 | 14.2529 | 14.2847 | 0.0318
GEN-2019-011 | 05 SOUTWEST | 763186 | GEN-2018-089 | 230 | 11.13 | 11.1335 | 0.0035
GEN-2019-011 | 05 SOUTWEST | 763483 | GEN-2019-003 | 230 | 8.9651 | 8.9679 | 0.0028
GEN-2019-011 | 05 SOUTWEST | 763516 | GEN-2019-011 | 345 | 9.441 | 9.8699 | 0.4289
GEN-2019-011 | 05 SOUTWEST | 763527 | GEN-2019-012 | 345 | 16.8284 | 16.8287 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 511456 | O.K.U.-7 | 345 | 5.8457 | 5.8457 | 0
GEN-2019-021 | 05 SOUTWEST | 511468 | L.E.S.-7 | 345 | 12.9352 | 12.9352 | 0
GEN-2019-021 | 05 SOUTWEST | 511553 | CHISHOLM7 | 345 | 10.2668 | 10.2669 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 511557 | CHISHOLM6 | 230 | 11.2597 | 11.2597 | 0
GEN-2019-021 | 05 SOUTWEST | 511565 | OKLAUN HVDC7 | 345 | 5.828 | 5.828 | 0
GEN-2019-021 | 05 SOUTWEST | 515375 | WWRDEHV7 | 345 | 19.0119 | 19.012 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 515376 | WWRDEHV4 | 138 | 25.384 | 25.384 | 0
GEN-2019-021 | 05 SOUTWEST | 515407 | TATONGA7 | 345 | 16.4723 | 16.4723 | 0
GEN-2019-021 | 05 SOUTWEST | 515458 | BORDER 7 | 345 | 7.4346 | 7.4346 | 0
GEN-2019-021 | 05 SOUTWEST | 515554 | BVRCNTY7 | 345 | 12.8494 | 12.8495 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 515852 | DGRASSE7 | 345 | 13.9914 | 13.9914 | 0
GEN-2019-021 | 05 SOUTWEST | 515961 | GUTHRIE7 | 345 | 11.8592 | 11.8592 | 0
GEN-2019-021 | 05 SOUTWEST | 523095 | HITCHLAND 6 | 230 | 14.0634 | 14.0634 | 0
GEN-2019-021 | 05 SOUTWEST | 523097 | HITCHLAND 7 | 345 | 13.5624 | 13.5626 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 523101 | NOBLE_WND 7 | 345 | 13.5151 | 13.5153 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 523112 | NOVUS1 7 | 345 | 13.3311 | 13.3313 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 523323 | MCDWL_CREEK6 | 230 | 9.4105 | 9.4109 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 523823 | CARPENTER 7 | 345 | 6.5517 | 6.5517 | 0
GEN-2019-021 | 05 SOUTWEST | 523853 | FINNEY 7 | 345 | 8.9671 | 8.9671 | 0
GEN-2019-021 | 05 SOUTWEST | 523869 | CHAN+TASCOS6 | 230 | 4.456 | 4.4561 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 523959 | POTTER_CO 6 | 230 | 23.0509 | 23.0545 | 0.0036
GEN-2019-021 | 05 SOUTWEST | 523961 | POTTER_CO 7 | 345 | 11.0564 | 11.0581 | 0.0017
GEN-2019-021 | 05 SOUTWEST | 523979 | HARRNG_EST 6 | 230 | 28.1523 | 28.1552 | 0.0029
GEN-2019-021 | 05 SOUTWEST | 524010 | ROLLHILLS 6 | 230 | 21.0248 | 21.0269 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 524044 | NICHOLS 6 | 230 | 27.2467 | 27.2494 | 0.0027
GEN-2019-021 | 05 SOUTWEST | 524267 | BUSHLAND 6 | 230 | 10.4082 | 10.4097 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3339 | 5.3342 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3339 | 5.3342 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 524365 | RANDALL 6 | 230 | 15.1419 | 15.143 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 524414 | AMA_SOUTH 3 | 115 | 17.386 | 17.3868 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2407 | 14.2417 | 0.001
GEN-2019-021 | 05 SOUTWEST | 524472 | LOPEZ 3 | 115 | 2.4049 | 2.4055 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 524486 | CAPROCK 3 | 115 | 2.7735 | 2.7743 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 524502 | NORTON 3 | 115 | 3.073 | 3.0743 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5416 | 2.5423 | 0.0007
GEN-2019-021 | 05 SOUTWEST | 524619 | DFSMTH_EST 3 | 115 | 11.7368 | 11.741 | 0.0042
GEN-2019-021 | 05 SOUTWEST | 524622 | DFSMTH_WST 3 | 115 | 11.7397 | 11.7439 | 0.0042
GEN-2019-021 | 05 SOUTWEST | 524623 | DEAFSMITH 6 | 230 | 8.4186 | 8.4216 | 0.003
GEN-2019-021 | 05 SOUTWEST | 524662 | PARMER_CO 3 | 115 | 4.5847 | 4.5909 | 0.0062
GEN-2019-021 | 05 SOUTWEST | 524664 | DS-#24 +3 | 115 | 4.5213 | 4.5271 | 0.0058
GEN-2019-021 | 05 SOUTWEST | 524669 | DS-#20 3 | 115 | 5.5013 | 5.513 | 0.0117
GEN-2019-021 | 05 SOUTWEST | 524746 | CASTRO_CNTY3 | 115 | 10.1588 | 10.1608 | 0.002
GEN-2019-021 | 05 SOUTWEST | 524764 | NORRIS_TP 3 | 115 | 11.292 | 11.3615 | 0.0695
GEN-2019-021 | 05 SOUTWEST | 524768 | PLSNT_HILL 3 | 115 | 10.8592 | 10.9246 | 0.0654
GEN-2019-021 | 05 SOUTWEST | 524770 | PLSNT_HILL 6 | 230 | 6.578 | 6.6398 | 0.0618
GEN-2019-021 | 05 SOUTWEST | 524773 | E_CLOVIS 3 | 115 | 9.1347 | 9.1806 | 0.0459
GEN-2019-021 | 05 SOUTWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.7621 | 7.7953 | 0.0332
GEN-2019-021 | 05 SOUTWEST | 524777 | N_CLOVIS 3 | 115 | 6.9994 | 7.0266 | 0.0272
GEN-2019-021 | 05 SOUTWEST | 524783 | W_CLOVIS 2 | 69 | 2.5503 | 2.5524 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 524784 | W_CLOVIS 3 | 115 | 6.5737 | 6.5979 | 0.0242
GEN-2019-021 | 05 SOUTWEST | 524790 | CANNON_TP 3 | 115 | 6.2156 | 6.2379 | 0.0223
GEN-2019-021 | 05 SOUTWEST | 524794 | CANNONAFB 3 | 115 | 5.8398 | 5.8594 | 0.0196
GEN-2019-021 | 05 SOUTWEST | 524797 | PERIMETER 3 | 115 | 6.6806 | 6.7079 | 0.0273
GEN-2019-021 | 05 SOUTWEST | 524801 | NORRIS 3 | 115 | 10.342 | 10.4005 | 0.0585
GEN-2019-021 | 05 SOUTWEST | 524808 | FE-CLVS_INT3 | 115 | 7.2256 | 7.2542 | 0.0286
GEN-2019-021 | 05 SOUTWEST | 524821 | CURRY 2 | 69 | 4.5151 | 4.5215 | 0.0064
GEN-2019-021 | 05 SOUTWEST | 524822 | CURRY 3 | 115 | 11.3225 | 11.3923 | 0.0698
GEN-2019-021 | 05 SOUTWEST | 524831 | FE-HOLLAND 3 | 115 | 9.4427 | 9.4918 | 0.0491
GEN-2019-021 | 05 SOUTWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7489 | 10.8119 | 0.063
GEN-2019-021 | 05 SOUTWEST | 524846 | FARWELL 2 | 69 | 2.212 | 2.2136 | 0.0016
GEN-2019-021 | 05 SOUTWEST | 524853 | DS-#10 +2 | 69 | 1.7991 | 1.7994 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0658 | 8.1043 | 0.0385
GEN-2019-021 | 05 SOUTWEST | 524874 | OASIS 3 | 115 | 9.9211 | 9.9847 | 0.0636
GEN-2019-021 | 05 SOUTWEST | 524875 | OASIS 6 | 230 | 7.9975 | 8.0854 | 0.0879
GEN-2019-021 | 05 SOUTWEST | 524885 | SN_JUAN_TAP6 | 230 | 5.0044 | 5.0165 | 0.0121
GEN-2019-021 | 05 SOUTWEST | 524889 | SN_JUAN_WND6 | 230 | 4.7905 | 4.8012 | 0.0107
GEN-2019-021 | 05 SOUTWEST | 524908 | ROOSEVELT 3 | 115 | 10.9401 | 11.0207 | 0.0806
GEN-2019-021 | 05 SOUTWEST | 524909 | ROOSEVELT 6 | 230 | 9.7827 | 9.9404 | 0.1577
GEN-2019-021 | 05 SOUTWEST | 524923 | PORTALES 2 | 69 | 7.7182 | 7.7409 | 0.0227
GEN-2019-021 | 05 SOUTWEST | 524924 | PORTALES 3 | 115 | 7.6503 | 7.6884 | 0.0381
GEN-2019-021 | 05 SOUTWEST | 524929 | RO-PORT_MTR2 | 69 | 7.7182 | 7.7409 | 0.0227
GEN-2019-021 | 05 SOUTWEST | 524934 | ZODIAC 2 | 69 | 5.6707 | 5.6832 | 0.0125
GEN-2019-021 | 05 SOUTWEST | 524935 | KILGORE 3 | 115 | 6.2774 | 6.3029 | 0.0255
GEN-2019-021 | 05 SOUTWEST | 524941 | PORTALES#1 2 | 69 | 5.9211 | 5.9346 | 0.0135
GEN-2019-021 | 05 SOUTWEST | 524948 | PORTALES#2 2 | 69 | 5.0227 | 5.0326 | 0.0099
GEN-2019-021 | 05 SOUTWEST | 524962 | S_PORTALES 2 | 69 | 4.4268 | 4.4346 | 0.0078
GEN-2019-021 | 05 SOUTWEST | 524963 | S_PORTALES 3 | 115 | 5.9043 | 5.9269 | 0.0226
GEN-2019-021 | 05 SOUTWEST | 524977 | GREYHOUND 3 | 115 | 5.8213 | 5.8433 | 0.022
GEN-2019-021 | 05 SOUTWEST | 525008 | MULESH_CTY 2 | 69 | 4.0395 | 4.0409 | 0.0014
GEN-2019-021 | 05 SOUTWEST | 525017 | EMULESH&VLY2 | 69 | 4.016 | 4.0174 | 0.0014
GEN-2019-021 | 05 SOUTWEST | 525018 | MULESHVALLY3 | 115 | 5.1375 | 5.1411 | 0.0036
GEN-2019-021 | 05 SOUTWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4671 | 5.4712 | 0.0041
GEN-2019-021 | 05 SOUTWEST | 525023 | BC-BAIL_MTR2 | 69 | 4.8774 | 4.8795 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 525027 | BAILEYCO 2 | 69 | 4.8774 | 4.8795 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 525028 | BAILEYCO 3 | 115 | 5.3627 | 5.3669 | 0.0042
GEN-2019-021 | 05 SOUTWEST | 525050 | BC-KELLEY +3 | 115 | 7.8677 | 7.8695 | 0.0018
GEN-2019-021 | 05 SOUTWEST | 525056 | BC-EARTH 3 | 115 | 8.2083 | 8.2104 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 525124 | HART_INDUST3 | 115 | 7.7563 | 7.7574 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 525192 | KRESS_INT 3 | 115 | 12.3339 | 12.3354 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 525212 | SWISHER 3 | 115 | 11.7808 | 11.7821 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 525213 | SWISHER 6 | 230 | 10.8421 | 10.8441 | 0.002
GEN-2019-021 | 05 SOUTWEST | 525326 | COX 3 | 115 | 6.6313 | 6.6317 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 525393 | ROCKYFORD 3 | 115 | 8.5457 | 8.5483 | 0.0026
GEN-2019-021 | 05 SOUTWEST | 525414 | LAMTON 3 | 115 | 7.844 | 7.8453 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 525440 | LC-S_OLTON+3 | 115 | 7.2633 | 7.2647 | 0.0014
GEN-2019-021 | 05 SOUTWEST | 525446 | RKYFORD_TP 3 | 115 | 9.4567 | 9.4599 | 0.0032
GEN-2019-021 | 05 SOUTWEST | 525453 | HALE_CNTY 2 | 69 | 6.7615 | 6.7619 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 525454 | HALE_CNTY 3 | 115 | 10.5584 | 10.5599 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 525460 | NEWHART 3 | 115 | 15.1875 | 15.1909 | 0.0034
GEN-2019-021 | 05 SOUTWEST | 525461 | NEWHART 6 | 230 | 11.4493 | 11.4527 | 0.0034
GEN-2019-021 | 05 SOUTWEST | 525480 | PLANT_X 3 | 115 | 15.4972 | 15.507 | 0.0098
GEN-2019-021 | 05 SOUTWEST | 525481 | PLANT_X 6 | 230 | 23.8106 | 23.8515 | 0.0409
GEN-2019-021 | 05 SOUTWEST | 525531 | TOLK 6 | 230 | 30.6349 | 30.7299 | 0.095
GEN-2019-021 | 05 SOUTWEST | 525549 | TOLK 7 | 345 | 13.4497 | 13.4662 | 0.0165
GEN-2019-021 | 05 SOUTWEST | 525584 | BLUECLDCOL 6 | 230 | 10.7096 | 10.7184 | 0.0088
GEN-2019-021 | 05 SOUTWEST | 525585 | BLUECLDPOI 6 | 230 | 11.3042 | 11.3141 | 0.0099
GEN-2019-021 | 05 SOUTWEST | 525586 | NEEDMORE 6 | 230 | 11.3042 | 11.3141 | 0.0099
GEN-2019-021 | 05 SOUTWEST | 525613 | W_LITTLFLD 2 | 69 | 3.171 | 3.1712 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3274 | 4.3279 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 525635 | LAMB_CNTY 2 | 69 | 6.123 | 6.1238 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4446 | 8.4473 | 0.0027
GEN-2019-021 | 05 SOUTWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9142 | 5.917 | 0.0028
GEN-2019-021 | 05 SOUTWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1537 | 5.1543 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.8004 | 4.8009 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1723 | 3.1724 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 525738 | HALECENTER 2 | 69 | 2.6087 | 2.6087 | 0
GEN-2019-021 | 05 SOUTWEST | 525763 | CALLAHAN 3 | 115 | 5.8399 | 5.8402 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4073 | 5.4075 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.5119 | 6.5121 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 525803 | BLANCO 3 | 115 | 5.2384 | 5.2385 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 525816 | TUCO_INT2 2 | 69 | 4.7714 | 4.7714 | 0
GEN-2019-021 | 05 SOUTWEST | 525826 | TUCO_INT 2 | 69 | 8.204 | 8.2042 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 525828 | TUCO_INT 3 | 115 | 19.8039 | 19.806 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 525830 | TUCO_INT 6 | 230 | 21.9043 | 21.909 | 0.0047
GEN-2019-021 | 05 SOUTWEST | 525832 | TUCO_INT 7 | 345 | 13.9918 | 13.9936 | 0.0018
GEN-2019-021 | 05 SOUTWEST | 525840 | ANTELOPE_1 6 | 230 | 21.7279 | 21.7325 | 0.0046
GEN-2019-021 | 05 SOUTWEST | 525850 | ELK_CT1 | 345 | 13.8919 | 13.8937 | 0.0018
GEN-2019-021 | 05 SOUTWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.75 | 2.75 | 0
GEN-2019-021 | 05 SOUTWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5203 | 3.5204 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 525926 | CROSBY 3 | 115 | 4.9208 | 4.9209 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 525957 | HALE_WNDCL16 | 230 | 10.7 | 10.701 | 0.001
GEN-2019-021 | 05 SOUTWEST | 526019 | HOCKLEY 2 | 69 | 5.3928 | 5.3931 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 526020 | HOCKLEY 3 | 115 | 5.6556 | 5.6562 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 526036 | LC-OPDYKE 3 | 115 | 5.9376 | 5.9382 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 526076 | STANTON_W 3 | 115 | 9.1752 | 9.1756 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 526109 | SP-ERSKINE 3 | 115 | 11.1284 | 11.129 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 526146 | INDIANA 3 | 115 | 9.5478 | 9.5483 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 526159 | CARLISLE 2 | 69 | 2.7515 | 2.7515 | 0
GEN-2019-021 | 05 SOUTWEST | 526160 | CARLISLE 3 | 115 | 12.802 | 12.8027 | 0.0007
GEN-2019-021 | 05 SOUTWEST | 526161 | CARLISLE 6 | 230 | 10.6948 | 10.6959 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.4725 | 11.473 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 526192 | MURPHY 3 | 115 | 10.5588 | 10.5593 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 526268 | LUBBCK_STH 3 | 115 | 18.1237 | 18.1246 | 0.0009
GEN-2019-021 | 05 SOUTWEST | 526269 | LUBBCK_STH 6 | 230 | 15.4534 | 15.4547 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 526297 | LUBBCK_EST 2 | 69 | 8.737 | 8.7371 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 526298 | LUBBCK_EST 3 | 115 | 14.8878 | 14.8886 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 526299 | LUBBCK_EST 6 | 230 | 11.473 | 11.4736 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 526337 | JONES 6 | 230 | 17.0994 | 17.1008 | 0.0014
GEN-2019-021 | 05 SOUTWEST | 526350 | LEHMAN_TP 3 | 115 | 5.5867 | 5.5869 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 526424 | PACIFIC 3 | 115 | 9.2345 | 9.2352 | 0.0007
GEN-2019-021 | 05 SOUTWEST | 526434 | SUNDOWN 3 | 115 | 10.7992 | 10.8003 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 526435 | SUNDOWN 6 | 230 | 11.5526 | 11.555 | 0.0024
GEN-2019-021 | 05 SOUTWEST | 526445 | AMOCO_TP 3 | 115 | 10.1943 | 10.1952 | 0.0009
GEN-2019-021 | 05 SOUTWEST | 526460 | AMOCO_SS 6 | 230 | 10.2692 | 10.2709 | 0.0017
GEN-2019-021 | 05 SOUTWEST | 526491 | LG-CLAUENE 3 | 115 | 8.163 | 8.1635 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 526524 | WOLFFORTH 3 | 115 | 11.3363 | 11.3369 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 526525 | WOLFFORTH 6 | 230 | 13.023 | 13.0245 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 526676 | GRASSLAND 3 | 115 | 7.2505 | 7.2506 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 526677 | GRASSLAND 6 | 230 | 6.2454 | 6.2456 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 526679 | CIRRUS_WND 6 | 230 | 4.8948 | 4.8949 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 526735 | TERRY_CNTY 2 | 69 | 7.1361 | 7.1362 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1248 | 11.1253 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 526784 | AMOCOWASSON6 | 230 | 16.5569 | 16.5582 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 526792 | PRENTICE 3 | 115 | 6.3127 | 6.3129 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 526928 | PLAINS_INT 3 | 115 | 10.2943 | 10.2947 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 526934 | YOAKUM 3 | 115 | 19.2978 | 19.2991 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 526935 | YOAKUM 6 | 230 | 20.8155 | 20.8189 | 0.0034
GEN-2019-021 | 05 SOUTWEST | 526936 | YOAKUM_345 | 345 | 10.5033 | 10.5046 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 526944 | LG-PLAINS 3 | 115 | 8.1538 | 8.1541 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527009 | BRU_SUB 6 | 230 | 16.5454 | 16.5471 | 0.0017
GEN-2019-021 | 05 SOUTWEST | 527010 | OXYBRU 6 | 230 | 16.3899 | 16.3916 | 0.0017
GEN-2019-021 | 05 SOUTWEST | 527011 | XTO_MAHONEY6 | 230 | 16.2409 | 16.2424 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 527018 | BENNETT 3 | 115 | 14.4086 | 14.4091 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 527024 | ALLRED_SUB 3 | 115 | 11.2855 | 11.2858 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527027 | INK_BASIN 3 | 115 | 13.7049 | 13.7053 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 527028 | INK_BASIN 6 | 230 | 11.7937 | 11.7946 | 0.0009
GEN-2019-021 | 05 SOUTWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.8527 | 12.853 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527033 | XTO_CORNEL+3 | 115 | 13.0056 | 13.006 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 527036 | SHELL_C2 3 | 115 | 15.4895 | 15.49 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 527041 | ARCO_TP 3 | 115 | 14.3065 | 14.3071 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 527047 | OXY_WILRD1 3 | 115 | 11.4329 | 11.4332 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527051 | ODC_TP 3 | 115 | 14.4259 | 14.4264 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 527062 | SHELL_CO2 3 | 115 | 17.4531 | 17.4538 | 0.0007
GEN-2019-021 | 05 SOUTWEST | 527080 | EL_PASO 3 | 115 | 17.1809 | 17.1816 | 0.0007
GEN-2019-021 | 05 SOUTWEST | 527105 | SAN_ANDS_TP3 | 115 | 18.0272 | 18.0278 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 527125 | DENVER_CTY 2 | 69 | 8.8545 | 8.8546 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 527130 | DENVER_N 3 | 115 | 23.3406 | 23.3418 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 527136 | DENVER_S 3 | 115 | 23.3406 | 23.3418 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 527146 | MUSTANG 3 | 115 | 24.9089 | 24.9101 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 527149 | MUSTANG 6 | 230 | 19.0053 | 19.0068 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 527151 | GS-MUSTANG 6 | 230 | 19.0053 | 19.0068 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3305 | 8.3307 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527201 | SEAGRAVES 2 | 69 | 5.6176 | 5.6177 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 527202 | SEAGRAVES 3 | 115 | 9.6122 | 9.6124 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527238 | ROZ 3 | 115 | 11.5278 | 11.5281 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527242 | AMERADA 3 | 115 | 11.6874 | 11.6877 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527257 | FLATLAND 3 | 115 | 7.0495 | 7.0496 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 527275 | SEMINOLE 3 | 115 | 14.7983 | 14.7988 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 527276 | SEMINOLE 6 | 230 | 8.8913 | 8.8916 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 527286 | HIGGEAST 3 | 115 | 10.7044 | 10.7046 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527322 | GAINES 3 | 115 | 9.8343 | 9.8345 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527340 | DOSS 3 | 115 | 8.3332 | 8.3334 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527363 | HIGG 3 | 115 | 10.8944 | 10.8946 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 527455 | RSWL_SLRCOL3 | 115 | 7.4112 | 7.4148 | 0.0036
GEN-2019-021 | 05 SOUTWEST | 527470 | CHVS_SLRCOL3 | 115 | 7.2357 | 7.2391 | 0.0034
GEN-2019-021 | 05 SOUTWEST | 527482 | CHAVES_CNTY3 | 115 | 7.486 | 7.4897 | 0.0037
GEN-2019-021 | 05 SOUTWEST | 527483 | CHAVES_CNTY6 | 230 | 4.5739 | 4.5773 | 0.0034
GEN-2019-021 | 05 SOUTWEST | 527501 | URTON 3 | 115 | 6.2498 | 6.2523 | 0.0025
GEN-2019-021 | 05 SOUTWEST | 527509 | PRICE_TAP 3 | 115 | 5.7959 | 5.798 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 527546 | SAMSON 3 | 115 | 5.8717 | 5.8738 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.3616 | 10.3648 | 0.0032
GEN-2019-021 | 05 SOUTWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.3616 | 10.3648 | 0.0032
GEN-2019-021 | 05 SOUTWEST | 527610 | SAGA_SCOL 7 | 345 | 10.3616 | 10.3648 | 0.0032
GEN-2019-021 | 05 SOUTWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.8182 | 8.8205 | 0.0023
GEN-2019-021 | 05 SOUTWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.1084 | 10.1115 | 0.0031
GEN-2019-021 | 05 SOUTWEST | 527656 | CROSSROADS 7 | 345 | 11.6222 | 11.6265 | 0.0043
GEN-2019-021 | 05 SOUTWEST | 527666 | RSVLT_COL1 7 | 345 | 8.8182 | 8.8205 | 0.0023
GEN-2019-021 | 05 SOUTWEST | 527667 | RSVLT_COL2 7 | 345 | 8.8182 | 8.8205 | 0.0023
GEN-2019-021 | 05 SOUTWEST | 527793 | EDDY_STH 3 | 115 | 12.3607 | 12.363 | 0.0023
GEN-2019-021 | 05 SOUTWEST | 527798 | EDDY_NTH 3 | 115 | 12.3607 | 12.363 | 0.0023
GEN-2019-021 | 05 SOUTWEST | 527799 | EDDY_NORTH 6 | 230 | 9.9024 | 9.9052 | 0.0028
GEN-2019-021 | 05 SOUTWEST | 527802 | EDDY_CNTY 7 | 345 | 7.5951 | 7.5969 | 0.0018
GEN-2019-021 | 05 SOUTWEST | 527864 | CUNNINHAM 3 | 115 | 28.4714 | 28.4729 | 0.0015
GEN-2019-021 | 05 SOUTWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.2963 | 18.2985 | 0.0022
GEN-2019-021 | 05 SOUTWEST | 527867 | CUNNIGHM_S 6 | 230 | 18.2963 | 18.2985 | 0.0022
GEN-2019-021 | 05 SOUTWEST | 527891 | HOBBS_INT 3 | 115 | 32.3287 | 32.3305 | 0.0018
GEN-2019-021 | 05 SOUTWEST | 527894 | HOBBS_INT 6 | 230 | 20.3373 | 20.34 | 0.0027
GEN-2019-021 | 05 SOUTWEST | 527896 | HOBBS_INT 7 | 345 | 12.3075 | 12.3104 | 0.0029
GEN-2019-021 | 05 SOUTWEST | 527930 | PCA 3 | 115 | 12.628 | 12.629 | 0.001
GEN-2019-021 | 05 SOUTWEST | 527961 | POTASH_JCT 2 | 69 | 9.9043 | 9.9047 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 527962 | POTASH_JCT 3 | 115 | 17.9732 | 17.9754 | 0.0022
GEN-2019-021 | 05 SOUTWEST | 527963 | POTASH_JCT 6 | 230 | 8.0009 | 8.0017 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 527965 | KIOWA 7 | 345 | 9.1994 | 9.2013 | 0.0019
GEN-2019-021 | 05 SOUTWEST | 527966 | KIOWA 3 | 115 | 17.983 | 17.9851 | 0.0021
GEN-2019-021 | 05 SOUTWEST | 527999 | INTREPDW_TP3 | 115 | 14.6407 | 14.6421 | 0.0014
GEN-2019-021 | 05 SOUTWEST | 528013 | PHANTOM 3 | 115 | 13.5635 | 13.5646 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 528015 | PHANTOM 7 | 345 | 6.1672 | 6.168 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528016 | SAND_DUNES 3 | 115 | 7.8238 | 7.8242 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 528018 | RED_BLUFF 3 | 115 | 10.7115 | 10.7121 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 528020 | BOPCO_PKRLK3 | 115 | 13.3665 | 13.3676 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 528024 | RR_SVC_HV 3 | 115 | 14.5259 | 14.5271 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 528025 | RDRUNNER 3 | 115 | 14.5259 | 14.5271 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 528027 | RDRUNNER 7 | 345 | 9.1961 | 9.1978 | 0.0017
GEN-2019-021 | 05 SOUTWEST | 528040 | BATTLE_AXE 3 | 115 | 3.4714 | 3.4714 | 0
GEN-2019-021 | 05 SOUTWEST | 528095 | 7-RIVERS 6 | 230 | 6.7584 | 6.7594 | 0.001
GEN-2019-021 | 05 SOUTWEST | 528160 | CARLSBAD 3 | 115 | 11.9203 | 11.9215 | 0.0012
GEN-2019-021 | 05 SOUTWEST | 528182 | NORTH_LOVNG3 | 115 | 12.8628 | 12.8639 | 0.0011
GEN-2019-021 | 05 SOUTWEST | 528185 | N_LOVING 7 | 345 | 6.9934 | 6.9944 | 0.001
GEN-2019-021 | 05 SOUTWEST | 528192 | SOUTH_LOVNG3 | 115 | 9.7553 | 9.7559 | 0.0006
GEN-2019-021 | 05 SOUTWEST | 528193 | BLACKRIVER 3 | 115 | 10.8039 | 10.8047 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528194 | MALAGABEND 3 | 115 | 8.2372 | 8.2376 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 528195 | AGAVE_PDURO3 | 115 | 8.375 | 8.3755 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 528222 | CHINA_DRAW 3 | 115 | 11.5572 | 11.558 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528223 | CHINA_DRAW 7 | 345 | 6.2424 | 6.2432 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528226 | HOPI_SUB 3 | 115 | 7.6372 | 7.6376 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 528228 | WOOD_DRAW 3 | 115 | 8.5715 | 8.5719 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 528230 | AGAVE_RHILL3 | 115 | 13.0036 | 13.0045 | 0.0009
GEN-2019-021 | 05 SOUTWEST | 528231 | AGAVE_RHIL23 | 115 | 12.3026 | 12.3034 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528232 | OCHOA 3 | 115 | 12.2835 | 12.2843 | 0.0008
GEN-2019-021 | 05 SOUTWEST | 528235 | WOLFCAMP_TP3 | 115 | 12.6787 | 12.6796 | 0.0009
GEN-2019-021 | 05 SOUTWEST | 528239 | CUSTERMTN 3 | 115 | 8.0861 | 8.0863 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528240 | PONDEROSA 3 | 115 | 4.277 | 4.2771 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528325 | LE-WAITS 3 | 115 | 9.4358 | 9.436 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528333 | LE-WEST_SUB3 | 115 | 9.3782 | 9.3783 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528334 | LE-NRTH_INT3 | 115 | 9.3232 | 9.3233 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.6573 | 8.6574 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528353 | MADDOXG23 3 | 115 | 27.184 | 27.1853 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 528355 | MADDOX 3 | 115 | 27.184 | 27.1853 | 0.0013
GEN-2019-021 | 05 SOUTWEST | 528392 | PEARLE 3 | 115 | 6.6687 | 6.6688 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528394 | QUAHADA 3 | 115 | 8.5972 | 8.5974 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528433 | BENSING 3 | 115 | 8.4035 | 8.4036 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 528434 | MILLEN_TPW 3 | 115 | 12.1877 | 12.188 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 528435 | MILLEN 3 | 115 | 12.1877 | 12.188 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 528436 | MILLEN_TPE 3 | 115 | 12.1877 | 12.188 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 528491 | MONUMENT 3 | 115 | 16.0861 | 16.0865 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 528540 | WHITTEN 3 | 115 | 8.0387 | 8.0389 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528568 | MONUMNT_TP 3 | 115 | 10.7671 | 10.7673 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528602 | ANDREWS 3 | 115 | 9.885 | 9.8853 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 528603 | NA_ENRICH 3 | 115 | 9.8093 | 9.8096 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 528604 | ANDREWS 6 | 230 | 6.3545 | 6.3547 | 0.0002
GEN-2019-021 | 05 SOUTWEST | 528617 | LE-WAITS 2 | 69 | 3.4236 | 3.4236 | 0
GEN-2019-021 | 05 SOUTWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6622 | 3.6622 | 0
GEN-2019-021 | 05 SOUTWEST | 528709 | LE-PLNSGOAB2 | 69 | 2.904 | 2.904 | 0
GEN-2019-021 | 05 SOUTWEST | 560071 | G16-003-TAP | 345 | 14.3009 | 14.301 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 560078 | G16-037-TAP | 345 | 8.7447 | 8.7447 | 0
GEN-2019-021 | 05 SOUTWEST | 560756 | CEILO-TAP-N | 115 | 0.478 | 0.478 | 0
GEN-2019-021 | 05 SOUTWEST | 576397 | G10014G11022 | 345 | 9.829 | 9.8291 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 583280 | A12-02&13-05 | 115 | 1.077 | 1.0773 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 587990 | GEN-2016-121 | 115 | 13.3812 | 13.3822 | 0.001
GEN-2019-021 | 05 SOUTWEST | 588460 | A16-008SUB | 115 | 13.7049 | 13.7053 | 0.0004
GEN-2019-021 | 05 SOUTWEST | 588760 | GEN-2017-033 | 345 | 4.268 | 4.2681 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 599950 | LAMAR7 | 345 | 2.3488 | 2.3488 | 0
GEN-2019-021 | 05 SOUTWEST | 599951 | LAMAR 6 | 345 | 13.4752 | 13.4752 | 0
GEN-2019-021 | 05 SOUTWEST | 599955 | PNM-DC6 | 230 | 9.7827 | 9.9404 | 0.1577
GEN-2019-021 | 05 SOUTWEST | 599956 | PNM-DC7 | 345 | 15.1757 | 15.1757 | 0
GEN-2019-021 | 05 SOUTWEST | 599960 | EPTNP-D6 | 230 | 9.9024 | 9.9052 | 0.0028
GEN-2019-021 | 05 SOUTWEST | 599961 | EPTNP 7 | 345 | 13.486 | 13.486 | 0
GEN-2019-021 | 05 SOUTWEST | 755000 | WWDBORDT | 345 | 10.2589 | 10.259 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 760494 | GEN-2017-146 | 230 | 7.7748 | 7.7777 | 0.0029
GEN-2019-021 | 05 SOUTWEST | 760498 | G17-146-TAP | 230 | 8.0755 | 8.0786 | 0.0031
GEN-2019-021 | 05 SOUTWEST | 762132 | GEN-2017-158 | 230 | 14.0871 | 14.1047 | 0.0176
GEN-2019-021 | 05 SOUTWEST | 762216 | G17-151TAP | 345 | 8.535 | 8.5355 | 0.0005
GEN-2019-021 | 05 SOUTWEST | 762217 | GEN-2017-151 | 345 | 6.2751 | 6.2754 | 0.0003
GEN-2019-021 | 05 SOUTWEST | 762467 | G18-015-TAP | 345 | 5.321 | 5.3211 | 0.0001
GEN-2019-021 | 05 SOUTWEST | 763186 | GEN-2018-089 | 230 | 11.1303 | 11.1335 | 0.0032
GEN-2019-021 | 05 SOUTWEST | 763483 | GEN-2019-003 | 230 | 8.8084 | 8.9679 | 0.1595
GEN-2019-021 | 05 SOUTWEST | 763516 | GEN-2019-011 | 345 | 9.8687 | 9.8699 | 0.0012

## SCRCCT
Group | Season | Case Type | Gen Number | POI | Contingency | SCR | Critical Clearing Time | Stability_Margin | Pg_out | Pg_rated | SCR PASS/FAIL | CCT PASS/FAIL
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | Base | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | Base | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | Base | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | Base | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | Base | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | Base | 4.679 | 3.0717 | 2971.7137 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | Base | 26.469 | 15.509 | 15409.0357 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 6.9472 | 0.4763 | 376.3411 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.679 | 3.0717 | 2971.6969 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 26.4688 | 15.509 | 15409.0225 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 7.011 | 0.4762 | 376.1973 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 3.0716 | 2971.5651 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 26.4665 | 15.5091 | 15409.0611 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 3.9466 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 3.9466 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.6789 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 7.0409 | 0.4761 | 376.0619 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.6789 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.6789 | 3.0717 | 2971.7161 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 26.4688 | 15.5091 | 15409.0533 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 3.9468 | 0.4936 | 393.5888 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 3.9468 | 0.4876 | 387.5938 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.679 | 0.3099 | 209.9172 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.679 | 0.3774 | 277.3873 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.679 | 3.0716 | 2971.6083 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 26.4463 | 15.5069 | 15406.9053 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 3.9464 | 0.4936 | 393.5938 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 3.9464 | 0.4876 | 387.5983 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.6788 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.6788 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.6788 | 3.0715 | 2971.455 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 26.4641 | 15.5063 | 15406.2877 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 3.9466 | 0.4936 | 393.6029 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 3.9466 | 0.4876 | 387.6065 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.6789 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.6789 | 0.3774 | 277.3876 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.6789 | 3.0717 | 2971.7438 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 26.455 | 15.5075 | 15407.4692 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 3.3275 | 0.5025 | 402.5085 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 3.3275 | 0.4959 | 395.9005 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6787 | 0.3099 | 209.9166 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 7.0413 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6787 | 0.3774 | 277.3868 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6787 | 3.0713 | 2971.3312 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 26.4646 | 15.5088 | 15408.798 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 3.9183 | 0.4943 | 394.3052 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 3.9183 | 0.4883 | 388.2989 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.6748 | 0.3099 | 209.9243 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.6748 | 0.3774 | 277.3984 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.6748 | 3.07 | 2969.9522 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 26.4266 | 15.5118 | 15411.7573 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 3.6444 | 0.4965 | 396.5333 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 3.6444 | 0.4903 | 390.3333 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.6727 | 0.3099 | 209.9247 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 7.0421 | 0.4761 | 376.0504 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.6727 | 0.3774 | 277.3973 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.6727 | 3.0744 | 2974.4442 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 26.356 | 15.5231 | 15423.0546 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 3.8659 | 0.494 | 393.9877 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 3.8659 | 0.4881 | 388.132 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.6754 | 0.3099 | 209.9166 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 7.0417 | 0.4761 | 376.0521 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.6754 | 0.3774 | 277.3897 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.6754 | 3.0672 | 2967.2047 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 26.4303 | 15.5102 | 15410.2126 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 3.9402 | 0.4935 | 393.5454 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 3.9402 | 0.4876 | 387.5748 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3433 | 0.3362 | 236.2079 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 7.0414 | 0.4761 | 376.0521 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3433 | 0.412 | 312.0032 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3433 | 3.4569 | 3356.8912 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 26.4105 | 15.5158 | 15415.8429 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 3.9217 | 0.4942 | 394.2136 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 3.9217 | 0.4882 | 388.1938 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.6789 | 0.3099 | 209.9175 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.6789 | 0.3774 | 277.3877 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.6789 | 3.072 | 2971.9842 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 26.4671 | 15.5096 | 15409.5596 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 3.8207 | 0.4962 | 396.2048 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 3.8207 | 0.49 | 390.0273 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.6763 | 0.3099 | 209.9215 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.6763 | 0.3774 | 277.3946 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.6763 | 3.0688 | 2968.7922 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 26.4282 | 15.5153 | 15415.326 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 0.75521 | 0.7167 | 616.6972 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 0.75521 | 0.6942 | 594.1861 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6771 | 0.3099 | 209.9138 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 7.0415 | 0.4761 | 376.0519 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6771 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.6771 | 3.0645 | 2964.5469 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 26.4593 | 15.5085 | 15408.507 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 6.7345 | 0.4778 | 377.8363 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.679 | 3.0717 | 2971.7097 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 26.4689 | 15.509 | 15409.0429 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9118 | 0.4936 | 393.6258 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9118 | 0.4876 | 387.6235 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6783 | 0.3099 | 209.9094 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 7.0411 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6783 | 0.3774 | 277.3794 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6783 | 3.0679 | 2967.8927 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 25.2107 | 15.4565 | 15356.5424 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.946 | 0.4936 | 393.5915 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.946 | 0.4876 | 387.5962 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6731 | 0.3099 | 209.9299 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6731 | 0.3774 | 277.4061 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6731 | 3.07 | 2969.972 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 24.3394 | 15.5506 | 15450.6225 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 3.946 | 0.4936 | 393.5916 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 3.946 | 0.4876 | 387.5962 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.6731 | 0.3099 | 209.9299 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.6731 | 0.3774 | 277.4061 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.6731 | 3.07 | 2969.9696 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 24.3397 | 15.5503 | 15450.2645 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 3.9459 | 0.4936 | 393.6021 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 3.9459 | 0.4876 | 387.6047 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.6779 | 0.3099 | 209.9204 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.6779 | 0.3774 | 277.3912 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.6779 | 3.0729 | 2972.9485 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 24.8395 | 15.542 | 15441.994 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 3.946 | 0.4936 | 393.5976 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 3.946 | 0.4876 | 387.601 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.678 | 0.3099 | 209.9184 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.678 | 0.3774 | 277.3891 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.678 | 3.0719 | 2971.8505 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 25.1487 | 15.5532 | 15453.2094 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 3.9357 | 0.4937 | 393.6565 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 3.9357 | 0.4877 | 387.6554 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.6782 | 0.3099 | 209.9163 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.6782 | 0.3774 | 277.3866 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.6782 | 3.0715 | 2971.4533 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 26.451 | 15.5035 | 15403.5002 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9455 | 0.4936 | 393.6 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9455 | 0.4876 | 387.6032 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.678 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.678 | 0.3774 | 277.3879 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.678 | 3.0717 | 2971.7082 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 24.9968 | 15.549 | 15448.9733 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 3.9468 | 0.4936 | 393.5986 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 3.9468 | 0.4876 | 387.6012 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.6793 | 0.3099 | 209.9167 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 7.0418 | 0.4761 | 376.051 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.6793 | 0.3774 | 277.3865 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.6793 | 3.0723 | 2972.2801 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 26.4834 | 15.5219 | 15421.8634 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 3.9448 | 0.4936 | 393.6115 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 3.9448 | 0.4876 | 387.6151 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.6782 | 0.3099 | 209.9189 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 7.0412 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.6782 | 0.3774 | 277.3896 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.6782 | 3.0715 | 2971.5356 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 26.2438 | 15.5061 | 15406.137 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9423 | 0.4936 | 393.5977 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9423 | 0.4876 | 387.599 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6727 | 0.3099 | 209.9241 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 7.043 | 0.476 | 376.0483 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6727 | 0.3774 | 277.3972 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6727 | 3.0727 | 2972.6547 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 23.4393 | 15.6631 | 15563.1433 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 3.9508 | 0.4939 | 393.9449 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 3.9508 | 0.488 | 387.9735 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.6786 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 7.0411 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.6786 | 0.3774 | 277.3874 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.6786 | 3.0713 | 2971.2964 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 26.4673 | 15.5086 | 15408.5811 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 3.3109 | 0.4996 | 399.6011 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 3.3109 | 0.4929 | 392.8878 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.6785 | 0.3099 | 209.9167 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.6785 | 0.3774 | 277.3869 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.6785 | 3.0714 | 2971.4267 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 26.4646 | 15.5089 | 15408.8889 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 3.943 | 0.4945 | 394.4575 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 3.943 | 0.4885 | 388.4659 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.6783 | 0.3099 | 209.9175 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 7.041 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.6783 | 0.3774 | 277.388 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.6783 | 3.0711 | 2971.0872 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 26.4648 | 15.5083 | 15408.3136 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.9347 | 0.4935 | 393.5491 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.9347 | 0.4876 | 387.5633 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.7404 | 0.3141 | 214.0738 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 7.0413 | 0.4761 | 376.0522 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.7404 | 0.3828 | 282.8239 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.7404 | 3.2255 | 3125.5131 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 26.1353 | 15.5396 | 15439.614 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 3.93 | 0.4936 | 393.6328 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 3.93 | 0.4876 | 387.6417 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6548 | 0.31 | 210.045 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6548 | 0.3776 | 277.5518 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6548 | 3.077 | 2977.008 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 26.4362 | 15.5038 | 15403.8276 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 3.9464 | 0.4936 | 393.5998 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 3.9464 | 0.4876 | 387.6035 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.6787 | 0.3099 | 209.9192 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.6787 | 0.3774 | 277.3897 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.6787 | 3.0719 | 2971.9447 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 26.4669 | 15.509 | 15409.017 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 3.9446 | 0.4936 | 393.611 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 3.9446 | 0.4876 | 387.6145 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.6768 | 0.3099 | 209.9331 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.6768 | 0.3774 | 277.4071 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.6768 | 3.0732 | 2973.2048 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 26.4525 | 15.5088 | 15408.8025 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9456 | 0.4936 | 393.6034 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9456 | 0.4876 | 387.6061 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6783 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6783 | 0.3774 | 277.3882 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6783 | 3.0701 | 2970.0954 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 25.3451 | 15.524 | 15423.9954 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 3.9476 | 0.4936 | 393.606 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 3.9476 | 0.4876 | 387.6046 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.6803 | 0.3099 | 209.919 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 7.0411 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.6803 | 0.3774 | 277.3859 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.6803 | 3.0793 | 2979.2794 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 26.3672 | 15.5113 | 15411.3208 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 3.9461 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 3.9461 | 0.4876 | 387.6014 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.6782 | 0.3099 | 209.9175 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 7.0419 | 0.4761 | 376.051 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.6782 | 0.3774 | 277.388 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.6782 | 3.0716 | 2971.632 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 26.0841 | 15.525 | 15425.0465 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 3.9465 | 0.4936 | 393.5996 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 3.9465 | 0.4876 | 387.6033 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.6787 | 0.3099 | 209.918 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 7.0406 | 0.4761 | 376.0531 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.6787 | 0.3774 | 277.3883 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.6787 | 3.0718 | 2971.791 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 26.453 | 15.5032 | 15403.2383 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 3.9465 | 0.4936 | 393.6029 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 3.9465 | 0.4876 | 387.6062 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.6787 | 0.3099 | 209.9203 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 7.0403 | 0.4761 | 376.0532 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.6787 | 0.3774 | 277.3909 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.6787 | 3.0726 | 2972.6029 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 26.4431 | 15.5035 | 15403.4902 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 3.9466 | 0.4936 | 393.6048 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 3.9466 | 0.4876 | 387.608 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.6789 | 0.3099 | 209.9217 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 7.0408 | 0.4761 | 376.0535 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.6789 | 0.3774 | 277.3924 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.6789 | 3.0729 | 2972.8976 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 26.4357 | 15.501 | 15401.0241 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 3.9466 | 0.4936 | 393.607 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 3.9466 | 0.4876 | 387.6099 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.6789 | 0.3099 | 209.9231 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 7.0407 | 0.4761 | 376.0538 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.6789 | 0.3774 | 277.394 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.6789 | 3.0733 | 2973.268 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 26.4253 | 15.4986 | 15398.6473 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.6789 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.6789 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.6789 | 3.0716 | 2971.6415 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 26.4696 | 15.5087 | 15408.7491 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.6789 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.6789 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.6789 | 3.0716 | 2971.6417 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 26.4696 | 15.5087 | 15408.749 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9396 | 0.4935 | 393.5394 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9396 | 0.4876 | 387.5709 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3579 | 0.3373 | 237.3112 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 7.0414 | 0.4761 | 376.0519 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3579 | 0.4135 | 313.4745 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3579 | 3.2208 | 3120.8353 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 26.4108 | 15.5173 | 15417.3117 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 3.9458 | 0.4936 | 393.5975 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 3.9458 | 0.4876 | 387.6069 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.6787 | 0.3099 | 209.9158 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 7.0415 | 0.4761 | 376.0518 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.6787 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.6787 | 3.0696 | 2969.6148 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 26.4827 | 15.5137 | 15413.7103 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.6789 | 0.3099 | 209.9167 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 7.0111 | 0.4762 | 376.1627 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.6789 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.6789 | 3.0714 | 2971.3653 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 26.4652 | 15.509 | 15408.9853 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 3.898 | 0.4942 | 394.2138 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 3.898 | 0.4882 | 388.1985 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.67 | 0.31 | 209.9718 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 7.0411 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.67 | 0.3775 | 277.4514 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.67 | 3.0929 | 2992.9166 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 26.344 | 15.5097 | 15409.671 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 3.9458 | 0.4936 | 393.6283 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 3.9458 | 0.4876 | 387.6314 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.6793 | 0.3099 | 209.9161 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 7.0422 | 0.4761 | 376.0503 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.6793 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.6793 | 3.0709 | 2970.9063 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 26.4901 | 15.5251 | 15425.1196 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 3.9457 | 0.4937 | 393.6539 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 3.9457 | 0.4876 | 387.6414 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.6781 | 0.3099 | 209.9209 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 7.0411 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.6781 | 0.3774 | 277.391 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.6781 | 3.0744 | 2974.4094 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 26.3135 | 15.5156 | 15415.579 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 3.9308 | 0.4934 | 393.426 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 3.9308 | 0.4875 | 387.4576 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.6769 | 0.3099 | 209.9305 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.6769 | 0.3774 | 277.4078 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.6769 | 3.063 | 2962.9813 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 26.3529 | 15.493 | 15392.9966 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 3.9466 | 0.4937 | 393.6613 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 3.9466 | 0.4877 | 387.6583 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.6794 | 0.31 | 209.9572 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 7.0401 | 0.4761 | 376.0552 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.6794 | 0.3774 | 277.432 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.6794 | 3.0823 | 2982.2634 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 26.4029 | 15.4963 | 15396.3092 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 3.9443 | 0.4936 | 393.5862 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 3.9443 | 0.4876 | 387.5939 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.6735 | 0.3099 | 209.9211 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 7.0413 | 0.4761 | 376.0517 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.6735 | 0.3774 | 277.3973 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.6735 | 3.0635 | 2963.5449 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 26.046 | 15.4767 | 15376.7213 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9448 | 0.4936 | 393.6007 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9448 | 0.4876 | 387.6028 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6757 | 0.3099 | 209.9238 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 7.0411 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6757 | 0.3774 | 277.3966 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6757 | 3.0718 | 2971.8198 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 24.9904 | 15.5707 | 15470.6902 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 3.9449 | 0.4936 | 393.6011 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 3.9449 | 0.4876 | 387.6031 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.6757 | 0.3099 | 209.924 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 7.0411 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.6757 | 0.3774 | 277.3967 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.6757 | 3.0721 | 2972.1307 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 24.9796 | 15.5763 | 15476.2953 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9449 | 0.4936 | 393.5983 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9449 | 0.4876 | 387.6015 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6767 | 0.3099 | 209.9225 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 7.0413 | 0.4761 | 376.0511 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6767 | 0.3774 | 277.3948 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.6767 | 3.0718 | 2971.7934 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 25.0851 | 15.5422 | 15442.1679 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 3.945 | 0.4936 | 393.6005 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 3.945 | 0.4876 | 387.6027 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.6769 | 0.3099 | 209.9233 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 7.0413 | 0.4761 | 376.0513 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.6769 | 0.3774 | 277.3952 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.6769 | 3.0731 | 2973.1269 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 25.0391 | 15.5662 | 15466.1618 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 6.6244 | 0.4776 | 377.6052 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.679 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.679 | 3.0718 | 2971.8428 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 26.4691 | 15.5091 | 15409.1027 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 3.9461 | 0.4936 | 393.5981 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 3.9461 | 0.4876 | 387.6027 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6655 | 0.3103 | 210.3228 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 7.0409 | 0.4761 | 376.0528 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6655 | 0.3779 | 277.8936 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6655 | 3.0626 | 2962.5828 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 26.464 | 15.5083 | 15408.2674 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 6.8476 | 0.4772 | 377.1756 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.679 | 3.0717 | 2971.7213 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 26.4689 | 15.509 | 15409.0376 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 6.9173 | 0.4767 | 376.7299 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.679 | 3.0717 | 2971.7164 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 26.4689 | 15.509 | 15409.0388 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 6.8893 | 0.4769 | 376.9107 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.679 | 3.0717 | 2971.7079 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 26.4689 | 15.509 | 15409.0345 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 6.8002 | 0.4772 | 377.1562 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.679 | 3.0717 | 2971.7153 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 26.469 | 15.509 | 15409.0355 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 7.0803 | 0.471 | 371.0055 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 3.0717 | 2971.678 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 26.4688 | 15.509 | 15408.9908 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 7.0803 | 0.471 | 371.0055 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.679 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.679 | 3.0717 | 2971.6781 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 26.4688 | 15.509 | 15408.9908 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 7.0817 | 0.471 | 371.0242 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.679 | 3.0717 | 2971.6781 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 26.4688 | 15.509 | 15408.9908 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 7.0817 | 0.471 | 371.0242 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.679 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.679 | 3.0717 | 2971.6781 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 26.4688 | 15.509 | 15408.9908 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.6789 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 7.0374 | 0.4761 | 376.067 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.6789 | 0.3774 | 277.3875 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.6789 | 3.0718 | 2971.8162 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 26.4679 | 15.509 | 15409.0067 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 5.2863 | 0.4864 | 386.4454 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.7156 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 26.4687 | 15.5091 | 15409.0612 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 5.4077 | 0.4915 | 391.461 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.679 | 3.0717 | 2971.7156 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 26.4689 | 15.5091 | 15409.0538 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 3.9446 | 0.4936 | 393.5694 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 3.9446 | 0.4876 | 387.5745 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6505 | 0.31 | 209.9819 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6505 | 0.3775 | 277.4804 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6505 | 3.0697 | 2969.7191 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 17.9367 | 15.7858 | 15685.7588 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.6789 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 7.0104 | 0.4762 | 376.2146 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.6789 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.6789 | 3.0716 | 2971.5955 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 26.4665 | 15.5091 | 15409.0844 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 6.735 | 0.4778 | 377.8356 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.679 | 3.0717 | 2971.7098 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 26.469 | 15.509 | 15409.0428 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 7.0419 | 0.476 | 376.0498 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.679 | 3.0717 | 2971.7136 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 26.469 | 15.509 | 15409.0356 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 7.0417 | 0.476 | 376.0488 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 3.0717 | 2971.7135 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 26.4689 | 15.509 | 15409.0356 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 3.9469 | 0.4936 | 393.6003 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 3.9469 | 0.4876 | 387.6029 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.6797 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 7.0428 | 0.476 | 376.0488 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.6797 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.6797 | 3.0728 | 2972.7686 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 26.5395 | 15.5602 | 15460.1841 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 5.9454 | 0.4841 | 384.128 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.679 | 3.0717 | 2971.7241 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 26.4689 | 15.509 | 15409.0362 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 3.9467 | 0.4936 | 393.598 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 3.9467 | 0.4876 | 387.6018 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.679 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.679 | 3.0717 | 2971.7431 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 26.4653 | 15.5086 | 15408.6028 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 3.9467 | 0.4936 | 393.598 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 3.9467 | 0.4876 | 387.6018 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.679 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.679 | 3.0717 | 2971.7431 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 26.4653 | 15.5086 | 15408.6028 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 3.3247 | 0.5024 | 402.4385 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 3.3247 | 0.4958 | 395.8184 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.6787 | 0.3099 | 209.9167 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 7.0413 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.6787 | 0.3774 | 277.3869 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.6787 | 3.0714 | 2971.3572 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 26.4644 | 15.5088 | 15408.8217 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.738 | 0.4964 | 396.3606 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.738 | 0.4903 | 390.2997 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6748 | 0.3099 | 209.9162 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6748 | 0.3774 | 277.3888 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6748 | 3.0678 | 2967.8065 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.4026 | 15.5122 | 15412.2006 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.5736 | 0.5026 | 402.5618 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.5736 | 0.4961 | 396.0739 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6745 | 0.3099 | 209.916 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 7.0413 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6745 | 0.3774 | 277.3908 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6745 | 3.0628 | 2962.8059 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.4177 | 15.5144 | 15414.4226 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 7.0413 | 0.4761 | 376.0523 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.679 | 3.0717 | 2971.7137 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 26.469 | 15.509 | 15409.0357 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 3.9181 | 0.4938 | 393.8201 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 3.9181 | 0.4878 | 387.8237 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.6762 | 0.3099 | 209.918 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.6762 | 0.3774 | 277.3908 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.6762 | 3.0671 | 2967.0876 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 25.9389 | 15.5411 | 15441.0736 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 3.9392 | 0.4936 | 393.5879 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 3.9392 | 0.4876 | 387.5881 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6623 | 0.3099 | 209.937 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 7.0443 | 0.476 | 376.0452 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6623 | 0.3774 | 277.4178 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6623 | 3.0702 | 2970.2301 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 24.4392 | 15.6445 | 15544.5329 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 3.9393 | 0.4936 | 393.5868 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 3.9393 | 0.4876 | 387.5869 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.6624 | 0.3099 | 209.9364 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 7.0443 | 0.476 | 376.0452 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.6624 | 0.3774 | 277.4169 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.6624 | 3.0703 | 2970.2677 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 24.4414 | 15.6465 | 15546.5184 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9444 | 0.4936 | 393.5989 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9444 | 0.4876 | 387.6015 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6763 | 0.3099 | 209.9209 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 7.0411 | 0.4761 | 376.0528 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6763 | 0.3774 | 277.3927 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.6763 | 3.0716 | 2971.6079 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 24.7437 | 15.5765 | 15476.4761 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 3.9362 | 0.4936 | 393.5841 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 3.9362 | 0.4876 | 387.5894 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6174 | 0.3101 | 210.1029 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6174 | 0.3776 | 277.6349 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6174 | 3.084 | 2983.9594 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 26.1084 | 15.4901 | 15390.0623 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.679 | 3.0717 | 2971.7046 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 26.469 | 15.509 | 15409.0003 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.679 | 3.0717 | 2971.7046 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 26.469 | 15.509 | 15409.0003 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 3.9463 | 0.4936 | 393.6018 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 3.9463 | 0.4876 | 387.6056 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.6784 | 0.3099 | 209.9198 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 7.0403 | 0.4761 | 376.0532 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.6784 | 0.3774 | 277.3906 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.6784 | 3.0716 | 2971.5624 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 26.4523 | 15.4991 | 15399.1227 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9272 | 0.4935 | 393.482 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9272 | 0.4875 | 387.4961 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6206 | 0.31 | 210.0051 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 7.0411 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6206 | 0.3775 | 277.5197 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6206 | 3.0689 | 2968.8599 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 25.9344 | 15.4781 | 15378.1079 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 3.9448 | 0.4936 | 393.5964 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 3.9448 | 0.4876 | 387.5995 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.675 | 0.3099 | 209.9263 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 7.0414 | 0.4761 | 376.051 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.675 | 0.3774 | 277.4 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.675 | 3.0721 | 2972.0899 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 25.9583 | 15.5132 | 15413.1772 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 3.9429 | 0.4936 | 393.6044 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 3.9429 | 0.4876 | 387.6076 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.6791 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.6791 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.6791 | 3.0714 | 2971.4135 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 26.1294 | 15.4984 | 15398.3829 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 3.9441 | 0.4936 | 393.5949 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 3.9441 | 0.4876 | 387.5984 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.6752 | 0.3099 | 209.9193 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 7.0428 | 0.476 | 376.0489 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.6752 | 0.3774 | 277.3914 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.6752 | 3.0707 | 2970.6835 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 24.9577 | 15.5671 | 15467.116 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 3.946 | 0.4936 | 393.5997 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 3.946 | 0.4876 | 387.6032 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.6781 | 0.3099 | 209.9185 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 7.0416 | 0.4761 | 376.0515 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.6781 | 0.3774 | 277.3892 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.6781 | 3.0717 | 2971.7379 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 26.0696 | 15.5189 | 15418.8796 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9455 | 0.4936 | 393.6051 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9455 | 0.4876 | 387.6117 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6265 | 0.3102 | 210.1643 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6265 | 0.3777 | 277.7081 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6265 | 3.0786 | 2978.5556 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 26.3759 | 15.513 | 15413.0051 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.679 | 0.3099 | 209.9172 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 6.9824 | 0.4763 | 376.3464 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.679 | 0.3774 | 277.3873 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.679 | 3.0718 | 2971.8336 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 26.4687 | 15.509 | 15409.011 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 3.9446 | 0.4936 | 393.596 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 3.9446 | 0.4876 | 387.6003 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.6752 | 0.3099 | 209.9221 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 7.041 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.6752 | 0.3774 | 277.3957 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.6752 | 3.0689 | 2968.9216 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 25.0876 | 15.5203 | 15420.3049 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 3.9447 | 0.4936 | 393.595 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 3.9447 | 0.4876 | 387.5997 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.6763 | 0.3099 | 209.9212 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 7.0413 | 0.4761 | 376.0514 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.6763 | 0.3774 | 277.3942 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.6763 | 3.0697 | 2969.6548 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 25.1568 | 15.5051 | 15405.1133 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 3.9461 | 0.4936 | 393.5981 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 3.9461 | 0.4876 | 387.6027 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6655 | 0.3103 | 210.3228 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 7.0409 | 0.4761 | 376.0528 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6655 | 0.3779 | 277.8936 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6655 | 3.0626 | 2962.5829 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 26.464 | 15.5083 | 15408.2674 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9468 | 0.4936 | 393.5996 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9468 | 0.4876 | 387.6026 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6797 | 0.3099 | 209.9172 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 7.0428 | 0.476 | 376.0488 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6797 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.6797 | 3.0724 | 2972.4133 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 26.5506 | 15.5539 | 15453.9185 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 3.9469 | 0.4936 | 393.6003 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 3.9469 | 0.4876 | 387.6029 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.6797 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 7.0428 | 0.476 | 376.0488 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.6797 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.6797 | 3.0728 | 2972.7686 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 26.5395 | 15.5602 | 15460.1841 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 3.9464 | 0.4936 | 393.5982 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 3.9464 | 0.4876 | 387.602 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.6782 | 0.3099 | 209.9186 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.6782 | 0.3774 | 277.3893 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.6782 | 3.0717 | 2971.7152 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 26.371 | 15.5116 | 15411.5516 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 3.9466 | 0.4936 | 393.598 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 3.9466 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.6786 | 0.3099 | 209.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.6786 | 0.3774 | 277.3885 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.6786 | 3.0718 | 2971.7557 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 26.4113 | 15.5109 | 15410.8934 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 3.9464 | 0.4936 | 393.5943 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 3.9464 | 0.4876 | 387.599 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.6782 | 0.3099 | 209.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 7.0413 | 0.4761 | 376.0523 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.6782 | 0.3774 | 277.389 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.6782 | 3.0707 | 2970.6791 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 26.3676 | 15.5183 | 15418.2617 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 7.0095 | 0.4762 | 376.1645 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.679 | 3.0717 | 2971.7343 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 26.4689 | 15.509 | 15409.0322 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 7.0384 | 0.4761 | 376.0724 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.679 | 3.0717 | 2971.7216 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 26.4689 | 15.509 | 15409.034 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9475 | 0.4936 | 393.6121 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9475 | 0.4876 | 387.6121 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9353 | 0.3157 | 215.6718 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9353 | 0.3849 | 284.8977 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9353 | 3.0521 | 2952.1344 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 26.4469 | 15.5091 | 15409.0663 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 7.0402 | 0.4761 | 376.0616 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.679 | 3.0717 | 2971.7178 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 26.469 | 15.509 | 15409.0338 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 3.8797 | 0.4948 | 394.7574 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 3.8797 | 0.4887 | 388.7323 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.6718 | 0.31 | 209.9532 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 7.0411 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.6718 | 0.3774 | 277.4394 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.6718 | 3.059 | 2959.0134 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 26.4388 | 15.5099 | 15409.8738 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 3.9436 | 0.4936 | 393.6017 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 3.9436 | 0.4876 | 387.6092 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.6768 | 0.3099 | 209.9262 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.6768 | 0.3774 | 277.4 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.6768 | 3.0697 | 2969.6834 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 26.457 | 15.5126 | 15412.599 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 3.9281 | 0.4943 | 394.2739 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 3.9281 | 0.4883 | 388.2631 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.6777 | 0.3099 | 209.9246 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.6777 | 0.3774 | 277.3975 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.6777 | 3.07 | 2970.0453 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 26.4565 | 15.5094 | 15409.358 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 3.8922 | 0.4945 | 394.5095 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 3.8922 | 0.4885 | 388.4547 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.6809 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.6809 | 0.3774 | 277.3842 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.6809 | 3.0779 | 2977.8751 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 26.4329 | 15.5129 | 15412.8959 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9471 | 0.4936 | 393.6033 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9471 | 0.4876 | 387.6068 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5795 | 0.3313 | 231.3131 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5795 | 0.4057 | 305.7126 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5795 | 3.1523 | 3052.2537 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 26.4098 | 15.51 | 15410.0367 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 3.9448 | 0.4936 | 393.6272 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 3.9448 | 0.4876 | 387.6295 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3477 | 0.3119 | 211.8902 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3477 | 0.38 | 279.9876 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3477 | 3.0882 | 2988.1724 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 26.4459 | 15.5097 | 15409.7383 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 3.9466 | 0.4936 | 393.5992 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 3.9466 | 0.4876 | 387.6031 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.6766 | 0.3099 | 209.9215 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.6766 | 0.3774 | 277.3949 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.6766 | 3.0711 | 2971.1463 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 26.4689 | 15.509 | 15409.0159 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 3.947 | 0.4936 | 393.6088 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 3.947 | 0.4876 | 387.6114 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6493 | 0.3101 | 210.1251 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6493 | 0.3777 | 277.66 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6493 | 3.0585 | 2958.4682 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 26.4685 | 15.509 | 15408.9744 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 3.946 | 0.4937 | 393.7072 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 3.946 | 0.4877 | 387.6972 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.3991 | 0.3118 | 211.7876 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.3991 | 0.3798 | 279.8215 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.3991 | 3.0554 | 2955.3936 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 26.4633 | 15.5116 | 15411.572 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 7.027 | 0.4761 | 376.1496 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.6985 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 26.4687 | 15.5091 | 15409.0606 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 3.9466 | 0.4936 | 393.6418 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 3.9466 | 0.4876 | 387.6362 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.6314 | 0.3102 | 210.2362 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.6314 | 0.3778 | 277.8119 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.6314 | 3.0398 | 2939.8154 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 26.4678 | 15.5091 | 15409.1386 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 3.947 | 0.4936 | 393.6149 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 3.947 | 0.4876 | 387.613 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.5782 | 0.3104 | 210.4153 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 7.0415 | 0.4761 | 376.0518 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.5782 | 0.378 | 278.0309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.5782 | 3.1132 | 3013.1921 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 26.4631 | 15.5122 | 15412.225 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 3.947 | 0.4936 | 393.615 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 3.947 | 0.4876 | 387.613 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.5785 | 0.3104 | 210.4126 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 7.0415 | 0.4761 | 376.0517 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.5785 | 0.378 | 278.0272 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.5785 | 3.1136 | 3013.6296 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 26.4632 | 15.5123 | 15412.2571 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 3.9455 | 0.4936 | 393.596 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 3.9455 | 0.4876 | 387.6048 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5105 | 0.3121 | 212.057 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 7.0413 | 0.4761 | 376.0523 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5105 | 0.3802 | 280.1726 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5105 | 2.9643 | 2864.257 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 26.4643 | 15.5101 | 15410.109 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 3.9469 | 0.4936 | 393.5991 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 3.9469 | 0.4876 | 387.6023 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.6631 | 0.3101 | 210.0697 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.6631 | 0.3776 | 277.5819 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.6631 | 3.0628 | 2962.8124 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 26.4625 | 15.5091 | 15409.0753 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 3.94 | 0.4936 | 393.6179 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 3.94 | 0.4876 | 387.6205 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4162 | 0.3113 | 211.3347 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0526 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4162 | 0.3792 | 279.2342 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4162 | 3.0762 | 2976.2027 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 26.3576 | 15.5128 | 15412.8274 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 3.9465 | 0.4936 | 393.6003 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 3.9465 | 0.4876 | 387.6041 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.6783 | 0.3099 | 209.9468 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 7.0409 | 0.4761 | 376.0528 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.6783 | 0.3774 | 277.4232 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.6783 | 3.0729 | 2972.9236 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 26.464 | 15.5083 | 15408.2511 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 3.945 | 0.4936 | 393.5837 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 3.945 | 0.4876 | 387.5902 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.6497 | 0.31 | 209.9708 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.6497 | 0.3775 | 277.4811 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.6497 | 3.0277 | 2927.6954 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 26.4252 | 15.5203 | 15420.3174 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 3.9461 | 0.4936 | 393.6037 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 3.9461 | 0.4876 | 387.6054 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.5882 | 0.3104 | 210.3959 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.5882 | 0.378 | 277.9933 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.5882 | 3.1157 | 3015.6754 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 26.4372 | 15.5144 | 15414.428 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 3.9451 | 0.4936 | 393.6005 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 3.9451 | 0.4876 | 387.6041 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5408 | 0.3106 | 210.5729 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5408 | 0.3782 | 278.243 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5408 | 3.0774 | 2977.3902 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 26.4255 | 15.5133 | 15413.3495 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 7.0269 | 0.4762 | 376.1503 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.6982 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 26.4687 | 15.5091 | 15409.0609 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 3.9462 | 0.4936 | 393.5962 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 3.9462 | 0.4876 | 387.6009 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.6775 | 0.3099 | 209.9166 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 7.041 | 0.4761 | 376.0529 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.6775 | 0.3774 | 277.3886 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.6775 | 3.0678 | 2967.7621 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 26.3776 | 15.4952 | 15395.1603 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 3.9463 | 0.4936 | 393.5992 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 3.9463 | 0.4876 | 387.6023 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.6784 | 0.3099 | 209.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 7.042 | 0.4761 | 376.0507 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.6784 | 0.3774 | 277.3883 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.6784 | 3.0725 | 2972.5095 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 26.3056 | 15.5232 | 15423.2264 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 3.9463 | 0.4936 | 393.5992 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 3.9463 | 0.4876 | 387.6025 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.6784 | 0.3099 | 209.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 7.042 | 0.4761 | 376.0507 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.6784 | 0.3774 | 277.3883 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.6784 | 3.0725 | 2972.5097 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 26.3057 | 15.5232 | 15423.2234 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 3.9463 | 0.4936 | 393.5993 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 3.9463 | 0.4876 | 387.6025 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.6784 | 0.3099 | 209.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 7.042 | 0.4761 | 376.0507 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.6784 | 0.3774 | 277.3883 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.6784 | 3.0725 | 2972.5096 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 26.3058 | 15.5232 | 15423.2204 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 3.9465 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 3.9465 | 0.4876 | 387.6019 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.6779 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 7.0413 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.6779 | 0.3774 | 277.388 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.6779 | 3.0697 | 2969.7108 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 26.4143 | 15.5012 | 15401.1985 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 3.9461 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 3.9461 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.6784 | 0.3099 | 209.9175 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.6784 | 0.3774 | 277.388 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.6784 | 3.0713 | 2971.2783 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 26.3785 | 15.5084 | 15408.352 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 3.9466 | 0.4936 | 393.5984 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 3.9466 | 0.4876 | 387.6022 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.6789 | 0.3099 | 209.9174 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 7.041 | 0.4761 | 376.0528 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.6789 | 0.3774 | 277.3876 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.6789 | 3.0718 | 2971.8417 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 26.4637 | 15.508 | 15408.0448 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 3.9456 | 0.4936 | 393.6026 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 3.9456 | 0.4876 | 387.6055 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.6782 | 0.3099 | 209.9169 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 7.0412 | 0.4761 | 376.0527 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.6782 | 0.3774 | 277.388 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.6782 | 3.0698 | 2969.8202 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 25.3485 | 15.5275 | 15427.4508 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 3.9467 | 0.4936 | 393.5977 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.6789 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 7.0363 | 0.4761 | 376.0675 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.6789 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.6789 | 3.0715 | 2971.5374 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 26.4642 | 15.509 | 15408.9583 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5977 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6015 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.6787 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 7.0403 | 0.4761 | 376.0548 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.6787 | 0.3774 | 277.3874 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.6787 | 3.0713 | 2971.2518 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 26.4486 | 15.509 | 15408.9538 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.6042 | 0.5008 | 400.7586 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.6042 | 0.4944 | 394.4307 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6775 | 0.3099 | 209.9279 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6775 | 0.3774 | 277.4012 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.6775 | 3.0725 | 2972.5136 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.459 | 15.5112 | 15411.1808 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 7.0408 | 0.4761 | 376.0551 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.679 | 3.0717 | 2971.7315 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 26.4689 | 15.509 | 15409.0359 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 7.0408 | 0.4761 | 376.0551 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.679 | 3.0717 | 2971.7315 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 26.4689 | 15.509 | 15409.0359 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5977 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 0.3099 | 209.9167 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 7.034 | 0.4761 | 376.0661 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 0.3774 | 277.387 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.6789 | 3.0713 | 2971.318 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 26.466 | 15.5089 | 15408.8661 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.6789 | 0.3099 | 209.9172 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 7.041 | 0.4761 | 376.0504 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.6789 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.6789 | 3.0719 | 2971.8671 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 26.4655 | 15.5091 | 15409.1425 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.6789 | 0.3099 | 209.9172 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 7.041 | 0.4761 | 376.0504 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.6789 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.6789 | 3.0719 | 2971.8675 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 26.4655 | 15.5091 | 15409.142 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 7.041 | 0.4761 | 376.0516 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.679 | 0.3774 | 277.3872 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.679 | 3.0718 | 2971.792 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 26.467 | 15.5091 | 15409.1027 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 3.9466 | 0.4936 | 393.5977 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 3.9466 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.6787 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 7.0401 | 0.4761 | 376.0562 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.6787 | 0.3774 | 277.3874 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.6787 | 3.0713 | 2971.2919 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 26.4483 | 15.5091 | 15409.0542 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 7.0038 | 0.4763 | 376.2708 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.679 | 3.0717 | 2971.6838 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 26.4679 | 15.509 | 15409.0151 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 6.968 | 0.4763 | 376.321 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.679 | 3.0717 | 2971.7458 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 26.4689 | 15.509 | 15409.048 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.679 | 0.3099 | 209.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 6.9696 | 0.4763 | 376.3159 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.679 | 3.0717 | 2971.7451 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 26.4689 | 15.509 | 15409.0474 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 3.9453 | 0.4936 | 393.5878 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 3.9453 | 0.4876 | 387.5981 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.369 | 0.3116 | 211.5845 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 7.0413 | 0.4761 | 376.0524 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.369 | 0.3796 | 279.5956 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.369 | 3.0445 | 2944.4754 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 26.4518 | 15.5095 | 15409.488 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 5.2863 | 0.4864 | 386.4455 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.679 | 3.0717 | 2971.7156 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 26.4687 | 15.5091 | 15409.0612 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.4688 | 0.5025 | 402.5368 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 3.0717 | 2971.7089 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 26.4683 | 15.509 | 15409.0317 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 7.0072 | 0.4763 | 376.2617 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.7013 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 26.4683 | 15.5091 | 15409.086 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 7.0298 | 0.4761 | 376.0942 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.6954 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 26.4689 | 15.5091 | 15409.0591 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 7.0411 | 0.4761 | 376.0521 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.679 | 3.0717 | 2971.7119 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 26.469 | 15.509 | 15409.0353 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 6.767 | 0.4788 | 378.7843 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.679 | 3.0717 | 2971.7149 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 26.4689 | 15.509 | 15409.0389 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 6.7634 | 0.4788 | 378.8219 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.679 | 3.0717 | 2971.7149 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 26.4689 | 15.509 | 15409.039 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 3.9467 | 0.4936 | 393.5979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 3.9467 | 0.4876 | 387.6017 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 6.4261 | 0.4799 | 379.88 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.679 | 3.0717 | 2971.7153 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 26.4691 | 15.5091 | 15409.1062 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 6.9557 | 0.4763 | 376.3194 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.679 | 3.0717 | 2971.6971 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 26.4688 | 15.509 | 15409.0229 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 3.9467 | 0.4936 | 393.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 3.9467 | 0.4876 | 387.6016 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.679 | 0.3099 | 209.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 6.9558 | 0.4763 | 376.3189 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.679 | 0.3774 | 277.3871 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.679 | 3.0717 | 2971.697 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 26.4688 | 15.509 | 15409.0228 | 150 | 167.2 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 3.9468 | 0.4936 | 393.5968 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 3.9468 | 0.4876 | 387.6005 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.501 | 0.3106 | 210.6243 | 125 | 144 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 7.0412 | 0.4761 | 376.0525 | 72 | 88.9 | PASS | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.501 | 0.3784 | 278.3827 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.501 | 3.0554 | 2955.4435 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25SP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 26.4719 | 15.5087 | 15408.6772 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | Base | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | Base | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | Base | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | Base | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | Base | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | Base | 4.708 | 3.3819 | 3281.884 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | Base | 26.6121 | 15.5351 | 15435.0613 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 6.6108 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 4.708 | 3.3819 | 3281.884 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658002 [EXIRA 3G 13.800] CKT 1 | 26.6121 | 15.5351 | 15435.0613 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.708 | 0.3069 | 206.9287 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 6.5811 | 0.4771 | 377.1427 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.708 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.708 | 3.3817 | 3281.7458 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 26.6088 | 15.5347 | 15434.7171 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 3.9649 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 3.9649 | 0.4856 | 385.5523 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 6.609 | 0.477 | 377.0074 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 4.708 | 3.3819 | 3281.8688 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655484 [RASMUSN-ER4 230.00] TO BUS 655485 [RASMUSN-ER8 69.000] CKT 1 | 26.6117 | 15.535 | 15435.0305 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 3.9652 | 0.4915 | 391.5309 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 3.9652 | 0.4855 | 385.5437 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.7079 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.7079 | 0.3736 | 273.631 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 4.7079 | 3.3813 | 3281.3076 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655905 [RBNSNLAK-MW7115.00] CKT 1 | 26.5891 | 15.5309 | 15430.8628 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 3.9644 | 0.4915 | 391.5337 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 3.9644 | 0.4855 | 385.5469 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.7076 | 0.3069 | 206.9284 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 6.6107 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.7076 | 0.3736 | 273.6305 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 4.7076 | 3.3812 | 3281.1959 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655919 [OSBORN -MW7115.00] CKT 1 | 26.6066 | 15.5311 | 15431.054 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 3.9649 | 0.4915 | 391.5468 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 3.9649 | 0.4856 | 385.5583 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.708 | 0.3069 | 206.9294 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.708 | 0.3736 | 273.6315 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 4.708 | 3.3821 | 3282.0805 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 655920 [VANHOOK -MW7115.00] CKT 1 | 26.5972 | 15.5334 | 15433.427 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 3.3396 | 0.501 | 401.0451 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 3.3396 | 0.4945 | 394.4504 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7076 | 0.3069 | 206.9279 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 6.6109 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7076 | 0.3736 | 273.6301 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7076 | 3.3809 | 3280.9066 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 26.6071 | 15.5345 | 15434.5407 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 3.9364 | 0.4923 | 392.2516 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 3.9364 | 0.4863 | 386.2525 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.7042 | 0.3069 | 206.9263 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.7042 | 0.3736 | 273.63 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 4.7042 | 3.3796 | 3279.6033 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 26.5765 | 15.5381 | 15438.1446 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 3.6691 | 0.4938 | 393.7819 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 3.6691 | 0.4876 | 387.6064 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.7008 | 0.3069 | 206.9178 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 6.6125 | 0.477 | 376.989 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.7008 | 0.3736 | 273.6214 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 4.7008 | 3.3777 | 3277.6513 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659347 [PIONEER1-BE7115.00] CKT Z | 26.5084 | 15.5438 | 15443.8274 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 3.8874 | 0.4919 | 391.9254 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 3.8874 | 0.4861 | 386.0592 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.7042 | 0.3069 | 206.9195 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 6.6114 | 0.477 | 376.9926 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.7042 | 0.3736 | 273.623 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 4.7042 | 3.3752 | 3275.1655 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 659430 [PIONEER2-BE7115.00] CKT 1 | 26.578 | 15.5356 | 15435.6206 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 3.963 | 0.4915 | 391.518 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 3.963 | 0.4855 | 385.5377 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3864 | 0.3265 | 226.4835 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 6.6109 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3864 | 0.3997 | 299.6816 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 2.3864 | 4.5283 | 4428.2997 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659247 [MEDORA__-UM4230.00] CKT 1 | 26.5452 | 15.5395 | 15439.5415 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 3.9398 | 0.4922 | 392.17 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 3.9398 | 0.4862 | 386.1567 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.708 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 4.708 | 3.3823 | 3282.2867 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655934 [N.WLST_T-MW7115.00] CKT 1 | 26.6106 | 15.5355 | 15435.5452 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 3.8384 | 0.494 | 393.979 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 3.8384 | 0.4878 | 387.8124 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.7078 | 0.3069 | 206.9323 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.7078 | 0.3736 | 273.6335 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 4.7078 | 3.3863 | 3286.3428 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655957 [EASTFORK-MW7115.00] CKT 1 | 26.5726 | 15.5419 | 15441.9253 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 0.7667 | 0.7006 | 600.5546 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 0.7667 | 0.6786 | 578.621 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7059 | 0.3069 | 206.9181 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 6.6113 | 0.477 | 376.9921 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7059 | 0.3736 | 273.6221 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 4.7059 | 3.3727 | 3272.6739 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655940 [MONT -MW7115.00] TO BUS 655941 [STRNDAHL-MW7115.00] CKT 1 | 26.6037 | 15.5336 | 15433.5525 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 6.3232 | 0.4788 | 378.8352 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 4.708 | 3.3819 | 3281.8813 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 656267 [MANNINGTAP 869.000] TO BUS 656247 [TEMPLTON8 69.000] CKT 1 | 26.612 | 15.5351 | 15435.059 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9333 | 0.4914 | 391.4249 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9333 | 0.4854 | 385.4379 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.705 | 0.3069 | 206.9105 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.705 | 0.3736 | 273.6149 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.705 | 3.3662 | 3266.1586 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 25.2942 | 15.4649 | 15364.9308 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9645 | 0.4915 | 391.5314 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9645 | 0.4855 | 385.5442 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7027 | 0.3069 | 206.9291 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7027 | 0.3736 | 273.6341 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7027 | 3.3803 | 3280.3255 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 24.4459 | 15.5727 | 15472.7312 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 3.9645 | 0.4915 | 391.5314 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 3.9645 | 0.4855 | 385.5441 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.7027 | 0.3069 | 206.9291 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.7027 | 0.3736 | 273.6342 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 4.7027 | 3.3803 | 3280.3276 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 24.4461 | 15.5723 | 15472.3363 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 3.9643 | 0.4915 | 391.5422 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 3.9643 | 0.4856 | 385.5525 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.7073 | 0.3069 | 206.9305 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 6.6108 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.7073 | 0.3736 | 273.6325 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 4.7073 | 3.3839 | 3283.9477 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 24.9852 | 15.5754 | 15475.3973 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 3.9644 | 0.4915 | 391.5382 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 3.9644 | 0.4855 | 385.5494 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.7073 | 0.3069 | 206.9285 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.7073 | 0.3736 | 273.6305 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 4.7073 | 3.3825 | 3282.5177 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659105 [LELAND_O-BE3345.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 25.2933 | 15.5857 | 15485.6751 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 3.9548 | 0.4916 | 391.5627 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 3.9548 | 0.4856 | 385.5697 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.7071 | 0.3069 | 206.9252 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.7071 | 0.3736 | 273.6272 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 4.7071 | 3.3803 | 3280.2603 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659143 [BLAISDEL-BE4230.00] CKT 1 | 26.5896 | 15.5272 | 15427.1991 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9638 | 0.4915 | 391.5381 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9638 | 0.4855 | 385.5496 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7071 | 0.3069 | 206.927 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7071 | 0.3736 | 273.629 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7071 | 3.3816 | 3281.5555 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 25.1237 | 15.5748 | 15474.7631 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 3.9649 | 0.4915 | 391.5333 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 3.9649 | 0.4855 | 385.5444 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.7079 | 0.3069 | 206.9271 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 6.612 | 0.477 | 376.9902 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.7079 | 0.3736 | 273.6289 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 4.7079 | 3.3818 | 3281.835 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 760998 [GEN-2017-214230.00] CKT 1 | 26.6164 | 15.5454 | 15445.4162 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 3.9629 | 0.4916 | 391.5515 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 3.9629 | 0.4856 | 385.5635 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.7075 | 0.3069 | 206.9304 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 6.6107 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.7075 | 0.3736 | 273.6326 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 4.7075 | 3.3825 | 3282.4702 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659108 [LOGAN___-BE4230.00] TO BUS 659155 [LOGAN___-BE7115.00] TO BUS 659208 [LGN.KW1A-BE913.800] CKT 1 | 26.3821 | 15.5314 | 15431.4334 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9614 | 0.4915 | 391.5246 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9614 | 0.4855 | 385.5342 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7023 | 0.3069 | 206.925 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 6.6151 | 0.477 | 376.9827 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7023 | 0.3736 | 273.6275 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7023 | 3.3838 | 3283.8469 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659111 [LELAND_2-BEG20.000] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 23.5849 | 15.6954 | 15595.3637 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 3.9667 | 0.4922 | 392.1899 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 3.9667 | 0.4862 | 386.2234 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.7077 | 0.3069 | 206.929 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 6.6105 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.7077 | 0.3736 | 273.6311 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 4.7077 | 3.3816 | 3281.6313 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655776 [ALKABO -SH7115.00] CKT 1 | 26.61 | 15.5348 | 15434.7855 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 3.3316 | 0.4966 | 396.5892 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 3.3316 | 0.4899 | 389.8991 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.7077 | 0.3069 | 206.9283 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.7077 | 0.3736 | 273.6304 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 4.7077 | 3.3815 | 3281.4591 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 655778 [SNAKEBTT-SH7115.00] CKT 1 | 26.6094 | 15.5349 | 15434.8866 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 3.9593 | 0.4928 | 392.8146 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 3.9593 | 0.4868 | 386.8322 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.7074 | 0.3069 | 206.9294 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 6.6103 | 0.477 | 376.9937 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.7074 | 0.3736 | 273.6315 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 4.7074 | 3.3816 | 3281.6272 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659145 [GRENORA_-UM7115.00] TO BUS 661077 [PLNTYWD7 115.00] CKT 1 | 26.6079 | 15.5347 | 15434.7128 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.9539 | 0.4915 | 391.4706 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.9539 | 0.4855 | 385.4906 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.8179 | 0.3095 | 209.5015 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.8179 | 0.377 | 277.0437 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 3.8179 | 3.7587 | 3658.7478 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 652424 [BELFELD3 345.00] CKT 1 | 26.2499 | 15.5592 | 15459.1931 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 3.9486 | 0.4915 | 391.5257 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 3.9486 | 0.4855 | 385.5458 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6833 | 0.307 | 207.0284 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6833 | 0.3738 | 273.7594 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.6833 | 3.3915 | 3291.5473 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 26.5742 | 15.5289 | 15428.8818 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 3.9648 | 0.4915 | 391.5417 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 3.9648 | 0.4856 | 385.5535 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.7078 | 0.3069 | 206.9306 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.7078 | 0.3736 | 273.6331 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 4.7078 | 3.3821 | 3282.0697 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 26.6099 | 15.535 | 15435.0069 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 3.963 | 0.4915 | 391.5483 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 3.963 | 0.4856 | 385.5597 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.7056 | 0.3069 | 206.9421 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.7056 | 0.3736 | 273.6477 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 4.7056 | 3.3829 | 3282.9344 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 26.5948 | 15.5345 | 15434.5143 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9639 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.9639 | 0.4856 | 385.5516 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7082 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 6.6107 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7082 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7082 | 3.3823 | 3282.3179 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 25.4801 | 15.5531 | 15453.1101 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 3.9659 | 0.4915 | 391.5498 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 3.9659 | 0.4856 | 385.556 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.7089 | 0.3069 | 206.9341 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.7089 | 0.3736 | 273.6352 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 4.7089 | 3.3865 | 3286.5132 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 26.5119 | 15.5377 | 15437.6531 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 3.9644 | 0.4915 | 391.5383 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 3.9644 | 0.4855 | 385.5498 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.7072 | 0.3069 | 206.9283 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 6.612 | 0.477 | 376.9902 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.7072 | 0.3736 | 273.6303 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 4.7072 | 3.3821 | 3282.135 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 587030 [GEN-2016-004230.00] CKT 1 | 26.2263 | 15.5511 | 15451.1367 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 3.9648 | 0.4915 | 391.5424 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 3.9648 | 0.4856 | 385.5542 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.7078 | 0.3069 | 206.9298 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 6.6097 | 0.477 | 376.9944 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.7078 | 0.3736 | 273.632 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 4.7078 | 3.3819 | 3281.9144 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659199 [BASIN___-BE4230.00] TO BUS 659109 [BASIN___-BE7115.00] TO BUS 659200 [BAL.KY1A-BE913.800] CKT 1 | 26.5939 | 15.5282 | 15428.2485 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 3.9648 | 0.4915 | 391.5451 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 3.9648 | 0.4856 | 385.5565 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.7079 | 0.3069 | 206.9321 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 6.6096 | 0.477 | 376.9944 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.7079 | 0.3736 | 273.6345 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 4.7079 | 3.3829 | 3282.8728 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659233 [DGC_____-BE4230.00] TO BUS 659232 [DGC_____-BE913.800] CKT 1 | 26.5897 | 15.5305 | 15430.5142 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 3.9649 | 0.4915 | 391.5471 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 3.9649 | 0.4856 | 385.5581 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.708 | 0.3069 | 206.9335 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 6.6101 | 0.477 | 376.9949 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.708 | 0.3736 | 273.636 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 4.708 | 3.3832 | 3283.1957 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659214 [DGC5301B-BE913.800] TO BUS 659215 [DGC5302A-BE913.800] CKT 1 | 26.5829 | 15.5285 | 15428.4561 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 3.9649 | 0.4915 | 391.5491 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 3.9649 | 0.4856 | 385.56 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.708 | 0.3069 | 206.9349 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 6.6099 | 0.477 | 376.9955 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.708 | 0.3736 | 273.6376 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 4.708 | 3.3836 | 3283.6106 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659212 [DGC_____-BE3345.00] TO BUS 659220 [DGC5301A-BE913.800] TO BUS 659221 [DGC5302B-BE913.800] CKT 1 | 26.5738 | 15.5265 | 15426.5093 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 3.965 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.708 | 0.3069 | 206.9287 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.708 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 4.708 | 3.3817 | 3281.7143 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659219 [COTEAU 1-RR913.800] CKT 1 | 26.6133 | 15.5345 | 15434.5307 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 3.965 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.708 | 0.3069 | 206.9287 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.708 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 4.708 | 3.3817 | 3281.7147 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659218 [COTEAU__-RR3345.00] TO BUS 659222 [COTEAU_1-RR869.000] TO BUS 659231 [COTEAU 2-RR913.800] CKT 2 | 26.6133 | 15.5345 | 15434.5316 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9626 | 0.4915 | 391.5119 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9626 | 0.4855 | 385.5336 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3971 | 0.328 | 227.9504 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 6.611 | 0.477 | 376.993 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3971 | 0.4016 | 301.6424 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.3971 | 4.0226 | 3922.6293 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659247 [MEDORA__-UM4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 26.548 | 15.5408 | 15440.803 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 3.9638 | 0.4915 | 391.5102 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 3.9638 | 0.4855 | 385.5287 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.7068 | 0.3069 | 206.9213 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 6.612 | 0.477 | 376.9902 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.7068 | 0.3736 | 273.624 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 4.7068 | 3.3772 | 3277.2356 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659404 [BURKE___-PP3345.00] CKT 1 | 26.6189 | 15.5386 | 15438.5598 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5401 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.965 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7079 | 0.3069 | 206.9285 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 6.5811 | 0.4771 | 377.1046 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7079 | 0.3736 | 273.6305 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7079 | 3.3816 | 3281.6377 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 26.6075 | 15.5344 | 15434.4462 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 3.9154 | 0.492 | 392.0055 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 3.9154 | 0.486 | 386.0078 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.6989 | 0.3069 | 206.9171 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 6.6108 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.6989 | 0.3736 | 273.6254 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 4.6989 | 3.3694 | 3269.4017 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT Z | 26.487 | 15.5329 | 15432.9342 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 3.9637 | 0.4915 | 391.5137 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 3.9637 | 0.4855 | 385.5269 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.7066 | 0.3069 | 206.9184 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 6.6127 | 0.477 | 376.9887 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.7066 | 0.3736 | 273.621 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 4.7066 | 3.3773 | 3277.2715 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659479 [TRADEWND-UA3345.00] CKT 1 | 26.615 | 15.5468 | 15446.7878 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 3.9644 | 0.4916 | 391.5978 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 3.9644 | 0.4856 | 385.5918 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.7075 | 0.3069 | 206.9324 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 6.6107 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.7075 | 0.3736 | 273.634 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 4.7075 | 3.3856 | 3285.6052 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659336 [TANDE___-BE3345.00] TO BUS 659337 [TANDE___-BE4230.00] TO BUS 659338 [TND.KU3A-BE913.800] CKT 1 | 26.4569 | 15.5434 | 15443.4063 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 3.9488 | 0.4913 | 391.2771 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 3.9488 | 0.4853 | 385.3308 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.7015 | 0.3069 | 206.9338 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.993 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.7015 | 0.3736 | 273.6472 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 4.7015 | 3.3578 | 3257.7713 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 26.4791 | 15.5128 | 15412.8043 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 3.965 | 0.4916 | 391.6143 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 3.965 | 0.4856 | 385.6171 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.7091 | 0.307 | 206.9808 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 6.6086 | 0.477 | 376.9983 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.7091 | 0.3737 | 273.6879 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 4.7091 | 3.399 | 3299.0346 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 26.5472 | 15.5289 | 15428.874 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 3.9626 | 0.4915 | 391.5181 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 3.9626 | 0.4855 | 385.5349 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.7024 | 0.3069 | 206.9184 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 6.6104 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.7024 | 0.3736 | 273.6247 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 4.7024 | 3.3688 | 3268.7687 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659420 [AV.LS-BD-BE3345.00] TO BUS 659421 [BD.LS-AV-BE3345.00] CKT 1 | 26.2086 | 15.5099 | 15409.8944 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9634 | 0.4915 | 391.5354 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9634 | 0.4855 | 385.546 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7059 | 0.3069 | 206.9292 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 6.6106 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7059 | 0.3736 | 273.6317 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7059 | 3.3827 | 3282.6733 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 25.1294 | 15.5967 | 15496.6569 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 3.9634 | 0.4915 | 391.5361 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 3.9634 | 0.4855 | 385.5463 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.706 | 0.3069 | 206.9295 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 6.6106 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.706 | 0.3736 | 273.6319 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 4.706 | 3.3831 | 3283.0823 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659423 [GR.LS-LO-BE3345.00] TO BUS 659160 [GROTON__-BE3345.00] CKT Z | 25.1187 | 15.6023 | 15502.3481 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9633 | 0.4915 | 391.5335 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 3.9633 | 0.4855 | 385.545 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7063 | 0.3069 | 206.9277 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 6.6101 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7063 | 0.3736 | 273.6304 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 4.7063 | 3.3812 | 3281.1635 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT Z | 25.2204 | 15.572 | 15471.9896 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 3.9634 | 0.4915 | 391.5358 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 3.9634 | 0.4855 | 385.5464 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.7066 | 0.3069 | 206.9291 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 6.6102 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.7066 | 0.3736 | 273.6313 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 4.7066 | 3.3829 | 3282.9212 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 659130 [CHAPELLE-BE3345.00] CKT Z | 25.1745 | 15.5964 | 15496.3586 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.7081 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 6.2043 | 0.4786 | 378.6101 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.7081 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 4.7081 | 3.3819 | 3281.9337 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT Z1 | 26.6124 | 15.5352 | 15435.2058 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 3.9645 | 0.4915 | 391.5413 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 3.9645 | 0.4856 | 385.5536 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6903 | 0.3074 | 207.4355 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 6.6103 | 0.477 | 376.9937 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6903 | 0.3743 | 274.2619 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 4.6903 | 3.37 | 3269.9648 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT Z | 26.6079 | 15.5348 | 15434.8481 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 6.4216 | 0.4782 | 378.1986 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 4.708 | 3.3819 | 3281.8847 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659854 [K335AMAI-NI869.000] CKT 1 | 26.612 | 15.5351 | 15435.0593 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 3.965 | 0.4856 | 385.5523 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 6.4892 | 0.4778 | 377.7648 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 4.708 | 3.3819 | 3281.8821 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659862 [K307DENI-NI869.000] CKT 1 | 26.612 | 15.5351 | 15435.0593 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 6.4589 | 0.478 | 377.9717 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 4.708 | 3.3819 | 3281.8826 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659885 [K306SCHL-NI869.000] CKT 1 | 26.6121 | 15.5351 | 15435.0603 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 6.3721 | 0.4782 | 378.1996 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 4.708 | 3.3819 | 3281.8839 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659912 [J6BOYER_-NI869.000] TO BUS 659918 [J12_____-NI869.000] CKT 1 | 26.6121 | 15.5351 | 15435.0597 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 6.6478 | 0.4718 | 371.8151 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 3.3819 | 3281.894 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 26.612 | 15.5351 | 15435.093 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 6.6478 | 0.4718 | 371.8151 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 4.708 | 3.3819 | 3281.894 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760516 [G17-222-XFM134.500] TO BUS 760517 [G17-222-GSU134.500] CKT 1 | 26.612 | 15.5351 | 15435.0932 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 6.6491 | 0.4718 | 371.8346 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 4.708 | 3.3819 | 3281.894 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760515 [GEN-2017-222230.00] CKT 1 | 26.612 | 15.5351 | 15435.0931 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 6.6491 | 0.4718 | 371.8346 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 4.708 | 3.3819 | 3281.8938 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 760519 [G17-222-XFM234.500] TO BUS 760520 [G17-222-GSU234.500] CKT 1 | 26.612 | 15.5351 | 15435.0931 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 6.6072 | 0.477 | 377.0067 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 4.708 | 3.3819 | 3281.8885 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 & 2 | 26.6106 | 15.5349 | 15434.9441 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 5.2509 | 0.4863 | 386.3449 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.862 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652603 [EXIRA 5 161.00] CKT 1 | 26.6117 | 15.535 | 15435.0224 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 5.0267 | 0.4938 | 393.8019 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 4.708 | 3.3819 | 3281.869 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 & 2 | 26.6118 | 15.535 | 15435.0223 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 3.9629 | 0.4915 | 391.4966 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 3.9629 | 0.4855 | 385.5107 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6812 | 0.3069 | 206.9286 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 6.6109 | 0.477 | 376.9929 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6812 | 0.3736 | 273.6434 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 4.6812 | 3.3813 | 3281.3346 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 & 2 | 17.9408 | 15.7945 | 15694.5394 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.708 | 0.3069 | 206.9287 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 6.5794 | 0.4772 | 377.1657 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.708 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 4.708 | 3.3818 | 3281.7727 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 655484 [RASMUSN-ER4 230.00] CKT 1 | 26.6089 | 15.5348 | 15434.8097 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 3.965 | 0.4856 | 385.5523 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 6.3235 | 0.4788 | 378.8347 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 4.708 | 3.3819 | 3281.8813 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 656267 [MANNINGTAP 869.000] CKT 1 | 26.612 | 15.5351 | 15435.059 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 6.6115 | 0.477 | 376.9909 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 4.708 | 3.3819 | 3281.8838 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658030 [DENISONWEST869.000] CKT 1 | 26.6121 | 15.5351 | 15435.0611 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 6.6113 | 0.477 | 376.9899 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 3.3819 | 3281.8841 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 26.6121 | 15.5351 | 15435.0611 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 3.9652 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 3.9652 | 0.4856 | 385.5509 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.7082 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 6.6136 | 0.477 | 376.9865 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.7082 | 0.3736 | 273.6305 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 4.7082 | 3.3836 | 3283.5826 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 588211 [G16-130XFMR134.500] CKT 1 | 26.6662 | 15.5817 | 15481.6756 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 5.5302 | 0.486 | 385.9945 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 4.708 | 3.3819 | 3281.8802 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 659912 [J6BOYER_-NI869.000] CKT 1 | 26.6119 | 15.535 | 15435.0422 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 3.9649 | 0.4915 | 391.54 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 3.9649 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.708 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.708 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 4.708 | 3.3818 | 3281.7998 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 26.6086 | 15.5341 | 15434.0655 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 3.9649 | 0.4915 | 391.54 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 3.9649 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.708 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.708 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 4.708 | 3.3818 | 3281.7998 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655906 [FINSTAD -MW7115.00] TO BUS 659060 [FINSTAD345 345.00] CKT 2 | 26.6086 | 15.5341 | 15434.0655 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 3.3369 | 0.5009 | 400.9479 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 3.3369 | 0.4943 | 394.3408 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.7076 | 0.3069 | 206.928 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 6.6109 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.7076 | 0.3736 | 273.6301 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 4.7076 | 3.381 | 3280.9548 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655915 [BARRBUTE-MW7115.00] TO BUS 659145 [GRENORA_-UM7115.00] CKT 1 | 26.607 | 15.5346 | 15434.5756 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.7597 | 0.494 | 394.0009 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.7597 | 0.4879 | 387.9497 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.705 | 0.3069 | 206.9199 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.705 | 0.3736 | 273.6222 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.705 | 3.378 | 3278.0489 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655924 [STATELIN-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.5587 | 15.5386 | 15438.5762 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.5883 | 0.5003 | 400.3342 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.5883 | 0.4939 | 393.8511 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.7066 | 0.3069 | 206.9224 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.7066 | 0.3736 | 273.6245 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.7066 | 3.3793 | 3279.252 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 655933 [N.MISRDG-MW7115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.568 | 15.5408 | 15440.7638 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 6.6108 | 0.477 | 376.993 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 4.708 | 3.3819 | 3281.8839 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 658030 [DENISONWEST869.000] TO BUS 658031 [DENSOUMAIN8 69.000] CKT 1 | 26.6121 | 15.5351 | 15435.0613 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 3.9366 | 0.4917 | 391.7364 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 3.9366 | 0.4858 | 385.7504 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.7059 | 0.3069 | 206.9274 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.7059 | 0.3736 | 273.631 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 4.7059 | 3.3777 | 3277.6668 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659060 [FINSTAD345 345.00] TO BUS 659336 [TANDE___-BE3345.00] CKT 1 | 26.0631 | 15.5737 | 15473.686 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 3.9587 | 0.4915 | 391.499 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 3.9587 | 0.4855 | 385.5083 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6929 | 0.3069 | 206.9177 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 6.6164 | 0.477 | 376.9794 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6929 | 0.3736 | 273.6227 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 4.6929 | 3.3826 | 3282.5761 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 24.569 | 15.6644 | 15564.437 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 3.9587 | 0.4915 | 391.498 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 3.9587 | 0.4855 | 385.5072 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.693 | 0.3069 | 206.917 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 6.6164 | 0.477 | 376.9794 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.693 | 0.3736 | 273.6219 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 4.693 | 3.3826 | 3282.6157 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 24.5716 | 15.6664 | 15566.391 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.963 | 0.4915 | 391.5326 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 3.963 | 0.4855 | 385.5435 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7061 | 0.3069 | 206.9281 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 6.6107 | 0.477 | 376.9936 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7061 | 0.3736 | 273.6303 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 4.7061 | 3.3827 | 3282.7039 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 659106 [LELAND_O-BE4230.00] CKT 1 | 24.8815 | 15.6083 | 15508.2862 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 3.9547 | 0.4915 | 391.4678 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 3.9547 | 0.4855 | 385.4878 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6496 | 0.3069 | 206.9487 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6496 | 0.3737 | 273.6882 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 4.6496 | 3.3557 | 3255.7459 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 26.221 | 15.5057 | 15405.6749 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 4.708 | 3.3819 | 3281.8719 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 26.6122 | 15.535 | 15435.0266 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 4.708 | 3.3819 | 3281.8719 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 26.6122 | 15.535 | 15435.0266 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 3.9648 | 0.4915 | 391.5442 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 3.9648 | 0.4856 | 385.5564 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.7075 | 0.3069 | 206.9313 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 6.6101 | 0.477 | 376.9949 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.7075 | 0.3736 | 273.6343 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 4.7075 | 3.3805 | 3280.5202 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 26.6028 | 15.5204 | 15420.4427 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9461 | 0.4913 | 391.3081 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.9461 | 0.4853 | 385.3433 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6525 | 0.3069 | 206.8676 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6525 | 0.3736 | 273.5874 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6525 | 3.3599 | 3259.8578 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 26.0226 | 15.4906 | 15390.6206 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 3.9632 | 0.4915 | 391.5291 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 3.9632 | 0.4855 | 385.5412 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.7044 | 0.3069 | 206.927 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 6.6106 | 0.477 | 376.9923 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.7044 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 4.7044 | 3.38 | 3280.0305 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 26.1239 | 15.5477 | 15447.7333 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 3.9618 | 0.4915 | 391.5344 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 3.9618 | 0.4855 | 385.5458 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.7077 | 0.3069 | 206.9277 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.7077 | 0.3736 | 273.6304 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 4.7077 | 3.3796 | 3279.608 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659108 [LOGAN___-BE4230.00] CKT 1 | 26.2538 | 15.5177 | 15417.6689 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 3.9631 | 0.4915 | 391.5318 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 3.9631 | 0.4855 | 385.5423 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.7051 | 0.3069 | 206.927 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 6.6135 | 0.477 | 376.9865 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.7051 | 0.3736 | 273.629 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 4.7051 | 3.3835 | 3283.4776 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659110 [LELAND_1-BEG22.000] CKT 1 | 25.1512 | 15.6149 | 15514.8528 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 3.9644 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 3.9644 | 0.4856 | 385.5519 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.7071 | 0.3069 | 206.9294 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 6.6115 | 0.477 | 376.9912 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.7071 | 0.3736 | 273.6316 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 4.7071 | 3.3822 | 3282.238 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659106 [LELAND_O-BE4230.00] TO BUS 659199 [BASIN___-BE4230.00] CKT 1 | 26.2096 | 15.544 | 15443.9504 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.964 | 0.4915 | 391.5484 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 3.964 | 0.4856 | 385.5618 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6575 | 0.3071 | 207.1093 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6575 | 0.3739 | 273.8647 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 4.6575 | 3.4026 | 3302.5581 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 26.5167 | 15.5375 | 15437.5061 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7081 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 6.5534 | 0.4773 | 377.3013 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7081 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 4.7081 | 3.3819 | 3281.9166 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 652565 [SIOUXCY4 230.00] CKT 1 | 26.6118 | 15.5351 | 15435.0925 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 3.9631 | 0.4915 | 391.5304 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 3.9631 | 0.4855 | 385.543 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.7053 | 0.3069 | 206.9263 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 6.6106 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.7053 | 0.3736 | 273.6297 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 4.7053 | 3.379 | 3278.9727 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659422 [LO.LS-GR-BE3345.00] TO BUS 659423 [GR.LS-LO-BE3345.00] CKT 1 | 25.226 | 15.5456 | 15445.615 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 3.9631 | 0.4915 | 391.5297 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 3.9631 | 0.4855 | 385.5428 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.7059 | 0.3069 | 206.9256 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 6.6101 | 0.477 | 376.9935 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.7059 | 0.3736 | 273.629 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 4.7059 | 3.3784 | 3278.3608 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT 1 | 25.2915 | 15.5344 | 15434.3619 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 3.9645 | 0.4915 | 391.5413 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 3.9645 | 0.4856 | 385.5536 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6903 | 0.3074 | 207.4355 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 6.6103 | 0.477 | 376.9937 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6903 | 0.3743 | 274.2619 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 4.6903 | 3.37 | 3269.9648 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 659535 [BEAVRHIL-GW4230.00] TO BUS 659536 [BEAVRHIL-GW7115.00] TO BUS 659537 [BEAVRHIL-GW913.200] CKT 1 | 26.6079 | 15.5348 | 15434.848 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9651 | 0.4915 | 391.5395 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 3.9651 | 0.4856 | 385.5505 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7081 | 0.3069 | 206.9285 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 6.6136 | 0.477 | 376.9865 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7081 | 0.3736 | 273.6303 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 4.7081 | 3.3831 | 3283.1189 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588210 [GEN-2016-130345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 26.6772 | 15.5753 | 15475.3279 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 3.9652 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 3.9652 | 0.4856 | 385.5509 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.7082 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 6.6136 | 0.477 | 376.9865 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.7082 | 0.3736 | 273.6305 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 4.7082 | 3.3836 | 3283.5826 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 588211 [G16-130XFMR134.500] TO BUS 588212 [G16-130-GSU134.500] CKT 1 | 26.6662 | 15.5817 | 15481.6756 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 3.9647 | 0.4915 | 391.5401 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 3.9647 | 0.4856 | 385.5518 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.7072 | 0.3069 | 206.9294 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 6.6107 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.7072 | 0.3736 | 273.6317 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 4.7072 | 3.3817 | 3281.692 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615600 [GRE-COAL CR4230.00] CKT 1 | 26.5129 | 15.5374 | 15437.3989 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 3.9649 | 0.4915 | 391.5402 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 3.9649 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.7076 | 0.3069 | 206.9293 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.7076 | 0.3736 | 273.6314 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 4.7076 | 3.3817 | 3281.7055 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 615900 [GRE-COAL TP4230.00] CKT 1 | 26.5531 | 15.5366 | 15436.6197 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 3.9647 | 0.4915 | 391.5353 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 3.9647 | 0.4855 | 385.5482 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.7062 | 0.3069 | 206.9274 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 6.6109 | 0.477 | 376.9929 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.7062 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 4.7062 | 3.3775 | 3277.5107 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 615901 [GRE-STANTON4230.00] TO BUS 657756 [SQBUTTE4 230.00] CKT 1 | 26.4999 | 15.5415 | 15441.4801 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 6.583 | 0.4771 | 377.0968 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 4.708 | 3.3819 | 3281.8888 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 26.6119 | 15.5351 | 15435.0672 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 6.6081 | 0.477 | 377.015 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 4.708 | 3.3819 | 3281.8865 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643155 [TWIN CH T4 913.800] CKT 1 | 26.6121 | 15.5351 | 15435.0644 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9655 | 0.4916 | 391.5555 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9655 | 0.4856 | 385.5648 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9749 | 0.3115 | 211.5148 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 6.6108 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9749 | 0.3796 | 279.6479 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 3.9749 | 3.468 | 3368.0159 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652211 [DAWSONC9 13.200] TO BUS 652403 [DAWSONC4 230.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 26.597 | 15.5357 | 15435.7234 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 6.6093 | 0.477 | 377.0038 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 4.708 | 3.3819 | 3281.8843 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 640386 [TWIN CH4 230.00] TO BUS 640387 [TWIN CH7 115.00] TO BUS 643156 [TWIN CH T6 913.800] CKT 2 | 26.612 | 15.5351 | 15435.0632 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 3.8979 | 0.4926 | 392.5766 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 3.8979 | 0.4866 | 386.5671 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.7032 | 0.307 | 206.9571 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 6.6107 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.7032 | 0.3737 | 273.6694 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 4.7032 | 3.3771 | 3277.0603 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 26.586 | 15.5361 | 15436.1469 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 3.9619 | 0.4915 | 391.5243 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 3.9619 | 0.4855 | 385.5422 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.7074 | 0.3069 | 206.937 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 6.6107 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.7074 | 0.3736 | 273.64 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 4.7074 | 3.385 | 3285.0159 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 26.6029 | 15.5388 | 15438.7924 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 3.9465 | 0.4922 | 392.2051 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 3.9465 | 0.4862 | 386.2013 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.707 | 0.3069 | 206.9356 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 6.6107 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.707 | 0.3736 | 273.6397 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 4.707 | 3.3812 | 3281.2375 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 26.6024 | 15.5356 | 15435.6368 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 3.9113 | 0.4924 | 392.3807 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 3.9113 | 0.4863 | 386.3298 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.7097 | 0.3069 | 206.9323 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 6.6107 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.7097 | 0.3736 | 273.6325 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 4.7097 | 3.3876 | 3287.5569 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 26.577 | 15.5393 | 15439.2843 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9681 | 0.4916 | 391.5627 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 3.9681 | 0.4856 | 385.5619 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5889 | 0.3307 | 230.7449 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5889 | 0.4049 | 304.948 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 2.5889 | 3.2408 | 3140.7664 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652616 [MINGUSVILLE4230.00] CKT 1 | 26.5349 | 15.5354 | 15435.3603 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 3.9633 | 0.4916 | 391.5582 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 3.9633 | 0.4856 | 385.5683 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3691 | 0.3082 | 208.2309 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3691 | 0.3754 | 275.3875 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 4.3691 | 3.4681 | 3368.1002 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652200 [GLENDIVE7 115.00] CKT 1 | 26.5942 | 15.5365 | 15436.4651 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 3.9648 | 0.4915 | 391.5405 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 3.9648 | 0.4856 | 385.5531 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.7117 | 0.3069 | 206.9389 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.7117 | 0.3736 | 273.6491 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 4.7117 | 3.3597 | 3259.6559 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652212 [GLENDIVEP2T7115.00] CKT 1 | 26.6133 | 15.5349 | 15434.9253 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 3.9649 | 0.4916 | 391.5506 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 3.9649 | 0.4856 | 385.5618 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6759 | 0.3071 | 207.095 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6759 | 0.3739 | 273.8512 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 4.6759 | 3.3731 | 3273.1019 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 652401 [CIRCLE 7 115.00] CKT 1 | 26.6115 | 15.535 | 15435.0295 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 3.9631 | 0.4916 | 391.6413 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 3.9631 | 0.4856 | 385.6468 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.4324 | 0.3082 | 208.1582 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.4324 | 0.3753 | 275.255 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 4.4324 | 3.4289 | 3328.9393 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652404 [DAWSONC7 115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 26.6142 | 15.5349 | 15434.8712 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 6.597 | 0.4771 | 377.0963 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.8716 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652308 [SIOUXC39 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 26.6117 | 15.535 | 15435.0443 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 3.9644 | 0.4916 | 391.58 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 3.9644 | 0.4856 | 385.5852 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.669 | 0.3072 | 207.1674 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.669 | 0.3739 | 273.9464 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 4.669 | 3.3649 | 3264.8712 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652406 [FTPECK 7 115.00] CKT 1 | 26.6117 | 15.535 | 15435.0498 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 3.9651 | 0.4915 | 391.5498 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 3.9651 | 0.4856 | 385.5573 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.6031 | 0.3072 | 207.1814 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 6.6113 | 0.477 | 376.9918 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.6031 | 0.374 | 273.9758 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 4.6031 | 3.4273 | 3327.2627 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652414 [FTPECK4G 13.800] CKT 1 | 26.6044 | 15.5363 | 15436.2814 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 3.9651 | 0.4915 | 391.5499 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 3.9651 | 0.4856 | 385.5572 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.6035 | 0.3072 | 207.1758 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 6.6113 | 0.477 | 376.9917 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.6035 | 0.374 | 273.9688 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 4.6035 | 3.4276 | 3327.633 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652405 [FTPECK 4 230.00] TO BUS 652415 [FTPECK5G 13.800] CKT 1 | 26.6045 | 15.5363 | 15436.291 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 3.9657 | 0.4915 | 391.5414 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 3.9657 | 0.4856 | 385.5506 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5442 | 0.3064 | 206.3594 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5442 | 0.373 | 273.0221 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 4.5442 | 3.4868 | 3386.7665 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 661004 [BAKER 4 230.00] CKT 1 | 26.6087 | 15.534 | 15433.9731 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 3.965 | 0.4915 | 391.5409 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 3.965 | 0.4856 | 385.5529 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.7094 | 0.3069 | 206.9221 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.7094 | 0.3736 | 273.6245 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 4.7094 | 3.3738 | 3273.8097 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652411 [MI CTYE4 230.00] TO BUS 652412 [MI CTYE7 115.00] TO BUS 652217 [MI CTYE9 13.800] CKT 1 | 26.6119 | 15.535 | 15435.0179 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 3.9596 | 0.4915 | 391.5386 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 3.9596 | 0.4855 | 385.5477 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4479 | 0.308 | 207.9895 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4479 | 0.375 | 275.0287 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 4.4479 | 3.4137 | 3313.6744 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659124 [DICKINSN-BE4230.00] CKT 1 | 26.5224 | 15.5426 | 15442.5925 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 3.9649 | 0.4915 | 391.5443 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 3.9649 | 0.4856 | 385.5558 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.7069 | 0.307 | 206.9742 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 6.6102 | 0.477 | 376.9938 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.7069 | 0.3737 | 273.6854 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 4.7069 | 3.3852 | 3285.1645 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659309 [S.HEART_-RR4230.00] CKT Z | 26.6069 | 15.5349 | 15434.8606 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 3.9638 | 0.4915 | 391.5305 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 3.9638 | 0.4855 | 385.5426 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.7259 | 0.3072 | 207.1573 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.7259 | 0.3739 | 273.9208 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 4.7259 | 3.3694 | 3269.4259 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 659448 [DAGLUM__-BE4230.00] CKT 1 | 26.5581 | 15.545 | 15445.0054 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 3.9644 | 0.4915 | 391.545 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 3.9644 | 0.4856 | 385.5548 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.6199 | 0.3073 | 207.2905 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.6199 | 0.3741 | 274.0856 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 4.6199 | 3.4503 | 3350.3051 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 26.5781 | 15.5399 | 15439.8644 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 3.9636 | 0.4915 | 391.5407 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 3.9636 | 0.4856 | 385.5523 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5738 | 0.3074 | 207.4029 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5738 | 0.3743 | 274.2538 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 4.5738 | 3.4136 | 3313.6051 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652425 [BELFELD4 230.00] TO BUS 652424 [BELFELD3 345.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 26.5652 | 15.5383 | 15438.3459 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 6.5969 | 0.4771 | 377.0969 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.8715 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652310 [SIOUXC49 13.800] TO BUS 652565 [SIOUXCY4 230.00] TO BUS 652566 [SIOUXCY5 161.00] CKT 1 | 26.6117 | 15.535 | 15435.0442 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 3.9646 | 0.4915 | 391.5372 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 3.9646 | 0.4856 | 385.55 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.7068 | 0.3069 | 206.9259 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 6.6106 | 0.477 | 376.9936 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.7068 | 0.3736 | 273.6291 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 4.7068 | 3.3776 | 3277.6083 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652444 [JAMESTN4 230.00] CKT 1 | 26.523 | 15.5231 | 15423.0631 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 3.9646 | 0.4915 | 391.54 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 3.9646 | 0.4856 | 385.5513 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.7075 | 0.3069 | 206.9296 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 6.6121 | 0.477 | 376.9899 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.7075 | 0.3736 | 273.6314 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 4.7075 | 3.3833 | 3283.3437 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652457 [GARISN1G 13.800] CKT 1 | 26.4453 | 15.5474 | 15447.4389 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 3.9646 | 0.4915 | 391.54 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 3.9646 | 0.4856 | 385.5513 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.7075 | 0.3069 | 206.9296 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 6.6121 | 0.477 | 376.9899 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.7075 | 0.3736 | 273.6314 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 4.7075 | 3.3833 | 3283.3436 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652458 [GARISN2G 13.800] CKT 1 | 26.4454 | 15.5474 | 15447.4356 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 3.9646 | 0.4915 | 391.54 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 3.9646 | 0.4856 | 385.5513 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.7075 | 0.3069 | 206.9296 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 6.6121 | 0.477 | 376.9899 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.7075 | 0.3736 | 273.6314 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 4.7075 | 3.3833 | 3283.3433 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652459 [GARISN3G 13.800] CKT 1 | 26.4454 | 15.5474 | 15447.4333 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 3.9649 | 0.4915 | 391.5401 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 3.9649 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.7077 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 6.6108 | 0.477 | 376.9931 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.7077 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 4.7077 | 3.3817 | 3281.7387 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652466 [HILKEN 4 230.00] CKT 1 | 26.5674 | 15.5318 | 15431.8236 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 3.9647 | 0.4915 | 391.5388 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 3.9647 | 0.4856 | 385.5504 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.708 | 0.3069 | 206.9293 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 6.6107 | 0.477 | 376.9933 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.708 | 0.3736 | 273.6314 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 4.708 | 3.3821 | 3282.1072 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652441 [GARRISN4 230.00] TO BUS 652442 [GARRISN7 115.00] TO BUS 652642 [GARRISON 9 13.800] CKT 1 | 26.5164 | 15.5314 | 15431.377 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 3.9649 | 0.4915 | 391.541 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 3.9649 | 0.4856 | 385.5526 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.708 | 0.3069 | 206.9292 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 6.6105 | 0.477 | 376.9936 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.708 | 0.3736 | 273.6312 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 4.708 | 3.382 | 3281.9666 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652325 [WASHBRN9 41.800] CKT 1 | 26.6074 | 15.5342 | 15434.1961 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 3.9639 | 0.4915 | 391.5397 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 3.9639 | 0.4856 | 385.5509 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.7081 | 0.3069 | 206.9285 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 6.6107 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.7081 | 0.3736 | 273.6304 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 4.7081 | 3.3818 | 3281.835 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652456 [WASHBRN4 230.00] TO BUS 652426 [BISMARK4 230.00] CKT 1 | 25.4831 | 15.5566 | 15456.639 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 3.965 | 0.4915 | 391.5401 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 3.965 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.7079 | 0.3069 | 206.9286 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 6.606 | 0.477 | 377.0085 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.7079 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 4.7079 | 3.3817 | 3281.7113 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 640540 [MEADOWGROVE4230.00] CKT 1 | 26.6065 | 15.5346 | 15434.5749 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 3.9649 | 0.4915 | 391.5399 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 3.9649 | 0.4856 | 385.5518 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.7077 | 0.3069 | 206.9286 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 6.6097 | 0.477 | 376.9958 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.7077 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 4.7077 | 3.3816 | 3281.6235 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652507 [FTTHOMP4 230.00] CKT 1 | 26.5918 | 15.5344 | 15434.4392 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.6213 | 0.4983 | 398.3453 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 3.6213 | 0.492 | 392.0319 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.707 | 0.3069 | 206.9358 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 6.6108 | 0.477 | 376.9932 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.707 | 0.3736 | 273.6395 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 4.707 | 3.3839 | 3283.9223 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 26.6033 | 15.5375 | 15437.5249 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 6.6103 | 0.477 | 376.9958 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 4.708 | 3.3819 | 3281.8759 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 1 | 26.6119 | 15.535 | 15435.04 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 6.6103 | 0.477 | 376.9958 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 4.708 | 3.3819 | 3281.8759 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652510 [FTRANDL7 115.00] CKT 2 | 26.6119 | 15.535 | 15435.04 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5401 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 3.965 | 0.4856 | 385.552 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.7079 | 0.3069 | 206.9286 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 6.6036 | 0.477 | 377.005 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.7079 | 0.3736 | 273.6306 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 4.7079 | 3.3817 | 3281.6683 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652526 [UTICAJC4 230.00] CKT 1 | 26.6089 | 15.5345 | 15434.4937 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.708 | 0.3069 | 206.929 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 6.6111 | 0.477 | 376.9891 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 4.708 | 3.382 | 3282.0329 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652547 [FTRDL34G 13.800] CKT 1 | 26.6095 | 15.5356 | 15435.5765 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.708 | 0.3069 | 206.929 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 6.6111 | 0.477 | 376.9891 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6309 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 4.708 | 3.382 | 3282.0332 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652548 [FTRDL56G 13.800] CKT 1 | 26.6095 | 15.5356 | 15435.5772 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5405 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.708 | 0.3069 | 206.9289 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 6.6108 | 0.477 | 376.9913 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 4.708 | 3.382 | 3281.9605 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 652549 [FTRDL78G 13.800] CKT 1 | 26.6106 | 15.5353 | 15435.335 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 3.9649 | 0.4915 | 391.5399 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 3.9649 | 0.4856 | 385.5519 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.7078 | 0.3069 | 206.9286 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 6.6094 | 0.477 | 376.9976 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.7078 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 4.7078 | 3.3817 | 3281.6684 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652509 [FTRANDL4 230.00] TO BUS 655475 [LAKPLAT-ER4 230.00] CKT 1 | 26.5919 | 15.5346 | 15434.6223 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 6.5724 | 0.4772 | 377.2344 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.708 | 0.3736 | 273.6307 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 4.708 | 3.3819 | 3281.8823 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 659900 [EAGLE___-NI4230.00] CKT 1 | 26.6108 | 15.5351 | 15435.136 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 6.5405 | 0.4773 | 377.2689 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 4.708 | 3.3819 | 3281.8986 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652304 [SIOUXC19 13.800] CKT 1 | 26.6121 | 15.5351 | 15435.1074 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 6.5421 | 0.4773 | 377.2636 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 4.708 | 3.3819 | 3281.8982 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652552 [SIOUXCY2 230.00] TO BUS 652564 [SIOUXCY3 345.00] TO BUS 652305 [SIOUXC29 13.800] CKT 1 | 26.6121 | 15.5351 | 15435.1062 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 3.9633 | 0.4915 | 391.5258 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 3.9633 | 0.4855 | 385.5461 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.3939 | 0.3079 | 207.9073 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 6.6109 | 0.477 | 376.993 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.3939 | 0.375 | 274.9734 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 4.3939 | 3.4276 | 3327.5585 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652405 [FTPECK 4 230.00] CKT 1 | 26.6022 | 15.5359 | 15435.8545 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 5.2509 | 0.4863 | 386.345 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 4.708 | 3.3819 | 3281.8617 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652561 [DENISON5 161.00] TO BUS 652567 [DENISON4 230.00] TO BUS 652657 [DENISON 9 13.800] CKT 1 | 26.6117 | 15.535 | 15435.0224 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.1018 | 0.5048 | 404.7537 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 3.3819 | 3281.884 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652565 [SIOUXCY4 230.00] TO BUS 652567 [DENISON4 230.00] CKT 1 | 26.6114 | 15.5351 | 15435.0818 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 6.5771 | 0.4772 | 377.2124 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.8639 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 635223 [PLYMOTH5 161.00] CKT 1 | 26.6111 | 15.535 | 15435.0329 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 6.5994 | 0.477 | 377.0385 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.8796 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652563 [SPENCER5 161.00] CKT 1 | 26.612 | 15.5351 | 15435.0634 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 6.6107 | 0.477 | 376.9926 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 4.708 | 3.3819 | 3281.8827 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652566 [SIOUXCY5 161.00] TO BUS 652574 [SIOUXCY8 69.000] CKT 1 | 26.6121 | 15.5351 | 15435.0576 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 6.3499 | 0.4799 | 379.9376 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 4.708 | 3.3819 | 3281.8812 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 1 | 26.612 | 15.5351 | 15435.0553 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 6.3465 | 0.48 | 379.9781 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 4.708 | 3.3819 | 3281.8812 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652583 [DENISON8 69.000] TO BUS 652567 [DENISON4 230.00] CKT 2 | 26.612 | 15.5351 | 15435.0552 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 3.965 | 0.4856 | 385.5522 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 5.2408 | 0.4864 | 386.4278 | 72 | 88.9 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 4.708 | 3.3819 | 3281.8619 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 631069 [ANTA TP5 161.00] CKT 1 | 26.6117 | 15.535 | 15435.0241 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 6.6108 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 4.708 | 3.3819 | 3281.8839 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658000 [EXIRA 1G 13.800] CKT 1 | 26.6121 | 15.5351 | 15435.0613 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 3.965 | 0.4915 | 391.5404 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 3.965 | 0.4856 | 385.5521 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.708 | 0.3069 | 206.9288 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 6.6108 | 0.477 | 376.9934 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.708 | 0.3736 | 273.6308 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 4.708 | 3.3819 | 3281.884 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652603 [EXIRA 5 161.00] TO BUS 658001 [EXIRA 2G 13.800] CKT 1 | 26.6121 | 15.5351 | 15435.0613 | 150 | 167.2 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 3.964 | 0.4915 | 391.5374 | 128.89 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-067 | 115kV Strandahl sub | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 3.964 | 0.4856 | 385.5541 | 126.11 | 140.85 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-069 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.5184 | 0.3095 | 209.4884 | 125 | 144 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2018-074 | Denison 230kV Substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 6.611 | 0.477 | 376.9927 | 72 | 88.9 | PASS | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.5184 | 0.3769 | 276.9398 | 77.06 | 122.07 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-023 | WAPA-UGP Mingusville 230kV | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 4.5184 | 3.2196 | 3119.5592 | 32.94 | 52.25 | FAIL | PASS
01 NORTH | 25WP | TC | GEN-2019-037 | Leland Olds 345kV substation | OPEN LINE FROM BUS 652403 [DAWSONC4 230.00] TO BUS 652411 [MI CTYE4 230.00] CKT 1 | 26.6204 | 15.5338 | 15433.8414 | 150 | 167.2 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | Base | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | Base | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | Base | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | Base | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | Base | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | Base | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | Base | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | Base | 9.2806 | 0.1711 | 71.0952 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | Base | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | Base | 10.7743 | 6.6989 | 6598.9461 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 18.1008 | 0.3174 | 217.3602 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.239 | 0.1889 | 88.8541 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.239 | 0.2209 | 120.858 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 9.2801 | 0.1711 | 71.0993 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 38.3641 | 0.619 | 519.0278 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.7738 | 6.6992 | 6599.1714 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 18.1008 | 0.3174 | 217.3601 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.239 | 0.1889 | 88.8542 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.239 | 0.2209 | 120.858 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 9.2801 | 0.1711 | 71.0994 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 38.364 | 0.619 | 519.0278 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.7738 | 6.6992 | 6599.1764 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 18.1072 | 0.3174 | 217.357 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.2393 | 0.1889 | 88.8526 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.2393 | 0.2209 | 120.8558 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 9.2805 | 0.1711 | 71.0972 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 38.3651 | 0.619 | 519.0289 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.7742 | 6.699 | 6598.9881 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-065 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.2273 | 3.0942 | 2994.2332 | 19.8 | 22.67 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.2273 | 0.3558 | 255.7537 | 151.2 | 170 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.2273 | 0.3558 | 255.7537 | 151.2 | 170 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.2917 | 0.2617 | 161.6985 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.2917 | 0.2617 | 161.6985 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 18.1001 | 0.3174 | 217.3533 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 2.384 | 0.2374 | 137.4414 | 221.4 | 251.1 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 2.384 | 0.287 | 186.9667 | 201.6 | 226.8 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 9.2445 | 0.1722 | 72.2347 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 38.3428 | 0.619 | 519.0249 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.2917 | 6.7118 | 6611.7826 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.2473 | 0.3023 | 202.2886 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.2473 | 0.3023 | 202.2886 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7977 | 0.2736 | 173.5595 | 125 | 141 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7977 | 0.2736 | 173.5595 | 125 | 141 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 18.0737 | 0.3174 | 217.3625 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.2093 | 0.186 | 86.0216 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.2093 | 0.2172 | 117.2418 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.9596 | 0.172 | 71.9631 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 37.8372 | 0.6189 | 518.9148 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7977 | 7.3384 | 7238.3627 | 100 | 113.4 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7977 | 4.0773 | 3977.2799 | 50 | 58.8 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7977 | 7.3384 | 7238.3627 | 100 | 113.4 | FAIL | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 12.4275 | 0.2994 | 199.356 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 12.4275 | 0.2994 | 199.356 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.7336 | 0.2613 | 161.3151 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.7336 | 0.2613 | 161.3151 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 18.1031 | 0.3174 | 217.3525 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.2035 | 0.1884 | 88.416 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.2035 | 0.2203 | 120.2636 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 9.2757 | 0.1711 | 71.1262 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 38.3528 | 0.619 | 519.0326 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.7336 | 6.6958 | 6595.8117 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 11.8078 | 0.2997 | 199.7397 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 11.8078 | 0.2997 | 199.7397 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 10.1126 | 0.2616 | 161.5617 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 10.1126 | 0.2616 | 161.5617 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 18.1054 | 0.3174 | 217.3502 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.6337 | 0.1891 | 89.1199 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.6337 | 0.2213 | 121.2778 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.2446 | 0.1711 | 71.1436 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 38.3261 | 0.619 | 519.0161 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 10.1126 | 6.7164 | 6616.4275 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 12.4667 | 0.2992 | 199.1911 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 12.4667 | 0.2992 | 199.1911 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.7771 | 0.2612 | 161.2246 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.7771 | 0.2612 | 161.2246 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 18.1084 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.2402 | 0.1889 | 88.9245 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.2402 | 0.221 | 120.954 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 9.2767 | 0.1711 | 71.0886 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 38.3656 | 0.619 | 519.0275 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.7771 | 6.701 | 6601.0181 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 12.343 | 0.2994 | 199.3622 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 12.343 | 0.2994 | 199.3622 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.6395 | 0.2613 | 161.3252 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.6395 | 0.2613 | 161.3252 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 18.1083 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.123 | 0.1887 | 88.7398 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.123 | 0.2207 | 120.7138 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 9.2705 | 0.1711 | 71.0881 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 38.3554 | 0.619 | 519.0276 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.6395 | 6.6991 | 6599.1379 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 12.4668 | 0.2992 | 199.1898 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 12.4668 | 0.2992 | 199.1898 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.7742 | 0.2612 | 161.2325 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.7742 | 0.2612 | 161.2325 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.2415 | 0.1889 | 88.8996 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.2415 | 0.2209 | 120.92 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 9.2783 | 0.1711 | 71.0902 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 38.3662 | 0.619 | 519.0284 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.7742 | 6.7001 | 6600.1149 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4647 | 0.2992 | 199.2013 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4647 | 0.2992 | 199.2013 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7681 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7681 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.105 | 0.3174 | 217.3506 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2364 | 0.1889 | 88.8576 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2364 | 0.2209 | 120.8629 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.277 | 0.1711 | 71.1081 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 37.1896 | 0.619 | 518.9616 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7681 | 6.6996 | 6599.6045 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 12.4673 | 0.2992 | 199.2037 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 12.4673 | 0.2992 | 199.2037 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.7713 | 0.2612 | 161.2316 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.7713 | 0.2612 | 161.2316 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 18.1083 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.2377 | 0.1889 | 88.8795 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.2377 | 0.2209 | 120.8929 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 9.2712 | 0.1711 | 71.1479 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 38.3655 | 0.619 | 519.0273 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.7713 | 6.7014 | 6601.4103 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 12.332 | 0.2994 | 199.3724 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 12.332 | 0.2994 | 199.3724 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.6538 | 0.2613 | 161.314 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.6538 | 0.2613 | 161.314 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 18.1075 | 0.3174 | 217.3503 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.1178 | 0.1889 | 88.8898 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.1178 | 0.2209 | 120.9194 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 9.2757 | 0.1711 | 71.1148 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 38.3615 | 0.619 | 519.0288 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.6538 | 6.706 | 6606.0155 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 12.4692 | 0.2992 | 199.1991 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 12.4692 | 0.2992 | 199.1991 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.7755 | 0.2612 | 161.2257 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.7755 | 0.2612 | 161.2257 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 18.1083 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.2406 | 0.1889 | 88.9071 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.2406 | 0.2209 | 120.9309 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 9.2802 | 0.1711 | 71.105 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 38.3655 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.7755 | 6.7008 | 6600.8403 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 12.4699 | 0.2992 | 199.199 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 12.4699 | 0.2992 | 199.199 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.7761 | 0.2612 | 161.2257 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.7761 | 0.2612 | 161.2257 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 18.1084 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.2412 | 0.1889 | 88.9082 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.2412 | 0.2209 | 120.9318 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 9.2804 | 0.1711 | 71.1052 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 38.3659 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.7761 | 6.7009 | 6600.8729 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 12.4667 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 12.4667 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.7724 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.7724 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 18.1044 | 0.3174 | 217.3518 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.2383 | 0.1889 | 88.8559 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.2383 | 0.2209 | 120.8604 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 9.2798 | 0.1711 | 71.0971 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 38.2873 | 0.619 | 519.033 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.7724 | 6.699 | 6599.0355 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 12.4677 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 12.4677 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.774 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.774 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 18.1074 | 0.3174 | 217.3506 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.2392 | 0.1889 | 88.8542 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.2392 | 0.2209 | 120.8581 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 9.2803 | 0.1711 | 71.0984 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 38.2085 | 0.6191 | 519.0913 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.774 | 6.699 | 6599.0018 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.7741 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.7741 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 18.1083 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.2392 | 0.1889 | 88.8538 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.2392 | 0.2209 | 120.8575 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 9.2803 | 0.1711 | 71.0993 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 38.3612 | 0.619 | 519.0239 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.7741 | 6.6992 | 6599.1507 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 12.4661 | 0.2992 | 199.2019 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 12.4661 | 0.2992 | 199.2019 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.772 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.772 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 17.8001 | 0.3176 | 217.6272 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.2379 | 0.1888 | 88.8462 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.2379 | 0.2208 | 120.8471 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 9.2798 | 0.1711 | 71.0943 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 38.3565 | 0.619 | 519.0252 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.772 | 6.6998 | 6599.7988 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 18.0564 | 0.3174 | 217.4471 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.2393 | 0.1889 | 88.8524 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.2393 | 0.2209 | 120.8555 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 9.2805 | 0.1711 | 71.0957 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 38.3643 | 0.619 | 519.0293 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.7742 | 6.699 | 6598.9833 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.4686 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.4686 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7731 | 0.2612 | 161.229 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7731 | 0.2612 | 161.229 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 17.719 | 0.3176 | 217.5577 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.2399 | 0.1889 | 88.9187 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.2399 | 0.2209 | 120.9464 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 9.269 | 0.1713 | 71.2994 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 37.2866 | 0.6188 | 518.848 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7731 | 6.7066 | 6606.6363 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4657 | 0.2992 | 199.2015 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4657 | 0.2992 | 199.2015 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7702 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7702 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.1063 | 0.3174 | 217.3506 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2374 | 0.1889 | 88.8517 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2374 | 0.2209 | 120.8547 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.2785 | 0.1711 | 71.0955 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 37.5708 | 0.6191 | 519.1325 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7702 | 6.699 | 6598.995 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.46 | 0.2992 | 199.2063 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.46 | 0.2992 | 199.2063 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.7536 | 0.2612 | 161.2396 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.7536 | 0.2612 | 161.2396 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 17.8167 | 0.3175 | 217.4809 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.2318 | 0.189 | 88.9812 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.2318 | 0.221 | 121.0328 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 9.2663 | 0.1714 | 71.4086 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 37.1672 | 0.6187 | 518.6994 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.7536 | 6.7141 | 6614.1152 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 12.3728 | 0.2993 | 199.2674 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 12.3728 | 0.2993 | 199.2674 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.5718 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.5718 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 18.0892 | 0.3174 | 217.3628 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.1517 | 0.1888 | 88.8148 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.1517 | 0.2208 | 120.8114 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.233 | 0.1711 | 71.0748 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 37.5639 | 0.619 | 519.0479 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.5718 | 6.6987 | 6598.6694 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 12.4665 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 12.4665 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.7701 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.7701 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 18.046 | 0.3174 | 217.3816 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.2381 | 0.1889 | 88.8869 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.2381 | 0.2209 | 120.9028 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 9.2755 | 0.1712 | 71.1546 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 36.3887 | 0.6189 | 518.8556 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.7701 | 6.7021 | 6602.1046 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 18.108 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2392 | 0.1889 | 88.8507 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2392 | 0.2209 | 120.8532 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.2806 | 0.1711 | 71.0949 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 36.6806 | 0.6192 | 519.1857 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 6.6988 | 6598.845 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 18.108 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.2392 | 0.1889 | 88.8507 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.2392 | 0.2209 | 120.8532 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 9.2806 | 0.1711 | 71.0949 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 36.6806 | 0.6192 | 519.1857 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.774 | 6.6988 | 6598.845 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 12.4663 | 0.2992 | 199.1992 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 12.4663 | 0.2992 | 199.1992 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.7671 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.7671 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 17.5907 | 0.3178 | 217.8111 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.2375 | 0.189 | 89.0317 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.2375 | 0.2211 | 121.1011 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 9.2651 | 0.1715 | 71.5404 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 38.2761 | 0.619 | 519.0217 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.7671 | 6.7157 | 6615.7408 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.4676 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.4676 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.7741 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.7741 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 18.0915 | 0.3174 | 217.3862 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.2391 | 0.1889 | 88.8515 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.2391 | 0.2209 | 120.8543 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 9.2803 | 0.1711 | 71.0941 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 38.3661 | 0.619 | 519.0278 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.7741 | 6.6989 | 6598.9432 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.4267 | 0.2992 | 199.2384 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.4267 | 0.2992 | 199.2384 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7036 | 0.2613 | 161.275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7036 | 0.2613 | 161.275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 18.1037 | 0.3174 | 217.3512 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.2024 | 0.1889 | 88.9425 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.2024 | 0.221 | 120.982 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 7.5945 | 0.1684 | 68.4324 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 38.2915 | 0.619 | 518.976 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7036 | 6.7074 | 6607.4396 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 12.4611 | 0.2992 | 199.2002 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 12.4611 | 0.2992 | 199.2002 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.7632 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.7632 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 18.1007 | 0.3174 | 217.3518 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.2333 | 0.1889 | 88.86 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.2333 | 0.2209 | 120.8663 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 8.7299 | 0.171 | 70.9799 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 38.263 | 0.6191 | 519.067 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.7632 | 6.6994 | 6599.418 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 12.4636 | 0.2992 | 199.2048 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 12.4636 | 0.2992 | 199.2048 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.7663 | 0.2612 | 161.2322 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.7663 | 0.2612 | 161.2322 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 18.0923 | 0.3174 | 217.3575 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.2355 | 0.1889 | 88.8538 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.2355 | 0.2209 | 120.8578 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 9.1099 | 0.1709 | 70.9331 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 38.3515 | 0.619 | 519.0334 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.7663 | 6.6992 | 6599.1794 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2019 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2019 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.7687 | 0.2612 | 161.2348 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.7687 | 0.2612 | 161.2348 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 18.1082 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.2391 | 0.1888 | 88.8358 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.2391 | 0.2208 | 120.8329 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 7.6519 | 0.1703 | 70.2566 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 38.3661 | 0.619 | 519.0268 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.7687 | 6.6973 | 6597.3123 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 18.1082 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.2392 | 0.1889 | 88.8546 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.2392 | 0.2209 | 120.8585 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 9.2799 | 0.1711 | 71.1264 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 38.3653 | 0.619 | 519.0289 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.7742 | 6.6992 | 6599.2304 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 18.1082 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.2392 | 0.1889 | 88.8547 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.2392 | 0.2209 | 120.8587 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 9.2799 | 0.1711 | 71.1279 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 38.3653 | 0.619 | 519.0289 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.7742 | 6.6992 | 6599.2438 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.1524 | 0.3015 | 201.5233 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.1524 | 0.3015 | 201.5233 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.4676 | 0.266 | 166.0179 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.4676 | 0.266 | 166.0179 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 18.0756 | 0.3174 | 217.3658 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.1266 | 0.1906 | 90.5721 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.1266 | 0.2234 | 123.4102 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.9831 | 0.1715 | 71.513 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 37.8984 | 0.6188 | 518.8358 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.4676 | 6.8328 | 6732.7821 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.4676 | 3.9124 | 3812.3978 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.4676 | 6.8328 | 6732.7821 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 12.2472 | 0.2995 | 199.457 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 12.2472 | 0.2995 | 199.457 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 10.1879 | 0.2618 | 161.7729 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 10.1879 | 0.2618 | 161.7729 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 18.0941 | 0.3174 | 217.3572 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 10.0308 | 0.1887 | 88.7207 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 10.0308 | 0.2207 | 120.6964 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.1555 | 0.1714 | 71.4055 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 38.3564 | 0.619 | 519.0327 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 10.1879 | 6.6917 | 6591.7326 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 12.467 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 12.467 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.7732 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.7732 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 18.1074 | 0.3174 | 217.3506 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.2386 | 0.1888 | 88.8293 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.2386 | 0.2208 | 120.824 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 9.281 | 0.171 | 71.0457 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 37.7098 | 0.6192 | 519.1836 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.7732 | 6.6962 | 6596.2326 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.4645 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.4645 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7656 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7656 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 11.1354 | 0.3303 | 230.3368 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.2361 | 0.1889 | 88.8812 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.2361 | 0.2209 | 120.8952 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 9.2725 | 0.1712 | 71.1925 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 38.2553 | 0.619 | 518.9972 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7656 | 6.7037 | 6603.654 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 12.4666 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 12.4666 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.7708 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.7708 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 17.9782 | 0.3175 | 217.5317 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.2381 | 0.1888 | 88.8439 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.2381 | 0.2208 | 120.844 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 9.2783 | 0.1711 | 71.0765 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 38.3323 | 0.619 | 519.0265 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.7708 | 6.6982 | 6598.1635 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 12.4613 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 12.4613 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.7733 | 0.2612 | 161.2261 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.7733 | 0.2612 | 161.2261 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 18.0751 | 0.3174 | 217.4081 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.2349 | 0.1889 | 88.8705 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.2349 | 0.2209 | 120.8805 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 9.2806 | 0.1711 | 71.0999 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 38.3612 | 0.619 | 519.0298 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.7733 | 6.6982 | 6598.1833 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 11.1839 | 0.3027 | 202.6661 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 11.1839 | 0.3027 | 202.6661 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.567 | 0.2615 | 161.541 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.567 | 0.2615 | 161.541 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 18.1119 | 0.3173 | 217.3479 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.3851 | 0.1934 | 93.3724 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.3851 | 0.2272 | 127.1539 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.2788 | 0.1712 | 71.2255 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 38.3605 | 0.619 | 519.0314 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.567 | 6.7898 | 6689.8457 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 12.3381 | 0.2994 | 199.3694 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 12.3381 | 0.2994 | 199.3694 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.7734 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.7734 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 18.1081 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.178 | 0.1888 | 88.7776 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.178 | 0.2208 | 120.7594 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 9.2801 | 0.1711 | 71.0974 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 38.3656 | 0.619 | 519.0281 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.7734 | 6.7007 | 6600.7058 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 12.465 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 12.465 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.7744 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.7744 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 18.1087 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.2372 | 0.1888 | 88.8391 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.2372 | 0.2208 | 120.8375 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 8.473 | 0.171 | 71.0402 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 38.3607 | 0.619 | 519.0289 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.7744 | 6.6983 | 6598.3089 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 12.1106 | 0.2997 | 199.7006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 12.1106 | 0.2997 | 199.7006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.6557 | 0.2613 | 161.301 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.6557 | 0.2613 | 161.301 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 18.1079 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.9817 | 0.1889 | 88.8566 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.9817 | 0.2209 | 120.8907 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.2697 | 0.1712 | 71.1579 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 38.3538 | 0.619 | 519.0279 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.6557 | 6.7128 | 6612.8115 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 12.4256 | 0.2993 | 199.3196 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 12.4256 | 0.2993 | 199.3196 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.7639 | 0.2612 | 161.2415 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.7639 | 0.2612 | 161.2415 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 18.1085 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.2092 | 0.1888 | 88.8208 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.2092 | 0.2208 | 120.8176 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 9.2808 | 0.1711 | 71.085 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 38.3663 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.7639 | 6.7007 | 6600.7033 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 12.4087 | 0.2994 | 199.3632 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 12.4087 | 0.2994 | 199.3632 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.7596 | 0.2612 | 161.247 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.7596 | 0.2612 | 161.247 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 18.1085 | 0.3173 | 217.3497 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.1971 | 0.1888 | 88.81 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.1971 | 0.2208 | 120.8048 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 9.2809 | 0.1711 | 71.0816 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 38.3664 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.7596 | 6.7014 | 6601.3795 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 12.4891 | 0.2994 | 199.4156 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 12.4891 | 0.2994 | 199.4156 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.7907 | 0.2613 | 161.2607 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.7907 | 0.2613 | 161.2607 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 18.1124 | 0.3173 | 217.3482 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.2585 | 0.19 | 89.9971 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.2585 | 0.2224 | 122.4418 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 9.2835 | 0.171 | 71.0459 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 38.372 | 0.619 | 519.0232 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.7907 | 6.6987 | 6598.7055 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 12.4452 | 0.2993 | 199.2633 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 12.4452 | 0.2993 | 199.2633 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.7634 | 0.2612 | 161.2381 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.7634 | 0.2612 | 161.2381 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 18.1074 | 0.3174 | 217.3504 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.222 | 0.1888 | 88.8334 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.222 | 0.2208 | 120.8319 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 9.279 | 0.1711 | 71.1124 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 38.3632 | 0.619 | 519.029 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.7634 | 6.7014 | 6601.439 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 12.494 | 0.2995 | 199.5349 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 12.494 | 0.2995 | 199.5349 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.8039 | 0.2614 | 161.439 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.8039 | 0.2614 | 161.439 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 18.1132 | 0.3173 | 217.348 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.2633 | 0.1886 | 88.5904 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.2633 | 0.2205 | 120.5329 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 9.2845 | 0.171 | 71.0093 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 38.3747 | 0.619 | 519.017 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.8039 | 6.6876 | 6587.5901 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 12.4406 | 0.2998 | 199.825 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 12.4406 | 0.2998 | 199.825 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.7399 | 0.2616 | 161.6389 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.7399 | 0.2616 | 161.6389 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 18.1119 | 0.3173 | 217.3488 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.2136 | 0.1937 | 93.7135 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.2136 | 0.2275 | 127.5039 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 9.2722 | 0.1714 | 71.3684 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 38.364 | 0.619 | 519.0112 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.7399 | 6.8492 | 6749.2218 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 12.4644 | 0.2992 | 199.2035 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 12.4644 | 0.2992 | 199.2035 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.7708 | 0.2612 | 161.228 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.7708 | 0.2612 | 161.228 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.2362 | 0.1888 | 88.7935 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.2362 | 0.2208 | 120.7752 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 9.2806 | 0.1711 | 71.0909 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 38.3659 | 0.619 | 519.0285 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.7708 | 6.6971 | 6597.0737 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 12.4663 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 12.4663 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.7727 | 0.2612 | 161.2282 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.7727 | 0.2612 | 161.2282 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 18.1079 | 0.3174 | 217.3513 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.2379 | 0.1888 | 88.7975 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.2379 | 0.2208 | 120.7805 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 9.2818 | 0.171 | 71.0457 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 33.7431 | 0.6189 | 518.8849 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.7727 | 6.6934 | 6593.433 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 12.4663 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 12.4663 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.7727 | 0.2612 | 161.2282 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.7727 | 0.2612 | 161.2282 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 18.1079 | 0.3174 | 217.3513 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.2379 | 0.1888 | 88.7975 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.2379 | 0.2208 | 120.7805 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 9.2818 | 0.171 | 71.0457 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 33.7431 | 0.6189 | 518.8849 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.7727 | 6.6934 | 6593.4329 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 11.4467 | 0.3002 | 200.1603 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 11.4467 | 0.3002 | 200.1603 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.6141 | 0.2631 | 163.1254 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.6141 | 0.2631 | 163.1254 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 18.1021 | 0.3174 | 217.3537 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.2987 | 0.1896 | 89.556 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.2987 | 0.2219 | 121.9034 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.2436 | 0.1713 | 71.3366 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 37.9195 | 0.6189 | 518.9154 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.6141 | 6.7857 | 6685.6508 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.6141 | 3.895 | 3795.0297 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.6141 | 6.7857 | 6685.6508 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 18.1076 | 0.3174 | 217.3503 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2393 | 0.1889 | 88.8706 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2393 | 0.2209 | 120.8806 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.2794 | 0.1711 | 71.1326 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 38.3952 | 0.619 | 519.0482 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7739 | 6.7009 | 6600.8871 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 18.1076 | 0.3174 | 217.3503 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.2393 | 0.1889 | 88.8706 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.2393 | 0.2209 | 120.8806 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 9.2794 | 0.1711 | 71.1326 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 38.3952 | 0.619 | 519.0482 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.7739 | 6.7009 | 6600.8871 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.7739 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 18.1076 | 0.3174 | 217.3503 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.2393 | 0.1889 | 88.8706 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.2393 | 0.2209 | 120.8806 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 9.2794 | 0.1711 | 71.1326 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 38.3952 | 0.619 | 519.0482 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.7739 | 6.7009 | 6600.8871 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 18.1082 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.2392 | 0.1889 | 88.8521 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.2392 | 0.2209 | 120.8552 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 9.2805 | 0.1711 | 71.0958 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 38.3403 | 0.619 | 519.0356 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 6.699 | 6598.9709 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 18.1083 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-009 | S1263 Brock 161kV substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 8.2076 | 9.789 | 9688.9564 | 100 | 114.88 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 9.2806 | 0.1711 | 71.0958 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 38.364 | 0.619 | 519.0256 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.7742 | 6.699 | 6598.9955 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 18.1083 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.8517 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8547 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 9.2806 | 0.1711 | 71.0957 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 38.3597 | 0.619 | 519.029 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.7742 | 6.699 | 6599.0061 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.2393 | 0.1889 | 88.8514 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.2393 | 0.2209 | 120.8543 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 9.2806 | 0.1711 | 71.0947 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 38.3656 | 0.619 | 519.029 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.7743 | 6.6989 | 6598.925 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.7739 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.7739 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 18.1081 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.2393 | 0.1889 | 88.8624 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.2393 | 0.2209 | 120.8693 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 9.2797 | 0.1711 | 71.1181 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 38.2929 | 0.619 | 518.9931 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.7739 | 6.7002 | 6600.1515 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 18.1084 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.2393 | 0.1889 | 88.8511 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.2393 | 0.2209 | 120.8537 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 9.2806 | 0.1711 | 71.094 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 38.3638 | 0.619 | 519.0295 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.7742 | 6.6989 | 6598.8929 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 18.1084 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.2393 | 0.1889 | 88.8514 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.2393 | 0.2209 | 120.8542 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 9.2806 | 0.1711 | 71.0945 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 38.3658 | 0.619 | 519.0294 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.7743 | 6.6989 | 6598.9098 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.4407 | 0.2992 | 199.2103 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.4407 | 0.2992 | 199.2103 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7168 | 0.2612 | 161.2466 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7168 | 0.2612 | 161.2466 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 18.0422 | 0.3174 | 217.378 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.2145 | 0.189 | 88.9629 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.2145 | 0.221 | 121.0084 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 9.2485 | 0.1713 | 71.2616 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 35.8682 | 0.6185 | 518.5033 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7168 | 6.709 | 6609.0189 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.7741 | 0.2612 | 161.2263 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.7741 | 0.2612 | 161.2263 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 18.1084 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.2393 | 0.1889 | 88.861 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.2393 | 0.2209 | 120.8673 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 9.28 | 0.1711 | 71.1133 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 38.356 | 0.619 | 519.0188 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.7741 | 6.6998 | 6599.8162 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.774 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 18.1082 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.2391 | 0.1888 | 88.8482 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.2391 | 0.2208 | 120.8498 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 9.2805 | 0.1711 | 71.0881 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 38.2057 | 0.619 | 519.0222 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.774 | 6.6986 | 6598.5856 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 9.2806 | 0.1711 | 71.0951 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.7743 | 6.6989 | 6598.9428 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 9.2806 | 0.1711 | 71.0951 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.7743 | 6.6989 | 6598.9425 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 9.2806 | 0.1711 | 71.0952 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.7743 | 6.6989 | 6598.945 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 9.2806 | 0.1711 | 71.0951 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.7743 | 6.6989 | 6598.9399 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 12.4677 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 12.4677 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.7736 | 0.2612 | 161.2263 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.7736 | 0.2612 | 161.2263 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 18.108 | 0.3174 | 217.3504 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.2392 | 0.1889 | 88.87 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.2392 | 0.2209 | 120.8796 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 9.2782 | 0.1712 | 71.1519 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 37.7641 | 0.6192 | 519.2481 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.7736 | 6.7008 | 6600.7933 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 18.1084 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.2392 | 0.1889 | 88.8525 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.2392 | 0.2209 | 120.8558 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 9.2787 | 0.1711 | 71.0993 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 38.2018 | 0.619 | 519.0333 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.7739 | 6.699 | 6599.0491 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 12.4678 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 12.4678 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.7743 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.7743 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 18.1084 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.2393 | 0.1888 | 88.8485 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.2393 | 0.2209 | 120.8502 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 9.2809 | 0.1711 | 71.0854 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 38.3646 | 0.619 | 519.0396 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.7743 | 6.6985 | 6598.545 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 12.4676 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.7738 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.7738 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 18.1081 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.2391 | 0.1889 | 88.8584 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.2391 | 0.2209 | 120.8638 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 9.2794 | 0.1711 | 71.1166 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 37.9992 | 0.6191 | 519.1395 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.7738 | 6.6996 | 6599.6474 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 18.1082 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.85 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8523 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 9.2806 | 0.1711 | 71.0915 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 38.3617 | 0.619 | 519.0276 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7743 | 6.6987 | 6598.7358 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.4682 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.4682 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7736 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7736 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 17.6256 | 0.3177 | 217.7351 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.2396 | 0.1889 | 88.8906 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.2396 | 0.2209 | 120.9079 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 9.2765 | 0.1712 | 71.2341 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 37.2462 | 0.6189 | 518.8958 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.7736 | 6.7035 | 6603.511 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 12.4636 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 12.4636 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.7556 | 0.2612 | 161.2343 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.7556 | 0.2612 | 161.2343 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 18.0283 | 0.3174 | 217.4224 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.235 | 0.189 | 88.9868 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.235 | 0.221 | 121.0401 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 9.2557 | 0.1715 | 71.4777 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 38.1334 | 0.6189 | 518.9325 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.7556 | 6.7182 | 6618.2326 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 12.4663 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 12.4663 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.7712 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.7712 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 18.0908 | 0.3174 | 217.3708 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.238 | 0.1889 | 88.8659 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.238 | 0.2209 | 120.8743 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 9.2771 | 0.1711 | 71.1257 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 38.358 | 0.619 | 519.0313 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.7712 | 6.7006 | 6600.564 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 12.4663 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 12.4663 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.7712 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.7712 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 18.091 | 0.3174 | 217.3706 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.238 | 0.1889 | 88.8658 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.238 | 0.2209 | 120.8741 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 9.2771 | 0.1711 | 71.1254 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 38.3581 | 0.619 | 519.0313 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.7712 | 6.7005 | 6600.5483 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 12.4656 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 12.4656 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.7698 | 0.2612 | 161.2283 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.7698 | 0.2612 | 161.2283 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 18.0831 | 0.3174 | 217.3795 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.2374 | 0.1889 | 88.8728 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.2374 | 0.2209 | 120.8837 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 9.2755 | 0.1711 | 71.1405 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 38.3546 | 0.619 | 519.0323 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.7698 | 6.7013 | 6601.3263 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 12.4683 | 0.2992 | 199.2028 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 12.4683 | 0.2992 | 199.2028 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.7766 | 0.2612 | 161.227 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.7766 | 0.2612 | 161.227 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 18.1166 | 0.3173 | 217.3465 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.2399 | 0.1887 | 88.6923 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.2399 | 0.2206 | 120.6363 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 38.3824 | 0.619 | 519.0309 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.7766 | 6.6896 | 6589.618 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 12.467 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 12.467 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.7724 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.7724 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 18.1015 | 0.3174 | 217.3522 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.2386 | 0.1889 | 88.9016 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.2386 | 0.2209 | 120.923 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 9.277 | 0.1712 | 71.1897 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 37.8371 | 0.6194 | 519.4157 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.7724 | 6.7027 | 6602.6932 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 12.4543 | 0.2992 | 199.2256 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 12.4543 | 0.2992 | 199.2256 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.7592 | 0.2613 | 161.2527 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.7592 | 0.2613 | 161.2527 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 18.107 | 0.3174 | 217.3514 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.2273 | 0.1885 | 88.5447 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.2273 | 0.2204 | 120.4352 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 9.2866 | 0.17 | 70.0209 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 38.3595 | 0.619 | 519.0366 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.7592 | 6.6688 | 6568.7541 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 12.4671 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 12.4671 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 18.0819 | 0.3174 | 217.3873 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.2387 | 0.1889 | 88.8602 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.2387 | 0.2209 | 120.8663 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 9.2796 | 0.1711 | 71.109 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 38.361 | 0.619 | 519.0257 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.7733 | 6.6997 | 6599.7161 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 12.4671 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 12.4671 | 0.2992 | 199.2005 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 18.082 | 0.3174 | 217.3871 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.2387 | 0.1889 | 88.8603 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.2387 | 0.2209 | 120.8664 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 9.2796 | 0.1711 | 71.1093 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 38.361 | 0.619 | 519.0257 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.7733 | 6.6997 | 6599.7313 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.0983 | 0.3174 | 217.3518 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2394 | 0.1889 | 88.8616 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2394 | 0.2209 | 120.8682 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.2786 | 0.1712 | 71.1547 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 37.7835 | 0.6195 | 519.4938 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7743 | 6.6999 | 6599.8567 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 12.4671 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 12.4671 | 0.2992 | 199.2006 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.7733 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 18.0837 | 0.3174 | 217.385 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.2388 | 0.1889 | 88.8596 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.2388 | 0.2209 | 120.8654 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 9.2796 | 0.1711 | 71.1079 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 38.3613 | 0.619 | 519.0259 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.7733 | 6.6997 | 6599.6597 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.4649 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.4649 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7687 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7687 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 18.1015 | 0.3174 | 217.3512 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.2366 | 0.1888 | 88.8353 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.2366 | 0.2208 | 120.8322 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 9.2806 | 0.1711 | 71.0885 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 21.2796 | 0.6223 | 522.3309 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7687 | 6.6973 | 6597.2692 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 11.799 | 0.3005 | 200.4669 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 11.799 | 0.3005 | 200.4669 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 10.5911 | 0.2614 | 161.3924 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 10.5911 | 0.2614 | 161.3924 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 18.1102 | 0.3173 | 217.346 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 9.7565 | 0.1888 | 88.7911 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 9.7565 | 0.2208 | 120.8372 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 9.2768 | 0.1712 | 71.2153 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 38.3686 | 0.619 | 519.0292 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 & 2 | 10.5911 | 6.7345 | 6634.5117 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 18.1039 | 0.3174 | 217.3524 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.2399 | 0.189 | 88.9699 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.2399 | 0.221 | 121.0166 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 9.2741 | 0.1713 | 71.3337 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 38.5557 | 0.6191 | 519.1476 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.7728 | 6.711 | 6611.0397 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 18.1039 | 0.3174 | 217.3524 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 10.2399 | 0.189 | 88.9699 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 10.2399 | 0.221 | 121.0166 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 9.2741 | 0.1713 | 71.3337 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 38.5557 | 0.6191 | 519.1476 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 3 | 10.7728 | 6.711 | 6611.0397 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 12.4684 | 0.2992 | 199.2 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 10.7728 | 0.2612 | 161.2271 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 18.1039 | 0.3174 | 217.3524 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 10.2399 | 0.189 | 88.9699 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 10.2399 | 0.221 | 121.0166 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 9.2741 | 0.1713 | 71.3337 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 38.5557 | 0.6191 | 519.1476 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 & 3 | 10.7728 | 6.711 | 6611.0397 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 12.4668 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 12.4668 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 10.7731 | 0.2612 | 161.2272 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 10.7731 | 0.2612 | 161.2272 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 18.1072 | 0.3174 | 217.3506 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 10.2385 | 0.1888 | 88.83 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 10.2385 | 0.2208 | 120.825 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 9.2808 | 0.171 | 71.047 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 37.7104 | 0.6192 | 519.1844 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640362 [STERLNG7 115.00] CKT 1 | 10.7731 | 6.6963 | 6596.3005 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 10.7744 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 10.7744 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 18.1084 | 0.3174 | 217.3502 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 10.2392 | 0.1888 | 88.8397 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 10.2392 | 0.2208 | 120.8382 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 9.2813 | 0.1711 | 71.0684 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 38.3481 | 0.6191 | 519.119 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640172 [FIRTH 9 34.500] TO BUS 643057 [FIRTH T1 913.800] CKT 1 | 10.7744 | 6.6975 | 6597.4956 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 18.112 | 0.3173 | 217.3491 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 10.2394 | 0.1888 | 88.8398 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 10.2394 | 0.2208 | 120.8384 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 9.2806 | 0.1711 | 71.0956 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 38.4566 | 0.6189 | 518.9168 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 583700 [GEN-2013-019115.00] CKT 1 | 10.774 | 6.6995 | 6599.5335 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 12.467 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 12.467 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.7728 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.7728 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 17.6809 | 0.3179 | 217.8663 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.2386 | 0.1888 | 88.8446 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.2386 | 0.2208 | 120.8449 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.28 | 0.1711 | 71.0835 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 38.3522 | 0.619 | 519.0272 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.7728 | 6.6987 | 6598.7272 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 12.4669 | 0.2992 | 199.1999 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 12.4669 | 0.2992 | 199.1999 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.7698 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.7698 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 17.5922 | 0.3179 | 217.9497 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.2383 | 0.189 | 88.9627 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.2383 | 0.221 | 121.0066 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 9.2712 | 0.1714 | 71.3648 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 38.3111 | 0.619 | 519.0265 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.7698 | 6.7096 | 6609.6285 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 12.4649 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 12.4649 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.7677 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.7677 | 0.2612 | 161.2278 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 17.9204 | 0.3175 | 217.4556 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.2366 | 0.1889 | 88.8571 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.2366 | 0.2209 | 120.8621 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 9.2755 | 0.1711 | 71.1215 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 38.2799 | 0.619 | 519.0054 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.7677 | 6.7003 | 6600.3441 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 12.46 | 0.2992 | 199.2024 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 12.46 | 0.2992 | 199.2024 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.7671 | 0.2612 | 161.227 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.7671 | 0.2612 | 161.227 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 17.8929 | 0.3177 | 217.6829 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.2329 | 0.1888 | 88.8425 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.2329 | 0.2208 | 120.8422 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 9.2785 | 0.1711 | 71.0652 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 38.3468 | 0.619 | 519.0254 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.7671 | 6.6973 | 6597.3311 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 17.8116 | 0.3177 | 217.6705 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.2391 | 0.1889 | 88.8522 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.2391 | 0.2209 | 120.8553 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 9.2802 | 0.1711 | 71.0977 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 38.3606 | 0.619 | 519.0282 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.7739 | 6.699 | 6599.0258 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 12.4676 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 17.8404 | 0.3176 | 217.6393 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.2391 | 0.1889 | 88.8521 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.2391 | 0.2209 | 120.8552 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 9.2803 | 0.1711 | 71.0974 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 38.3611 | 0.619 | 519.0283 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.7739 | 6.699 | 6599.0174 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 12.4586 | 0.3002 | 200.2206 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 12.4586 | 0.3002 | 200.2206 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 10.7589 | 0.2619 | 161.8952 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 10.7589 | 0.2619 | 161.8952 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 18.116 | 0.3173 | 217.3472 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 10.2299 | 0.1945 | 94.4593 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 10.2299 | 0.2285 | 128.5458 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 9.2735 | 0.1714 | 71.3605 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 38.3699 | 0.619 | 518.9964 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640588 [TURTLE.CRK 3345.00] CKT 1 | 10.7589 | 6.8682 | 6768.1946 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 12.1149 | 0.2997 | 199.723 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 12.1149 | 0.2997 | 199.723 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 10.3667 | 0.2616 | 161.588 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 10.3667 | 0.2616 | 161.588 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 18.1069 | 0.3174 | 217.3505 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 9.8999 | 0.1894 | 89.3513 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 9.8999 | 0.2216 | 121.5757 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 9.2683 | 0.1712 | 71.1925 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 38.3413 | 0.619 | 519.0307 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640227 [HOSKINS4 230.00] TO BUS 643082 [HOSKINS T2 913.800] CKT 1 | 10.3667 | 6.7327 | 6632.738 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 12.3468 | 0.2995 | 199.4639 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 12.3468 | 0.2995 | 199.4639 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 10.5695 | 0.2615 | 161.4703 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 10.5695 | 0.2615 | 161.4703 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 18.1081 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 10.105 | 0.1893 | 89.2682 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 10.105 | 0.2214 | 121.4421 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 9.2751 | 0.1713 | 71.29 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 38.358 | 0.619 | 519.031 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 640231 [HOSKNS19 13.800] CKT 1 | 10.5695 | 6.7268 | 6626.7925 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.4674 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.4674 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7737 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7737 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 18.1069 | 0.3174 | 217.3505 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.2389 | 0.1888 | 88.8489 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.2389 | 0.2209 | 120.8508 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 9.2805 | 0.1711 | 71.0903 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 38.3776 | 0.619 | 519.032 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.7737 | 6.6989 | 6598.8739 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 12.4681 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 12.4681 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7743 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7743 | 0.2612 | 161.2269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 18.1269 | 0.3175 | 217.5153 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.2396 | 0.1889 | 88.8617 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.2396 | 0.2209 | 120.8683 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 9.2801 | 0.1711 | 71.1226 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 38.3713 | 0.619 | 519.0217 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7743 | 6.7006 | 6600.6153 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.4378 | 0.2992 | 199.2188 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.4378 | 0.2992 | 199.2188 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7194 | 0.2613 | 161.2537 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7194 | 0.2613 | 161.2537 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 18.0496 | 0.3174 | 217.3824 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.2119 | 0.1887 | 88.6827 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.2119 | 0.2206 | 120.6249 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 9.2678 | 0.1709 | 70.8547 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 33.8605 | 0.6188 | 518.8237 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.7194 | 6.6807 | 6580.7445 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2021 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2021 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.7712 | 0.2612 | 161.2285 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.7712 | 0.2612 | 161.2285 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 18.1046 | 0.3174 | 217.3526 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.2378 | 0.1888 | 88.8493 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.2378 | 0.2209 | 120.8514 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 9.2801 | 0.1711 | 71.0958 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 35.4903 | 0.6189 | 518.8826 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.7712 | 6.6988 | 6598.761 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 12.4673 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 12.4673 | 0.2992 | 199.2004 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 10.7725 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 10.7725 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 18.1077 | 0.3174 | 217.3505 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 10.2388 | 0.1889 | 88.8787 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 10.2388 | 0.2209 | 120.8916 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 9.2737 | 0.1712 | 71.1994 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 37.0861 | 0.6194 | 519.3923 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650242 [FOLSM&PHIL7 115.00] CKT 1 | 10.7725 | 6.7018 | 6601.8107 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 12.4672 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 12.4672 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7722 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7722 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 18.1075 | 0.3174 | 217.3507 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.2387 | 0.1889 | 88.8841 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.2387 | 0.2209 | 120.8991 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 9.2727 | 0.1712 | 71.2179 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 36.7471 | 0.6195 | 519.499 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7722 | 6.7024 | 6602.3911 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 12.4678 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 12.4678 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2267 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 18.1083 | 0.3174 | 217.3502 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 10.2393 | 0.1888 | 88.8469 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 10.2393 | 0.2208 | 120.848 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 9.2809 | 0.1711 | 71.0833 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 38.3565 | 0.6191 | 519.0868 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640279 [SHELDON9 34.500] TO BUS 643104 [SHELDON T4 913.800] CKT 1 | 10.7743 | 6.6983 | 6598.3036 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 12.4348 | 0.2992 | 199.2201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 12.4348 | 0.2992 | 199.2201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 10.7171 | 0.2613 | 161.2527 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 10.7171 | 0.2613 | 161.2527 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 18.1068 | 0.3174 | 217.351 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 10.2097 | 0.1889 | 88.8965 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 10.2097 | 0.2209 | 120.9182 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 7.6711 | 0.1698 | 69.7523 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 38.2935 | 0.619 | 519.0189 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640340 [SEWARD 7 115.00] CKT 1 | 10.7171 | 6.7026 | 6602.5713 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 12.4673 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 12.4673 | 0.2992 | 199.2025 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 10.7735 | 0.2612 | 161.2287 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 10.7735 | 0.2612 | 161.2287 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 18.1077 | 0.3174 | 217.3504 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 10.2388 | 0.1889 | 88.867 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 10.2388 | 0.2209 | 120.8757 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 9.2806 | 0.1713 | 71.2783 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 38.3631 | 0.619 | 519.0317 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640329 [RISNGCY9 34.500] TO BUS 643126 [RISINGCTYT1913.800] CKT 1 | 10.7735 | 6.7003 | 6600.2624 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 12.4624 | 0.2992 | 199.2117 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 12.4624 | 0.2992 | 199.2117 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 10.767 | 0.2612 | 161.2388 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 10.767 | 0.2612 | 161.2388 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 18.1066 | 0.3174 | 217.3516 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 10.2345 | 0.1888 | 88.8023 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 10.2345 | 0.2208 | 120.7874 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 9.2338 | 0.1697 | 69.7377 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 38.357 | 0.619 | 519.0404 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 640417 [RISNGCY8 69.000] TO BUS 643127 [RISINGCTYT2913.800] CKT 1 | 10.767 | 6.6937 | 6593.6662 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 12.2471 | 0.2995 | 199.4571 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 12.2471 | 0.2995 | 199.4571 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 10.1878 | 0.2618 | 161.7729 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 10.1878 | 0.2618 | 161.7729 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 18.0942 | 0.3174 | 217.3572 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 10.0307 | 0.1887 | 88.7146 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 10.0307 | 0.2207 | 120.688 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 9.1559 | 0.1714 | 71.3766 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 38.3565 | 0.619 | 519.0326 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 640343 [SHELCRK4 230.00] TO BUS 643136 [SHELLCRK T1913.800] CKT 1 | 10.1878 | 6.6912 | 6591.1804 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 12.4547 | 0.2992 | 199.2046 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 12.4547 | 0.2992 | 199.2046 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.7478 | 0.2612 | 161.2346 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.7478 | 0.2612 | 161.2346 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 16.1299 | 0.3197 | 219.6672 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.2273 | 0.1889 | 88.9179 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.2273 | 0.2209 | 120.946 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 9.257 | 0.1713 | 71.2625 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 38.2244 | 0.619 | 518.9928 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.7478 | 6.7067 | 6606.679 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-065 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 9.5335 | 3.1626 | 3062.5726 | 19.8 | 22.67 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 9.5335 | 0.3022 | 202.2297 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 9.5335 | 0.3022 | 202.2297 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.8804 | 0.2631 | 163.147 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.8804 | 0.2631 | 163.147 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 18.0891 | 0.3174 | 217.3534 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.595 | 0.191 | 91.0414 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.595 | 0.2241 | 124.1312 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 9.0952 | 0.1716 | 71.624 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 38.1885 | 0.619 | 518.9873 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.8804 | 6.8404 | 6740.4278 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.8804 | 3.9135 | 3813.503 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 7.8804 | 6.8404 | 6740.4278 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 11.165 | 0.3027 | 202.7156 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 11.165 | 0.3027 | 202.7156 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 10.5591 | 0.2615 | 161.5456 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 10.5591 | 0.2615 | 161.5456 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 18.112 | 0.3173 | 217.3478 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 9.3698 | 0.1921 | 92.1459 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 9.3698 | 0.2255 | 125.5063 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 9.2792 | 0.1712 | 71.1971 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 38.3605 | 0.619 | 519.031 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 640521 [ANTELOPE 7115.00] TO BUS 640524 [ANTELOPE 913.800] CKT 1 | 10.5591 | 6.7777 | 6677.6883 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 18.1083 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.8529 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8563 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 9.2805 | 0.1711 | 71.097 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 38.3404 | 0.619 | 519.0356 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646366 [S1366 5 161.00] CKT 1 | 10.7743 | 6.699 | 6599.036 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 9.2806 | 0.1711 | 71.0951 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648600 [NC1HS 5 161.00] CKT 1 | 10.7743 | 6.6989 | 6598.9401 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 9.2806 | 0.1711 | 71.0951 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 648610 [NC2HS 5 161.00] CKT 1 | 10.7743 | 6.6989 | 6598.9397 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 12.4678 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 10.7742 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 10.7742 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 18.1083 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 10.2393 | 0.1889 | 88.8565 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 10.2393 | 0.2209 | 120.8612 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 9.2802 | 0.1711 | 71.1044 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 38.3619 | 0.619 | 519.028 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647963 [S963 8 69.000] CKT 1 | 10.7742 | 6.6994 | 6599.4025 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 12.4677 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 12.4677 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 18.1081 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 10.2392 | 0.1889 | 88.8513 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 10.2392 | 0.2209 | 120.8541 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 9.2804 | 0.1711 | 71.0947 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 38.207 | 0.619 | 519.0084 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 647967 [S967 8 69.000] CKT 1 | 10.7739 | 6.6989 | 6598.9279 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7739 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 18.1083 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.2392 | 0.1889 | 88.8567 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.2392 | 0.2209 | 120.8615 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 9.279 | 0.1711 | 71.1167 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 38.1605 | 0.6191 | 519.0836 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650246 [SW7&BENNET7 115.00] CKT 1 | 10.7739 | 6.6995 | 6599.4873 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 18.112 | 0.3173 | 217.3491 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2394 | 0.1888 | 88.8398 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2394 | 0.2208 | 120.8384 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.2806 | 0.1711 | 71.0956 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 38.4566 | 0.6189 | 518.9168 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 560746 [G13-002-TAP 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.774 | 6.6995 | 6599.5335 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 10.774 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 18.112 | 0.3173 | 217.3491 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 10.2394 | 0.1888 | 88.8395 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 10.2394 | 0.2208 | 120.838 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 9.2806 | 0.1711 | 71.095 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 38.4563 | 0.6189 | 518.9165 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 583700 [GEN-2013-019115.00] TO BUS 583701 [G13-019XFMR134.500] CKT 1 | 10.774 | 6.6995 | 6599.5055 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 12.4679 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.7747 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.7747 | 0.2612 | 161.2268 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 18.1308 | 0.3175 | 217.5261 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.2394 | 0.1888 | 88.8348 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.2394 | 0.2208 | 120.8316 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 9.2818 | 0.1711 | 71.06 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 38.3756 | 0.619 | 519.0199 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.7747 | 6.6979 | 6597.9328 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 12.4599 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 12.4599 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 10.7646 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 10.7646 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 16.2893 | 0.3189 | 218.9027 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 10.2329 | 0.1888 | 88.756 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 10.2329 | 0.2207 | 120.7238 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 9.2821 | 0.1709 | 70.8513 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 38.3204 | 0.619 | 518.9975 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640011 [GENTLM2G 24.000] TO BUS 640183 [GENTLMN3 345.00] CKT 1 | 10.7646 | 6.692 | 6591.9993 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 12.395 | 0.2993 | 199.2881 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 12.395 | 0.2993 | 199.2881 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.6977 | 0.2613 | 161.2835 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.6977 | 0.2613 | 161.2835 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 18.1079 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.1722 | 0.1888 | 88.8348 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.1722 | 0.2208 | 120.8408 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 9.2754 | 0.1711 | 71.101 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 38.3501 | 0.619 | 519.0183 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.6977 | 6.7003 | 6600.2551 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 12.4663 | 0.2992 | 199.2059 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 12.4663 | 0.2992 | 199.2059 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.7724 | 0.2612 | 161.2298 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.7724 | 0.2612 | 161.2298 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.2379 | 0.1889 | 88.8798 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.2379 | 0.2209 | 120.8933 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 9.2805 | 0.1711 | 71.1016 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 38.3656 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.7724 | 6.7006 | 6600.6322 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 12.3389 | 0.2993 | 199.2618 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 12.3389 | 0.2993 | 199.2618 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.6432 | 0.2613 | 161.2651 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.6432 | 0.2613 | 161.2651 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 18.1239 | 0.3173 | 217.342 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.1202 | 0.1888 | 88.8181 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.1202 | 0.2208 | 120.816 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 9.2762 | 0.171 | 70.959 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 38.3488 | 0.619 | 519.0186 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.6432 | 6.6874 | 6587.3651 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 12.2911 | 0.2993 | 199.2818 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 12.2911 | 0.2993 | 199.2818 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.5939 | 0.2613 | 161.2782 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.5939 | 0.2613 | 161.2782 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 18.1273 | 0.3173 | 217.3401 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.0761 | 0.1888 | 88.8227 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.0761 | 0.2208 | 120.8251 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 9.2737 | 0.1709 | 70.9327 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 38.3401 | 0.619 | 519.0145 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.5939 | 6.6852 | 6585.2153 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 12.4099 | 0.2993 | 199.2591 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 12.4099 | 0.2993 | 199.2591 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.7137 | 0.2613 | 161.2646 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.7137 | 0.2613 | 161.2646 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 18.1065 | 0.3174 | 217.3507 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.186 | 0.1889 | 88.8583 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.186 | 0.2209 | 120.8699 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 9.2757 | 0.1711 | 71.135 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 38.3576 | 0.619 | 519.0246 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.7137 | 6.7031 | 6603.0771 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 12.4509 | 0.2992 | 199.223 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 12.4509 | 0.2992 | 199.223 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.7542 | 0.2612 | 161.2426 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.7542 | 0.2612 | 161.2426 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 18.1129 | 0.3173 | 217.3478 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.2231 | 0.189 | 89.0234 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.2231 | 0.2211 | 121.0914 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 9.2807 | 0.1711 | 71.0804 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 38.361 | 0.619 | 519.0281 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.7542 | 6.7047 | 6604.7194 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 12.3545 | 0.2993 | 199.2848 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 12.3545 | 0.2993 | 199.2848 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.6705 | 0.2613 | 161.2741 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.6705 | 0.2613 | 161.2741 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 18.1041 | 0.3174 | 217.3519 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.1349 | 0.1889 | 88.8882 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.1349 | 0.2209 | 120.9127 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 9.275 | 0.1712 | 71.227 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 38.2768 | 0.619 | 518.9956 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.6705 | 6.7099 | 6609.9103 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 12.4663 | 0.2992 | 199.2059 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 12.4663 | 0.2992 | 199.2059 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.7725 | 0.2612 | 161.2298 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.7725 | 0.2612 | 161.2298 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.2379 | 0.1889 | 88.8797 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.2379 | 0.2209 | 120.8932 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 9.2805 | 0.1711 | 71.1016 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 38.3656 | 0.619 | 519.0287 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.7725 | 6.7006 | 6600.6284 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4598 | 0.2992 | 199.2022 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4598 | 0.2992 | 199.2022 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.761 | 0.2612 | 161.2291 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.761 | 0.2612 | 161.2291 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 17.6691 | 0.3178 | 217.7925 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.232 | 0.1889 | 88.8603 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.232 | 0.2209 | 120.8668 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 9.2723 | 0.1711 | 71.0861 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 38.1486 | 0.619 | 518.9565 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.761 | 6.6968 | 6596.7924 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 12.4655 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 12.4655 | 0.2992 | 199.2018 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 10.7683 | 0.2612 | 161.229 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 10.7683 | 0.2612 | 161.229 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 17.5168 | 0.3179 | 217.8598 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 10.2371 | 0.1889 | 88.8774 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 10.2371 | 0.2209 | 120.89 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 9.2772 | 0.1712 | 71.1506 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 37.9523 | 0.619 | 518.9515 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640312 [PAULINE3 345.00] CKT 1 | 10.7683 | 6.7016 | 6601.5532 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4609 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4609 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7599 | 0.2612 | 161.2292 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7599 | 0.2612 | 161.2292 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.0998 | 0.3174 | 217.3516 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.233 | 0.1889 | 88.8667 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.233 | 0.2209 | 120.8755 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.2719 | 0.1711 | 71.1445 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 36.1749 | 0.6186 | 518.6493 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640019 [SHELDN1G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7599 | 6.7019 | 6601.8898 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 12.4683 | 0.2992 | 199.1998 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 12.4683 | 0.2992 | 199.1998 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.7745 | 0.2612 | 161.2258 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.7745 | 0.2612 | 161.2258 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 18.0246 | 0.3175 | 217.4847 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.2398 | 0.1889 | 88.8721 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.2398 | 0.2209 | 120.8825 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 9.2794 | 0.1711 | 71.1422 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 38.3575 | 0.619 | 519.0374 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640066 [AXTELL 7 115.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.7745 | 6.701 | 6600.9528 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 10.7707 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 10.7707 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 18.1073 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 10.2378 | 0.1888 | 88.8443 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 10.2378 | 0.2208 | 120.8446 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 9.2789 | 0.1711 | 71.0921 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 37.9008 | 0.619 | 518.9677 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640022 [BPS GT1G 13.800] CKT 1 | 10.7707 | 6.6991 | 6599.1384 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2011 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 10.7708 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 10.7708 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 18.1073 | 0.3174 | 217.3501 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 10.2378 | 0.1888 | 88.8443 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 10.2378 | 0.2208 | 120.8445 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 9.2789 | 0.1711 | 71.0921 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 37.9013 | 0.619 | 518.9677 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640023 [BPS GT2G 13.800] CKT 1 | 10.7708 | 6.6991 | 6599.1384 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2012 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 12.4661 | 0.2992 | 199.2012 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 10.7707 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 10.7707 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 18.1075 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 10.2377 | 0.1888 | 88.8436 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 10.2377 | 0.2208 | 120.8436 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 9.2788 | 0.1711 | 71.0922 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 37.9026 | 0.619 | 518.9674 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640024 [BPS ST3G 13.800] CKT 1 | 10.7707 | 6.6992 | 6599.1871 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 18.1084 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 10.2394 | 0.1889 | 88.8527 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 10.2394 | 0.2209 | 120.856 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 9.2806 | 0.1711 | 71.0967 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 38.3447 | 0.6191 | 519.0529 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 | 10.7743 | 6.699 | 6599.0003 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 12.4679 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 12.4679 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 18.1084 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 10.2394 | 0.1889 | 88.8529 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 10.2394 | 0.2209 | 120.8562 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 9.2806 | 0.1711 | 71.0969 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 38.3425 | 0.6191 | 519.0549 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 2 | 10.7743 | 6.699 | 6599.008 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 12.4677 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 12.4677 | 0.2992 | 199.2009 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 10.7742 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 10.7742 | 0.2612 | 161.2266 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 18.1081 | 0.3174 | 217.3502 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 10.2393 | 0.1889 | 88.8505 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 10.2393 | 0.2209 | 120.853 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 9.2806 | 0.1711 | 71.0909 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 38.3572 | 0.6191 | 519.0587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640112 [CLATONA9 34.500] TO BUS 643035 [CLATONIA T1913.800] CKT 1 | 10.7742 | 6.6987 | 6598.6886 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 12.3895 | 0.2992 | 199.2194 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 12.3895 | 0.2992 | 199.2194 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 10.627 | 0.2613 | 161.2625 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 10.627 | 0.2613 | 161.2625 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 18.1031 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 10.1683 | 0.189 | 88.9535 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 10.1683 | 0.221 | 120.9984 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 9.013 | 0.1714 | 71.3738 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 38.2985 | 0.619 | 518.9898 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640028 [COLCOG1G 13.800] CKT 1 | 10.627 | 6.7106 | 6610.6295 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 12.4679 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 10.7744 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 10.7744 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 18.1084 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 10.2394 | 0.1889 | 88.8547 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 10.2394 | 0.2209 | 120.8587 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 9.2805 | 0.1711 | 71.1074 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 38.3658 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 | 10.7744 | 6.6992 | 6599.2357 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 12.4679 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 12.4679 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 10.7743 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 10.7743 | 0.2612 | 161.2264 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 18.1084 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 10.2394 | 0.1889 | 88.8541 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 10.2394 | 0.2209 | 120.8579 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 9.2805 | 0.1711 | 71.1049 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 38.3658 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 2 | 10.7743 | 6.6992 | 6599.1787 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4621 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4621 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7625 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7625 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.1003 | 0.3174 | 217.3517 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2341 | 0.1889 | 88.8657 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2341 | 0.2209 | 120.8741 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.2735 | 0.1711 | 71.1322 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 36.5156 | 0.6187 | 518.7023 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640020 [SHELDN2G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7625 | 6.701 | 6601.0083 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 12.4457 | 0.2992 | 199.2193 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 12.4457 | 0.2992 | 199.2193 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7165 | 0.2613 | 161.2667 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7165 | 0.2613 | 161.2667 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 18.1089 | 0.3173 | 217.3497 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.2183 | 0.1887 | 88.6534 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.2183 | 0.2206 | 120.5846 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 8.168 | 0.1717 | 71.719 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 38.3622 | 0.619 | 519.0293 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7165 | 6.6789 | 6578.9346 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.4286 | 0.2992 | 199.2416 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.4286 | 0.2992 | 199.2416 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7134 | 0.2613 | 161.2734 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7134 | 0.2613 | 161.2734 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 18.1089 | 0.3173 | 217.3489 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.2044 | 0.1886 | 88.587 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.2044 | 0.2205 | 120.495 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 1.8222 | 0.1488 | 48.7826 | 174.5 | 199.26 | FAIL | FAIL
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 38.305 | 0.619 | 518.9769 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.7134 | 6.6782 | 6578.1627 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 11.541 | 0.2999 | 199.8793 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 11.541 | 0.2999 | 199.8793 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9434 | 0.2625 | 162.483 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9434 | 0.2625 | 162.483 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 18.1007 | 0.3174 | 217.3551 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.3933 | 0.1894 | 89.3608 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.3933 | 0.2216 | 121.6218 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9407 | 0.1715 | 71.4958 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 37.4329 | 0.6189 | 518.8518 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9434 | 6.7543 | 6654.3351 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9434 | 3.8871 | 3787.0522 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 8.9434 | 6.7543 | 6654.3351 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 12.4095 | 0.2993 | 199.2909 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 12.4095 | 0.2993 | 199.2909 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 10.5683 | 0.2615 | 161.4581 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 10.5683 | 0.2615 | 161.4581 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 18.1075 | 0.3173 | 217.3496 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 10.1822 | 0.1888 | 88.8295 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 10.1822 | 0.2208 | 120.8306 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 8.6776 | 0.1712 | 71.2354 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 38.3359 | 0.619 | 519.0358 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640127 [COLMB.E7 115.00] TO BUS 640129 [COLMB.T9 13.800] CKT 1 | 10.5683 | 6.6969 | 6596.8518 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2296 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2296 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 18.1084 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 10.2325 | 0.1889 | 88.8552 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 10.2325 | 0.2209 | 120.8598 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 9.2599 | 0.1711 | 71.0796 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 38.3613 | 0.619 | 519.0254 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640006 [COLMBS1G 13.800] CKT 1 | 10.7611 | 6.6996 | 6599.6037 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2295 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2295 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 18.1084 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 10.2325 | 0.1889 | 88.8551 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 10.2325 | 0.2209 | 120.8598 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 9.26 | 0.1711 | 71.0794 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 38.3613 | 0.619 | 519.0254 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640007 [COLMBS2G 13.800] CKT 1 | 10.7611 | 6.6996 | 6599.598 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 12.4602 | 0.2992 | 199.2026 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2296 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 10.7611 | 0.2612 | 161.2296 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 18.1084 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 10.2325 | 0.1889 | 88.8552 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 10.2325 | 0.2209 | 120.8599 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 9.2599 | 0.1711 | 71.0796 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 38.3613 | 0.619 | 519.0254 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640008 [COLMBS3G 13.800] CKT 1 | 10.7611 | 6.6996 | 6599.6048 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 12.4683 | 0.2992 | 199.1999 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 12.4683 | 0.2992 | 199.1999 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7663 | 0.2612 | 161.2402 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7663 | 0.2612 | 161.2402 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 18.1082 | 0.3173 | 217.3498 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.2398 | 0.1889 | 88.8715 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.2398 | 0.2209 | 120.8817 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 9.2718 | 0.1711 | 71.1001 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 38.3595 | 0.619 | 519.0304 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640127 [COLMB.E7 115.00] CKT 1 | 10.7663 | 6.6989 | 6598.8864 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 12.4683 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 12.4683 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 10.7681 | 0.2612 | 161.2354 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 10.7681 | 0.2612 | 161.2354 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 18.1077 | 0.3174 | 217.3507 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 10.2396 | 0.1888 | 88.8468 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 10.2396 | 0.2208 | 120.8478 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 9.1551 | 0.1713 | 71.2819 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 38.3658 | 0.619 | 519.0288 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640134 [KELLY 7 115.00] CKT 1 | 10.7681 | 6.6956 | 6595.5666 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 12.3824 | 0.2992 | 199.2485 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 12.3824 | 0.2992 | 199.2485 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 10.7477 | 0.2612 | 161.2297 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 10.7477 | 0.2612 | 161.2297 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 18.1066 | 0.3174 | 217.3512 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 10.1638 | 0.189 | 88.9647 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 10.1638 | 0.221 | 121.0159 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 9.1606 | 0.1708 | 70.8202 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 38.3552 | 0.619 | 519.0261 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640151 [CRESTON7 115.00] CKT 1 | 10.7477 | 6.6989 | 6598.9066 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4659 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.4659 | 0.2992 | 199.201 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7701 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7701 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 18.1063 | 0.3174 | 217.3503 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2376 | 0.1889 | 88.8592 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.2376 | 0.2209 | 120.8649 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.2778 | 0.1711 | 71.1193 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 37.7288 | 0.6189 | 518.9216 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640021 [HALLAM3G 13.800] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.7701 | 6.7004 | 6600.3787 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 12.4282 | 0.2992 | 199.2085 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 12.4282 | 0.2992 | 199.2085 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 10.78 | 0.2612 | 161.2369 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 10.78 | 0.2612 | 161.2369 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 18.11 | 0.3173 | 217.3492 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 10.2184 | 0.1889 | 88.9125 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 10.2184 | 0.2209 | 120.9387 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 9.1836 | 0.1711 | 71.1459 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 38.3579 | 0.619 | 519.0318 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640181 [GENOA 7 115.00] CKT 1 | 10.78 | 6.6981 | 6598.0631 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 12.4384 | 0.2992 | 199.2219 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 12.4384 | 0.2992 | 199.2219 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 10.7151 | 0.2613 | 161.2631 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 10.7151 | 0.2613 | 161.2631 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 18.1032 | 0.3174 | 217.3528 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 10.2131 | 0.1888 | 88.8181 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 10.2131 | 0.2208 | 120.8107 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 9.1332 | 0.1709 | 70.9235 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 38.3396 | 0.619 | 519.0301 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640336 [SCHUYLR7 115.00] CKT 1 | 10.7151 | 6.6942 | 6594.1953 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 12.4329 | 0.2992 | 199.2364 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 12.4329 | 0.2992 | 199.2364 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 10.7175 | 0.2613 | 161.269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 10.7175 | 0.2613 | 161.269 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 18.0897 | 0.3174 | 217.3559 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 10.2081 | 0.1889 | 88.8539 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 10.2081 | 0.2209 | 120.8604 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 9.1781 | 0.1711 | 71.0938 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 38.3648 | 0.619 | 519.0278 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640345 [SILVRCK7 115.00] CKT 1 | 10.7175 | 6.7001 | 6600.1157 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 12.4684 | 0.2992 | 199.2002 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 12.4684 | 0.2992 | 199.2002 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 10.7748 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 10.7748 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 18.1083 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 10.2399 | 0.1889 | 88.8784 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 10.2399 | 0.2209 | 120.8912 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 9.2793 | 0.1712 | 71.1941 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 38.3655 | 0.619 | 519.0288 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643041 [COLUMBUS T5913.800] CKT 1 | 10.7748 | 6.7014 | 6601.3521 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 12.4684 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 12.4684 | 0.2992 | 199.2003 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 10.7748 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 10.7748 | 0.2612 | 161.2262 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 18.1082 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 10.2399 | 0.1889 | 88.8793 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 10.2399 | 0.2209 | 120.8924 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 9.2793 | 0.1712 | 71.1976 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 38.3654 | 0.619 | 519.0289 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640136 [COLMBUS7 115.00] TO BUS 640137 [COLMBUS9 34.500] TO BUS 643042 [COLUMBUS T6913.800] CKT 1 | 10.7748 | 6.7014 | 6601.4317 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 12.465 | 0.2992 | 199.2017 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 12.465 | 0.2992 | 199.2017 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.7698 | 0.2612 | 161.2279 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.7698 | 0.2612 | 161.2279 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 18.0994 | 0.3174 | 217.3539 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.2368 | 0.1889 | 88.863 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.2368 | 0.2209 | 120.8702 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 9.279 | 0.1711 | 71.088 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 38.2391 | 0.619 | 519.016 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.7698 | 6.6985 | 6598.5234 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 12.4631 | 0.2992 | 199.2023 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 12.4631 | 0.2992 | 199.2023 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.7668 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.7668 | 0.2612 | 161.2286 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 18.0925 | 0.3174 | 217.3569 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.235 | 0.1889 | 88.8626 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.235 | 0.2209 | 120.8698 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 9.2783 | 0.1711 | 71.074 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 38.164 | 0.619 | 519.0063 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.7668 | 6.6978 | 6597.7542 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 12.4677 | 0.2992 | 199.2015 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 12.4677 | 0.2992 | 199.2015 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.774 | 0.2612 | 161.2279 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.774 | 0.2612 | 161.2279 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 18.1067 | 0.3174 | 217.3514 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.2392 | 0.1889 | 88.8592 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.2392 | 0.2209 | 120.865 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 9.28 | 0.1711 | 71.0841 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 38.2303 | 0.619 | 519 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.774 | 6.698 | 6597.9619 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 12.4589 | 0.2992 | 199.202 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 12.4589 | 0.2992 | 199.202 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.755 | 0.2612 | 161.2306 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.755 | 0.2612 | 161.2306 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 18.1093 | 0.3173 | 217.348 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.2311 | 0.1889 | 88.9167 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.2311 | 0.2209 | 120.9439 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 9.2687 | 0.1713 | 71.2838 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 37.9463 | 0.6189 | 518.9232 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.755 | 6.7102 | 6610.2411 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 12.4661 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 12.4661 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.7715 | 0.2612 | 161.2274 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.7715 | 0.2612 | 161.2274 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 18.1043 | 0.3174 | 217.3518 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.2378 | 0.1889 | 88.8723 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.2378 | 0.2209 | 120.8829 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 9.2792 | 0.1711 | 71.1214 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 38.3545 | 0.619 | 519.0301 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.7715 | 6.7009 | 6600.8856 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 12.4678 | 0.2992 | 199.1997 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 12.4678 | 0.2992 | 199.1997 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7709 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7709 | 0.2612 | 161.2273 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 16.1467 | 0.3197 | 219.6907 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.2391 | 0.189 | 88.9597 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.2391 | 0.221 | 121.0025 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 9.2714 | 0.1714 | 71.3792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 38.2929 | 0.619 | 519.0125 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640065 [AXTELL 3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.7709 | 6.7107 | 6610.7077 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 18.1085 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.2393 | 0.1889 | 88.8514 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.2393 | 0.2209 | 120.8542 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 9.2806 | 0.1711 | 71.0946 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 38.3654 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.7743 | 6.6989 | 6598.9146 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 18.1085 | 0.3173 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.2393 | 0.1889 | 88.8514 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.2393 | 0.2209 | 120.8542 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 9.2806 | 0.1711 | 71.0947 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 38.3654 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.7743 | 6.6989 | 6598.9186 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 10.7743 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 18.1085 | 0.3173 | 217.3499 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 10.2393 | 0.1889 | 88.8516 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 10.2393 | 0.2209 | 120.8545 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 9.2806 | 0.1711 | 71.0952 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 38.3659 | 0.619 | 519.0286 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 640446 [COOPER 869.000] TO BUS 643173 [COOPER T6 913.800] CKT 1 | 10.7743 | 6.6989 | 6598.9462 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 12.4678 | 0.2992 | 199.2008 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 10.7742 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 18.099 | 0.3174 | 217.3561 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 10.2393 | 0.1889 | 88.8529 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 10.2393 | 0.2209 | 120.8563 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 9.2801 | 0.1711 | 71.0978 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 37.8115 | 0.6192 | 519.224 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640174 [FRIEND 7 115.00] CKT 1 | 10.7742 | 6.6991 | 6599.0807 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 10.7741 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 10.7741 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 18.1081 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 10.2392 | 0.1889 | 88.8547 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 10.2392 | 0.2209 | 120.8587 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 9.2802 | 0.1711 | 71.1021 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 38.3668 | 0.619 | 519.0307 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643048 [CRETE T1 913.800] CKT 1 | 10.7741 | 6.6993 | 6599.2549 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 12.4677 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 10.7741 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 10.7741 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 18.1081 | 0.3174 | 217.35 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 10.2392 | 0.1889 | 88.8546 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 10.2392 | 0.2209 | 120.8586 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 9.2802 | 0.1711 | 71.1019 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 38.3668 | 0.619 | 519.0306 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640154 [CRETE G 34.500] TO BUS 643049 [CRETE T2 913.800] CKT 1 | 10.7741 | 6.6992 | 6599.2449 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4669 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.4669 | 0.2992 | 199.2016 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7731 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7731 | 0.2612 | 161.2275 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 18.107 | 0.3174 | 217.3511 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2385 | 0.1888 | 88.8373 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.2385 | 0.2208 | 120.8349 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.2805 | 0.1711 | 71.0583 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 37.7128 | 0.6193 | 519.3188 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640171 [FIRTH 7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.7731 | 6.6968 | 6596.8388 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.4633 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.4633 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7655 | 0.2612 | 161.228 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7655 | 0.2612 | 161.228 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 9.0116 | 0.3368 | 236.7688 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.2352 | 0.1888 | 88.8457 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.2352 | 0.2208 | 120.8466 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 9.2748 | 0.1711 | 71.0897 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 38.2485 | 0.619 | 519.0059 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.7655 | 6.6989 | 6598.9165 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 12.4608 | 0.2992 | 199.2024 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 12.4608 | 0.2992 | 199.2024 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 10.7663 | 0.2612 | 161.2272 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 10.7663 | 0.2612 | 161.2272 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 17.0135 | 0.3181 | 218.1213 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 10.2337 | 0.1888 | 88.7604 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 10.2337 | 0.2207 | 120.7298 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 9.283 | 0.1709 | 70.8552 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 38.3409 | 0.619 | 519.0008 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1 | 10.7663 | 6.6922 | 6592.1777 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 12.4674 | 0.2992 | 199.2007 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 10.7738 | 0.2612 | 161.2265 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 18.1001 | 0.3174 | 217.3609 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 10.239 | 0.1889 | 88.8544 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 10.239 | 0.2209 | 120.8583 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 9.2801 | 0.1711 | 71.0998 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 38.3639 | 0.619 | 519.0277 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 | 10.7738 | 6.6992 | 6599.1964 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 12.4656 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 12.4656 | 0.2992 | 199.2014 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 10.77 | 0.2612 | 161.2277 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 10.77 | 0.2612 | 161.2277 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 18.106 | 0.3174 | 217.3505 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 10.2373 | 0.1889 | 88.8564 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 10.2373 | 0.2209 | 120.8612 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 9.2781 | 0.1711 | 71.1056 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 37.571 | 0.6191 | 519.0863 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25SP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640111 [CLATONA7 115.00] CKT 1 | 10.77 | 6.6995 | 6599.4962 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | Base | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | Base | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | Base | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | Base | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | Base | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | Base | 10.0716 | 0.1921 | 92.0979 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | Base | 10.0716 | 0.2253 | 125.2823 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | Base | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | Base | 35.2266 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | Base | 10.5148 | 7.0303 | 6930.2742 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 12.2898 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 12.2898 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.5141 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.5141 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 17.5771 | 0.3179 | 217.8812 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.0711 | 0.1921 | 92.099 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.0711 | 0.2253 | 125.2838 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 9.0976 | 0.1706 | 70.5818 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 35.2239 | 0.6186 | 518.5572 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 | 10.5141 | 7.0305 | 6930.4594 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 12.2898 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 12.2898 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.5141 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.5141 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 17.5771 | 0.3179 | 217.8812 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.0711 | 0.1921 | 92.0991 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.0711 | 0.2253 | 125.2839 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 9.0976 | 0.1706 | 70.5819 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 35.2239 | 0.6186 | 518.5572 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 3 | 10.5141 | 7.0305 | 6930.4659 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 17.5833 | 0.3179 | 217.8751 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.0715 | 0.1921 | 92.0993 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.0715 | 0.2253 | 125.2842 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 9.0979 | 0.1706 | 70.5822 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 35.2262 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640302 [OGALALA4 230.00] CKT 1 | 10.5147 | 7.0304 | 6930.4131 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-065 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.0904 | 3.1309 | 3030.8669 | 19.8 | 22.67 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.0904 | 0.3625 | 262.484 | 151.2 | 170 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 3.0904 | 0.3625 | 262.484 | 151.2 | 170 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.0313 | 0.2618 | 161.7631 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.0313 | 0.2618 | 161.7631 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 17.5627 | 0.3179 | 217.8816 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 2.2865 | 0.2506 | 150.6008 | 221.4 | 251.1 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 2.2865 | 0.3028 | 202.8435 | 201.6 | 226.8 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 9.0268 | 0.1729 | 72.9492 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 35.1945 | 0.6185 | 518.5455 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763443 [G18-131-TAP 345.00] CKT 1 | 10.0313 | 7.1755 | 7075.5188 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.0445 | 0.3028 | 202.8111 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.0445 | 0.3028 | 202.8111 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7119 | 0.2735 | 173.5383 | 125 | 141 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7119 | 0.2735 | 173.5383 | 125 | 141 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 17.5411 | 0.3179 | 217.8914 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.0271 | 0.1888 | 88.8486 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.0271 | 0.2212 | 121.1592 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.7775 | 0.1713 | 71.3044 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 34.6843 | 0.6184 | 518.4103 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7119 | 7.7304 | 7630.4221 | 100 | 113.4 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7119 | 4.1806 | 4080.5738 | 50 | 58.8 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 4.7119 | 7.7304 | 7630.4221 | 100 | 113.4 | FAIL | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 12.2489 | 0.2997 | 199.7305 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 12.2489 | 0.2997 | 199.7305 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.4719 | 0.2614 | 161.4406 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.4719 | 0.2614 | 161.4406 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 17.5751 | 0.3179 | 217.8786 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.0347 | 0.1917 | 91.6669 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.0347 | 0.2247 | 124.7065 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 9.0915 | 0.1706 | 70.6426 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 35.2067 | 0.6186 | 518.5633 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640230 [HOSK.T89 34.500] CKT 1 | 10.4719 | 7.0316 | 6931.5846 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 11.6423 | 0.3001 | 200.1315 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 11.6423 | 0.3001 | 200.1315 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.8724 | 0.2617 | 161.6861 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.8724 | 0.2617 | 161.6861 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 17.5775 | 0.3179 | 217.8763 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.4791 | 0.1926 | 92.6275 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.4791 | 0.2261 | 126.0522 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.0594 | 0.1707 | 70.6584 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 35.1802 | 0.6185 | 518.5435 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.8724 | 7.0581 | 6958.073 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.8724 | 3.9707 | 3870.7113 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640560 [WAKEFIELD 4230.00] CKT 1 | 9.8724 | 7.0581 | 6958.073 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 12.291 | 0.2996 | 199.5618 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 12.291 | 0.2996 | 199.5618 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.5176 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.5176 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 17.582 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.0735 | 0.1921 | 92.123 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.0735 | 0.2253 | 125.3158 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 9.0935 | 0.1706 | 70.5973 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 35.2262 | 0.6186 | 518.5573 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640227 [HOSKINS4 230.00] TO BUS 640228 [HOSKINS7 115.00] TO BUS 643083 [HOSKINS T1 913.800] CKT 1 | 10.5176 | 7.0317 | 6931.7055 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 12.1635 | 0.2997 | 199.7269 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 12.1635 | 0.2997 | 199.7269 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.3801 | 0.2614 | 161.4437 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.3801 | 0.2614 | 161.4437 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 17.5814 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 9.9539 | 0.1921 | 92.1045 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 9.9539 | 0.2253 | 125.3037 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 9.0865 | 0.1706 | 70.5938 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 35.2141 | 0.6186 | 518.5567 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640080 [BELDEN 7 115.00] CKT 1 | 10.3801 | 7.0349 | 6934.8623 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5617 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5617 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.5138 | 0.2614 | 161.3547 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.5138 | 0.2614 | 161.3547 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.0738 | 0.1921 | 92.0836 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.0738 | 0.2253 | 125.2627 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 9.0956 | 0.1706 | 70.5815 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 35.2269 | 0.6186 | 518.5584 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640296 [NORFK.N7 115.00] CKT 1 | 10.5138 | 7.0303 | 6930.2528 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2875 | 0.2996 | 199.5708 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2875 | 0.2996 | 199.5708 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5096 | 0.2613 | 161.3498 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5096 | 0.2613 | 161.3498 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 17.5796 | 0.3179 | 217.8761 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.069 | 0.1921 | 92.0994 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.069 | 0.2253 | 125.2845 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.0953 | 0.1706 | 70.5789 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 34.3464 | 0.6185 | 518.529 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5096 | 7.0302 | 6930.2199 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 12.2884 | 0.2996 | 199.5729 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 12.2884 | 0.2996 | 199.5729 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.5107 | 0.2614 | 161.3533 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.5107 | 0.2614 | 161.3533 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 17.5816 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.0687 | 0.1921 | 92.095 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.0687 | 0.2253 | 125.2787 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 9.0876 | 0.1706 | 70.63 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 35.2256 | 0.6186 | 518.5569 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640298 [NORFOLK7 115.00] CKT 1 | 10.5107 | 7.0322 | 6932.1804 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 12.1514 | 0.2998 | 199.7543 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 12.1514 | 0.2998 | 199.7543 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.393 | 0.2614 | 161.4398 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.393 | 0.2614 | 161.4398 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 17.5798 | 0.3179 | 217.8761 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 9.9478 | 0.192 | 91.9854 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 9.9478 | 0.2251 | 125.1436 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 9.0911 | 0.1706 | 70.6191 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 35.2172 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640363 [STNTN.N7 115.00] CKT 1 | 10.393 | 7.0351 | 6935.0818 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 12.2922 | 0.2996 | 199.568 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 12.2922 | 0.2996 | 199.568 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.5164 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.5164 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 17.582 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.0732 | 0.1922 | 92.1642 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.0732 | 0.2254 | 125.3721 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 9.0977 | 0.1706 | 70.589 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 35.2263 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643085 [HOSKINS T3 913.800] CKT 1 | 10.5164 | 7.0325 | 6932.4869 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 12.2928 | 0.2996 | 199.568 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 12.2928 | 0.2996 | 199.568 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.5168 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.5168 | 0.2613 | 161.3475 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 17.5821 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.0737 | 0.1922 | 92.1654 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.0737 | 0.2254 | 125.3733 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 9.0979 | 0.1706 | 70.5891 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 35.2267 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640228 [HOSKINS7 115.00] TO BUS 640229 [HOSKINS9 34.500] TO BUS 643086 [HOSKINS T6 913.800] CKT 1 | 10.5168 | 7.0325 | 6932.5242 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 12.2888 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 12.2888 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.5125 | 0.2613 | 161.3491 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.5125 | 0.2613 | 161.3491 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 17.5764 | 0.3179 | 217.878 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.0702 | 0.1921 | 92.0923 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.0702 | 0.2253 | 125.2749 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 9.0976 | 0.1706 | 70.5667 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 35.1484 | 0.6186 | 518.5638 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 646398 [S1398 5 161.00] CKT 1 | 10.5125 | 7.0294 | 6929.428 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 12.2901 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 12.2901 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.5143 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.5143 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 17.5807 | 0.3179 | 217.8766 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.0714 | 0.1921 | 92.0979 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.0714 | 0.2253 | 125.2824 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 9.0977 | 0.1706 | 70.5771 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 35.0317 | 0.6186 | 518.6219 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 640235 [HUMBOLT7 115.00] TO BUS 643087 [HUMBOLDT T2913.800] CKT 1 | 10.5143 | 7.03 | 6930.0451 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.5147 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.5147 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.0715 | 0.1921 | 92.0994 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.0715 | 0.2253 | 125.2844 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 9.0979 | 0.1706 | 70.5817 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 35.2241 | 0.6186 | 518.5531 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640234 [HUMBOLT5 161.00] TO BUS 647975 [S975 8 69.000] TO BUS 648275 [S975T4 9 13.800] CKT 1 | 10.5147 | 7.0304 | 6930.4091 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 12.2888 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 12.2888 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.5123 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.5123 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 17.2483 | 0.3182 | 218.1835 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.0703 | 0.1921 | 92.0953 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.0703 | 0.2253 | 125.2789 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 9.0968 | 0.1706 | 70.5795 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 35.2138 | 0.6186 | 518.5538 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT 1 | 10.5123 | 7.0313 | 6931.3496 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 17.5559 | 0.3179 | 217.9218 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.0715 | 0.1921 | 92.0981 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.0715 | 0.2253 | 125.2825 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 9.098 | 0.1706 | 70.5794 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 35.2259 | 0.6186 | 518.5588 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640252 [KEYSTON3 345.00] TO BUS 640253 [KEYSTON7 115.00] TO BUS 640254 [KEYSTON9 13.800] CKT 1 | 10.5147 | 7.0303 | 6930.2913 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.2898 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.2898 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5106 | 0.2614 | 161.3508 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5106 | 0.2614 | 161.3508 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 17.1509 | 0.3181 | 218.1322 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.0709 | 0.1923 | 92.2742 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.0709 | 0.2255 | 125.5202 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 9.0819 | 0.1709 | 70.8655 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.227 | 0.6183 | 518.2863 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5106 | 7.0465 | 6946.4623 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2882 | 0.2996 | 199.5709 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2882 | 0.2996 | 199.5709 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5108 | 0.2613 | 161.3498 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5108 | 0.2613 | 161.3498 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 17.58 | 0.3179 | 217.8763 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.0696 | 0.1921 | 92.1056 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.0696 | 0.2253 | 125.2929 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.0957 | 0.1706 | 70.5902 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 34.6228 | 0.6187 | 518.6786 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640111 [CLATONA7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5108 | 7.0309 | 6930.9246 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.2807 | 0.2996 | 199.5752 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.2807 | 0.2996 | 199.5752 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.4888 | 0.2614 | 161.3615 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.4888 | 0.2614 | 161.3615 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 17.2656 | 0.318 | 218.0317 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.0624 | 0.1924 | 92.3867 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.0624 | 0.2257 | 125.6729 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 9.0746 | 0.1711 | 71.125 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 34.0522 | 0.6181 | 518.0974 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.4888 | 7.0591 | 6959.1341 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 12.1946 | 0.2996 | 199.6413 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 12.1946 | 0.2996 | 199.6413 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.3154 | 0.2615 | 161.4711 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.3154 | 0.2615 | 161.4711 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 17.5624 | 0.3179 | 217.8899 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.9837 | 0.1921 | 92.076 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.9837 | 0.2253 | 125.2603 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 9.0492 | 0.1706 | 70.5639 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 34.5626 | 0.6186 | 518.5835 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.3154 | 7.0307 | 6930.6642 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 12.289 | 0.2996 | 199.5702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 12.289 | 0.2996 | 199.5702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.5107 | 0.2613 | 161.3495 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.5107 | 0.2613 | 161.3495 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 17.5113 | 0.3179 | 217.9145 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.0704 | 0.1921 | 92.1496 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.0704 | 0.2254 | 125.3521 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 9.0923 | 0.1706 | 70.6464 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 33.4423 | 0.6184 | 518.3804 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.5107 | 7.0342 | 6934.1687 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5146 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5146 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 17.5819 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.0715 | 0.1921 | 92.0951 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.0715 | 0.2253 | 125.2786 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 33.8264 | 0.6187 | 518.7085 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5146 | 7.03 | 6929.9994 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5146 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5146 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 17.5819 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.0715 | 0.1921 | 92.0951 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.0715 | 0.2253 | 125.2786 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 33.8264 | 0.6187 | 518.7085 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5146 | 7.03 | 6929.9994 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 12.2859 | 0.2996 | 199.5679 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 12.2859 | 0.2996 | 199.5679 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.5003 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.5003 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 16.9388 | 0.3185 | 218.4601 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.0672 | 0.1926 | 92.5674 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.0672 | 0.2259 | 125.9155 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 9.0676 | 0.1714 | 71.4277 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 35.0529 | 0.6185 | 518.5405 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 531451 [MINGO 7 345.00] CKT 1 | 10.5003 | 7.0678 | 6967.8081 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.2901 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.2901 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.5144 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.5144 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 17.5851 | 0.3179 | 217.8762 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.0714 | 0.1921 | 92.1047 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.0714 | 0.2253 | 125.2916 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 9.0974 | 0.1706 | 70.5927 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 35.2241 | 0.6186 | 518.5549 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.5144 | 7.0309 | 6930.8543 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.2516 | 0.2996 | 199.6071 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 12.2516 | 0.2996 | 199.6071 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.4493 | 0.2614 | 161.3937 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.4493 | 0.2614 | 161.3937 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 17.5774 | 0.3179 | 217.8765 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.0369 | 0.1922 | 92.2272 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.0369 | 0.2255 | 125.4597 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 7.4732 | 0.1683 | 68.3176 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 35.1467 | 0.6185 | 518.4982 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640328 [RISNGCY7 115.00] TO BUS 763718 [G19-039-TAP 115.00] CKT 1 | 10.4493 | 7.0408 | 6940.8231 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 12.2836 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 12.2836 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.5042 | 0.2613 | 161.3493 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.5042 | 0.2613 | 161.3493 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 17.5734 | 0.3179 | 217.8794 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.0656 | 0.1921 | 92.1085 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.0656 | 0.2253 | 125.2969 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 8.5643 | 0.1701 | 70.1177 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 35.1095 | 0.6186 | 518.5958 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640316 [PAWNEEL7 115.00] CKT 1 | 10.5042 | 7.0306 | 6930.6021 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 12.2862 | 0.2996 | 199.5737 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 12.2862 | 0.2996 | 199.5737 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.5068 | 0.2614 | 161.3537 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.5068 | 0.2614 | 161.3537 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 17.5638 | 0.3179 | 217.8881 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.0678 | 0.1921 | 92.1022 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.0678 | 0.2253 | 125.2886 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 8.9263 | 0.1705 | 70.5184 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 35.2099 | 0.6186 | 518.5569 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640375 [TAMORA 7 115.00] CKT 1 | 10.5068 | 7.0308 | 6930.8375 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.571 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.571 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.5094 | 0.2614 | 161.3562 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.5094 | 0.2614 | 161.3562 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 17.5817 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.0713 | 0.1921 | 92.0803 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.0713 | 0.2253 | 125.2586 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 7.5151 | 0.1697 | 69.7195 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 35.2264 | 0.6186 | 518.5564 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640124 [COL.SE 7 115.00] CKT 1 | 10.5094 | 7.0285 | 6928.4768 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.5146 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.5146 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 17.5817 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.0714 | 0.1921 | 92.1024 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.0714 | 0.2253 | 125.2885 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 9.0971 | 0.1706 | 70.6185 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 35.2258 | 0.6186 | 518.559 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643134 [SEWARD T1 913.800] CKT 1 | 10.5146 | 7.0307 | 6930.7081 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 12.2902 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.5146 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.5146 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 17.5817 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.0714 | 0.1921 | 92.1027 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.0714 | 0.2253 | 125.2888 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 9.0971 | 0.1706 | 70.6207 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 35.2257 | 0.6186 | 518.5591 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640340 [SEWARD 7 115.00] TO BUS 640341 [SEWARD 9 34.500] TO BUS 643135 [SEWARD T2 913.800] CKT 1 | 10.5146 | 7.0307 | 6930.7321 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.0231 | 0.302 | 201.968 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 10.0231 | 0.302 | 201.968 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.3581 | 0.2662 | 166.1506 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.3581 | 0.2662 | 166.1506 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 17.5425 | 0.3179 | 217.8965 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.009 | 0.1932 | 93.1769 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.009 | 0.2269 | 126.9437 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 8.7811 | 0.1716 | 71.5641 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 34.7479 | 0.6183 | 518.3095 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.3581 | 7.0777 | 6977.6613 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.3581 | 3.9815 | 3881.4946 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640342 [SHELCRK3 345.00] TO BUS 763982 [G19-069-TAP 345.00] CKT 1 | 6.3581 | 7.0777 | 6977.6613 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 12.0681 | 0.2998 | 199.8375 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 12.0681 | 0.2998 | 199.8375 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.9414 | 0.2619 | 161.9042 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.9414 | 0.2619 | 161.9042 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 17.5652 | 0.3179 | 217.8851 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.8623 | 0.1916 | 91.636 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.8623 | 0.2247 | 124.68 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 8.975 | 0.1711 | 71.0913 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 35.2203 | 0.6186 | 518.562 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.9414 | 6.9898 | 6889.7908 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.9414 | 3.9507 | 3850.7351 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640343 [SHELCRK4 230.00] TO BUS 640133 [COLMBUS4 230.00] CKT 1 | 9.9414 | 6.9898 | 6889.7908 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 12.2895 | 0.2996 | 199.5709 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 12.2895 | 0.2996 | 199.5709 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.5138 | 0.2613 | 161.3494 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.5138 | 0.2613 | 161.3494 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 17.5807 | 0.3179 | 217.8767 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.0708 | 0.1921 | 92.0704 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.0708 | 0.2252 | 125.2453 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 9.0986 | 0.1705 | 70.5254 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 34.6192 | 0.6187 | 518.7223 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640362 [STERLNG7 115.00] TO BUS 647974 [S974 8 69.000] TO BUS 643144 [STERLING T1913.800] CKT 1 | 10.5138 | 7.0268 | 6926.8152 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.2856 | 0.2996 | 199.5708 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 12.2856 | 0.2996 | 199.5708 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.5039 | 0.2614 | 161.3509 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.5039 | 0.2614 | 161.3509 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.9185 | 0.331 | 230.9761 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.0671 | 0.1922 | 92.1557 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.0671 | 0.2254 | 125.3605 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 9.0876 | 0.1707 | 70.7013 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 35.1063 | 0.6185 | 518.5189 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.5039 | 7.0372 | 6937.2012 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 12.2887 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 12.2887 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.5108 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.5108 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 17.4429 | 0.3181 | 218.0864 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.07 | 0.1921 | 92.09 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.07 | 0.2253 | 125.2717 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 9.0956 | 0.1706 | 70.5615 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 35.1926 | 0.6186 | 518.5553 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640510 [HOLT.CO3 345.00] CKT 1 | 10.5108 | 7.0294 | 6929.369 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 12.2818 | 0.2996 | 199.5741 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 12.2818 | 0.2996 | 199.5741 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.5125 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.5125 | 0.2613 | 161.3488 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 17.5555 | 0.3179 | 217.9282 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.0655 | 0.1921 | 92.0838 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.0655 | 0.2253 | 125.2635 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 9.0982 | 0.1706 | 70.574 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 35.2231 | 0.6186 | 518.5595 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640500 [THEDFRD3 345.00] TO BUS 640381 [THEDFRD7 115.00] TO BUS 640570 [THEDFORD9 13.800] CKT 1 | 10.5125 | 7.0291 | 6929.0756 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 11.0293 | 0.3027 | 202.6901 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 11.0293 | 0.3027 | 202.6901 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.3308 | 0.2616 | 161.6099 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.3308 | 0.2616 | 161.6099 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 17.5833 | 0.3179 | 217.8746 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.2447 | 0.2039 | 103.9041 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.2447 | 0.2411 | 141.0504 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 9.0968 | 0.1706 | 70.6307 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 35.222 | 0.6186 | 518.5593 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640520 [ANTELOPE 3345.00] TO BUS 763031 [G18-065-TAP 345.00] CKT 1 | 10.3308 | 7.1313 | 7031.2921 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 12.1751 | 0.2997 | 199.7396 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 12.1751 | 0.2997 | 199.7396 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.5127 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.5127 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 17.5813 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.0184 | 0.1922 | 92.1525 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.0184 | 0.2254 | 125.3618 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 9.097 | 0.1706 | 70.5928 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 35.226 | 0.6186 | 518.5575 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640115 [CO.LINE7 115.00] CKT 1 | 10.5127 | 7.0343 | 6934.3062 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 12.2877 | 0.2996 | 199.572 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 12.2877 | 0.2996 | 199.572 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.5149 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.5149 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 17.5823 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.0696 | 0.1921 | 92.0856 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.0696 | 0.2253 | 125.2659 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 8.3143 | 0.1704 | 70.3556 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 35.2209 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640124 [COL.SE 7 115.00] TO BUS 640136 [COLMBUS7 115.00] CKT 1 | 10.5149 | 7.0298 | 6929.8146 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 11.9449 | 0.3001 | 200.0557 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 11.9449 | 0.3001 | 200.0557 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.4023 | 0.2614 | 161.4189 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.4023 | 0.2614 | 161.4189 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 17.5811 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.8236 | 0.1922 | 92.1896 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.8236 | 0.2254 | 125.4344 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 9.0873 | 0.1706 | 70.6318 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 35.213 | 0.6186 | 518.5575 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640149 [CREITON7 115.00] CKT 1 | 10.4023 | 7.042 | 6941.969 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 12.249 | 0.2997 | 199.6702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 12.249 | 0.2997 | 199.6702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.5052 | 0.2614 | 161.3601 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.5052 | 0.2614 | 161.3601 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 17.5818 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.0423 | 0.1921 | 92.0916 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.0423 | 0.2253 | 125.2786 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 9.0982 | 0.1706 | 70.5665 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 35.227 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 1 | 10.5052 | 7.0314 | 6931.4162 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 12.2327 | 0.2997 | 199.707 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 12.2327 | 0.2997 | 199.707 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.5013 | 0.2614 | 161.3644 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.5013 | 0.2614 | 161.3644 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 17.5817 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.0307 | 0.1921 | 92.0894 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.0307 | 0.2253 | 125.2776 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 9.0982 | 0.1706 | 70.5618 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 35.2271 | 0.6186 | 518.5587 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640293 [NELIGH 7 115.00] CKT 2 | 10.5013 | 7.0318 | 6931.8462 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 12.2549 | 0.2998 | 199.8298 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 12.2549 | 0.2998 | 199.8298 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.5222 | 0.2614 | 161.3912 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.5222 | 0.2614 | 161.3912 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 17.5883 | 0.3179 | 217.8734 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.0555 | 0.1976 | 97.5645 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.0555 | 0.2326 | 132.6094 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 9.1004 | 0.1706 | 70.5566 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 35.2362 | 0.6186 | 518.5527 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 643254 [UPSTREAM.W 7115.00] CKT 1 | 10.5222 | 7.057 | 6957.0053 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 12.2725 | 0.2996 | 199.6232 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 12.2725 | 0.2996 | 199.6232 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.506 | 0.2614 | 161.3583 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.506 | 0.2614 | 161.3583 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 17.5809 | 0.3179 | 217.8761 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.0579 | 0.1921 | 92.1302 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.0579 | 0.2253 | 125.3278 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 9.0965 | 0.1706 | 70.6013 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 35.2234 | 0.6186 | 518.559 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640521 [ANTELOPE 7115.00] TO BUS 640522 [ANTELOPE 869.000] TO BUS 643182 [ANTELOPE.T2913.800] CKT 1 | 10.506 | 7.0337 | 6933.7339 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 12.3141 | 0.2999 | 199.9265 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 12.3141 | 0.2999 | 199.9265 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.5443 | 0.2616 | 161.567 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.5443 | 0.2616 | 161.567 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 17.5918 | 0.3179 | 217.8722 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.0932 | 0.1921 | 92.0633 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.0932 | 0.2253 | 125.2725 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 9.1047 | 0.1704 | 70.4341 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 35.2467 | 0.6185 | 518.5448 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640589 [SHOLES.W 3345.00] CKT 1 | 10.5443 | 7.0171 | 6917.0824 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 12.316 | 0.3002 | 200.2281 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 12.316 | 0.3002 | 200.2281 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.5457 | 0.2618 | 161.7505 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.5457 | 0.2618 | 161.7505 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 17.59 | 0.3179 | 217.8734 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.095 | 0.1917 | 91.7197 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.095 | 0.2248 | 124.8344 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 9.1042 | 0.1704 | 70.4395 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 35.2436 | 0.6185 | 518.5376 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 640598 [HAYSTACK.WD3345.00] CKT 1 | 10.5457 | 7.0138 | 6913.821 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 12.2865 | 0.2996 | 199.5731 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 12.2865 | 0.2996 | 199.5731 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.511 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.511 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.068 | 0.192 | 92.0338 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.068 | 0.2252 | 125.1961 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 9.098 | 0.1706 | 70.5754 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 35.2264 | 0.6186 | 518.5585 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640588 [TURTLE.CRK 3345.00] TO BUS 643271 [PLUMBCR.W 3345.00] CKT 1 | 10.511 | 7.0283 | 6928.2607 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 12.2889 | 0.2996 | 199.5719 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 12.2889 | 0.2996 | 199.5719 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.514 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.514 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 17.5829 | 0.3179 | 217.8769 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.0703 | 0.192 | 92.0219 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.0703 | 0.2252 | 125.1799 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 9.0995 | 0.1705 | 70.5296 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 31.104 | 0.6183 | 518.3169 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640596 [MONOLITHT1 913.800] CKT 1 | 10.514 | 7.0227 | 6922.7351 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 12.2889 | 0.2996 | 199.5719 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 12.2889 | 0.2996 | 199.5719 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.514 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.514 | 0.2614 | 161.3502 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 17.5829 | 0.3179 | 217.8769 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.0703 | 0.192 | 92.0219 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.0703 | 0.2252 | 125.1799 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 9.0995 | 0.1705 | 70.5296 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 31.104 | 0.6183 | 518.3169 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640590 [MONOLITH 3 345.00] TO BUS 640591 [MONOLITH 7 115.00] TO BUS 640597 [MONOLITHT2 913.800] CKT 1 | 10.514 | 7.0227 | 6922.7348 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 11.3005 | 0.3006 | 200.5526 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 11.3005 | 0.3006 | 200.5526 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.4449 | 0.2632 | 163.2358 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.4449 | 0.2632 | 163.2358 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 17.5725 | 0.3179 | 217.8807 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.1625 | 0.1931 | 93.0592 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.1625 | 0.2267 | 126.6616 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 9.0504 | 0.171 | 70.9636 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 34.7732 | 0.6184 | 518.4034 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-069 | Shell Creek-Hoskins 345kV Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.4449 | 7.1229 | 7022.8928 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-070 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.4449 | 3.9898 | 3889.8277 | 50 | 58.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640125 [COLMB.E3 345.00] TO BUS 640342 [SHELCRK3 345.00] CKT 1 | 8.4449 | 7.1229 | 7022.8928 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 17.5813 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.0716 | 0.1921 | 92.1208 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.0716 | 0.2253 | 125.3133 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 9.0968 | 0.1706 | 70.6175 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 35.2569 | 0.6186 | 518.5813 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 | 10.5145 | 7.0325 | 6932.5495 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 17.5813 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.0716 | 0.1921 | 92.1208 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.0716 | 0.2253 | 125.3133 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 9.0968 | 0.1706 | 70.6175 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 35.2569 | 0.6186 | 518.5813 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 2 | 10.5145 | 7.0325 | 6932.5495 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 12.2904 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.5145 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 17.5813 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.0716 | 0.1921 | 92.1208 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.0716 | 0.2253 | 125.3133 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 9.0968 | 0.1706 | 70.6175 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 35.2569 | 0.6186 | 518.5813 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640593 [MONOLITH 9 34.500] TO BUS 640591 [MONOLITH 7 115.00] CKT 3 | 10.5145 | 7.0325 | 6932.5495 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.2902 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 17.5817 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.0714 | 0.1921 | 92.098 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.0714 | 0.2253 | 125.2825 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 9.0981 | 0.1706 | 70.5805 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 35.2045 | 0.6186 | 518.5665 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646258 [S1258 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5147 | 7.0304 | 6930.3893 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.2901 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 12.2901 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5145 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5145 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 17.5816 | 0.3179 | 217.8758 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.0713 | 0.1921 | 92.0966 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.0713 | 0.2253 | 125.2806 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-009 | S1263 Brock 161kV substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 8.0697 | 9.7744 | 9674.3595 | 100 | 114.88 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 35.2238 | 0.6186 | 518.5539 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646280 [S1280 5 161.00] TO BUS 646263 [S1263 5 161.00] CKT 1 | 10.5145 | 7.0304 | 6930.3775 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 17.5818 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.0715 | 0.1921 | 92.0978 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.0715 | 0.2253 | 125.2821 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 9.098 | 0.1706 | 70.5803 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 35.2182 | 0.6186 | 518.5584 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 646244 [S1244 5 161.00] CKT 1 | 10.5147 | 7.0304 | 6930.4083 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 12.2903 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 12.2903 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.5148 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.5148 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.0716 | 0.1921 | 92.0979 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.0716 | 0.2253 | 125.2823 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 9.0981 | 0.1706 | 70.5791 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 35.2266 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 646366 [S1366 5 161.00] TO BUS 647866 [S6866 8 69.000] TO BUS 648266 [S1366T29 13.800] CKT 1 | 10.5148 | 7.0303 | 6930.2619 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.5144 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.5144 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 17.5817 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.0715 | 0.1921 | 92.11 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.0715 | 0.2253 | 125.2986 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 9.0972 | 0.1706 | 70.6014 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 35.1518 | 0.6185 | 518.5068 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647111 [W BROCK8 69.000] TO BUS 646263 [S1263 5 161.00] TO BUS 648263 [S1263T19 13.800] CKT 1 | 10.5144 | 7.0316 | 6931.5953 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.5147 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 17.5819 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.0715 | 0.1921 | 92.0972 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.0715 | 0.2253 | 125.2814 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 9.0981 | 0.1706 | 70.5782 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 35.2242 | 0.6186 | 518.5596 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647101 [AUBRNT 8 69.000] CKT 1 | 10.5147 | 7.0302 | 6930.2267 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 17.5821 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.0716 | 0.1921 | 92.0975 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.0716 | 0.2253 | 125.2818 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 9.0981 | 0.1706 | 70.5785 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 35.2265 | 0.6186 | 518.5596 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647973 [S973 8 69.000] CKT 1 | 10.5148 | 7.0302 | 6930.2225 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.2586 | 0.2996 | 199.5827 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 12.2586 | 0.2996 | 199.5827 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.4515 | 0.2614 | 161.3708 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.4515 | 0.2614 | 161.3708 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 17.5019 | 0.3179 | 217.9124 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.0428 | 0.1922 | 92.2389 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.0428 | 0.2255 | 125.4743 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 9.0608 | 0.1707 | 70.7236 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 32.7786 | 0.6179 | 517.922 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.4515 | 7.0397 | 6939.6692 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 12.2904 | 0.2996 | 199.5698 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 12.2904 | 0.2996 | 199.5698 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.5148 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.5148 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 17.5822 | 0.3179 | 217.8754 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.0716 | 0.1921 | 92.1063 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.0716 | 0.2253 | 125.2936 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 9.0976 | 0.1706 | 70.5928 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 35.2213 | 0.6185 | 518.5462 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647963 [S963 8 69.000] TO BUS 647977 [S977 8 69.000] CKT 1 | 10.5148 | 7.031 | 6930.9892 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 12.29 | 0.2996 | 199.5702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 12.29 | 0.2996 | 199.5702 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.5142 | 0.2613 | 161.3486 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.5142 | 0.2613 | 161.3486 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 17.5816 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.0712 | 0.1921 | 92.0932 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.0712 | 0.2253 | 125.276 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 9.0979 | 0.1706 | 70.571 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 35.0516 | 0.6185 | 518.5318 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 647967 [S967 8 69.000] TO BUS 647968 [S968 8 69.000] CKT 1 | 10.5142 | 7.0298 | 6929.7835 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.0716 | 0.1921 | 92.0978 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.0716 | 0.2253 | 125.2822 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 35.2266 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648605 [NC1HS1X9 4.2000] TO BUS 648606 [NC1HS1Y9 4.2000] CKT 1 | 10.5148 | 7.0303 | 6930.2695 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.0716 | 0.1921 | 92.0978 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.0716 | 0.2253 | 125.2822 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 35.2266 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648600 [NC1HS 5 161.00] TO BUS 648607 [NC1HS2X9 4.2000] TO BUS 648608 [NC1HS2Y9 4.2000] CKT 1 | 10.5148 | 7.0303 | 6930.2691 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.0716 | 0.1921 | 92.0979 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.0716 | 0.2253 | 125.2823 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 9.0981 | 0.1706 | 70.5792 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 35.2266 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648615 [NC2HS1X9 13.800] TO BUS 648616 [NC2HS1Y9 13.800] CKT 1 | 10.5148 | 7.0303 | 6930.2725 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 12.2903 | 0.2996 | 199.5701 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.5148 | 0.2613 | 161.3485 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 17.5821 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.0716 | 0.1921 | 92.0978 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.0716 | 0.2253 | 125.2822 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 9.0981 | 0.1706 | 70.5791 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 35.2267 | 0.6186 | 518.5586 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 648610 [NC2HS 5 161.00] TO BUS 648617 [NC2HS2X9 4.2000] TO BUS 648618 [NC2HS2Y9 4.2000] CKT 1 | 10.5148 | 7.0303 | 6930.2655 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.5141 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.5141 | 0.2613 | 161.3482 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 17.5816 | 0.3179 | 217.876 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.0714 | 0.1921 | 92.1192 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.0714 | 0.2253 | 125.3111 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 9.0956 | 0.1706 | 70.6347 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 34.6551 | 0.6188 | 518.7709 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650238 [20PIONEERS7 115.00] CKT 1 | 10.5141 | 7.0323 | 6932.314 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 12.2899 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 12.2899 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.5137 | 0.2613 | 161.3489 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.5137 | 0.2613 | 161.3489 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 17.582 | 0.3179 | 217.8755 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.0711 | 0.1921 | 92.1029 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.0711 | 0.2253 | 125.2891 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 9.0947 | 0.1706 | 70.5981 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 35.1305 | 0.6186 | 518.5736 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650290 [ROKEBY 7 115.00] CKT 1 | 10.5137 | 7.0308 | 6930.7808 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 12.2903 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 12.2903 | 0.2996 | 199.5703 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.5148 | 0.2613 | 161.3486 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.5148 | 0.2613 | 161.3486 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 17.582 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.0715 | 0.1921 | 92.0948 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.0715 | 0.2253 | 125.2781 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 9.0983 | 0.1706 | 70.5712 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 35.225 | 0.6186 | 518.5701 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650242 [FOLSM&PHIL7 115.00] TO BUS 650342 [FOLSM&PHIL9 12.470] TO BUS 650542 [421TERTIARY 7.2000] CKT 1 | 10.5148 | 7.0299 | 6929.8898 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 12.2902 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.5143 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.5143 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 17.5819 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.0714 | 0.1921 | 92.1098 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.0714 | 0.2253 | 125.2984 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 9.0964 | 0.1706 | 70.6119 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 34.9164 | 0.6187 | 518.6626 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 650246 [SW7&BENNET7 115.00] TO BUS 650247 [40&BENNET 7 115.00] CKT 1 | 10.5143 | 7.0314 | 6931.4364 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.2905 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 12.2905 | 0.2996 | 199.57 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.515 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.515 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 17.5819 | 0.3179 | 217.8756 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.0717 | 0.1921 | 92.0967 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.0717 | 0.2253 | 125.2807 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 9.0982 | 0.1706 | 70.5783 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 35.2114 | 0.6186 | 518.5541 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640140 [COOPER 5 161.00] TO BUS 646280 [S1280 5 161.00] CKT 1 | 10.515 | 7.0301 | 6930.1001 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.29 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 12.29 | 0.2996 | 199.5697 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5118 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5118 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 17.0633 | 0.3183 | 218.3241 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.0711 | 0.1922 | 92.2226 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.0711 | 0.2255 | 125.4506 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 9.0883 | 0.1709 | 70.8668 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.1468 | 0.6184 | 518.3729 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.5118 | 7.0417 | 6941.6993 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 12.2845 | 0.2996 | 199.5726 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 12.2845 | 0.2996 | 199.5726 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.4931 | 0.2614 | 161.3575 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.4931 | 0.2614 | 161.3575 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 17.4901 | 0.318 | 217.9597 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.0657 | 0.1923 | 92.2525 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.0657 | 0.2255 | 125.4916 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 9.0711 | 0.1709 | 70.895 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 34.974 | 0.6184 | 518.4369 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.4931 | 7.0509 | 6950.9236 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 12.2887 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 12.2887 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.5116 | 0.2614 | 161.35 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.5116 | 0.2614 | 161.35 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 17.5682 | 0.3179 | 217.8929 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.0701 | 0.1921 | 92.1061 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.0701 | 0.2253 | 125.2936 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 9.0948 | 0.1706 | 70.5944 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 35.2212 | 0.6186 | 518.5608 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.5116 | 7.0313 | 6931.2948 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 12.2887 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 12.2887 | 0.2996 | 199.5711 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.5117 | 0.2614 | 161.35 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.5117 | 0.2614 | 161.35 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 17.5684 | 0.3179 | 217.8927 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.0701 | 0.1921 | 92.106 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.0701 | 0.2253 | 125.2934 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 9.0948 | 0.1706 | 70.5942 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 35.2213 | 0.6186 | 518.5608 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.5117 | 7.0313 | 6931.2853 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 12.288 | 0.2996 | 199.5715 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 12.288 | 0.2996 | 199.5715 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.5102 | 0.2614 | 161.3507 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.5102 | 0.2614 | 161.3507 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 17.5622 | 0.3179 | 217.9001 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.0694 | 0.1921 | 92.1101 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.0694 | 0.2253 | 125.299 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 9.0933 | 0.1706 | 70.6018 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 35.2187 | 0.6186 | 518.5617 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.5102 | 7.0318 | 6931.7761 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 12.2915 | 0.2996 | 199.5722 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 12.2915 | 0.2996 | 199.5722 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.5188 | 0.2613 | 161.3491 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.5188 | 0.2613 | 161.3491 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 17.594 | 0.3179 | 217.8711 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.0727 | 0.1918 | 91.8478 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.0727 | 0.2249 | 124.9447 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 35.2568 | 0.6186 | 518.5638 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 763713 [G19-039-TER113.800] TO BUS 763714 [GEN-2019-039115.00] TO BUS 763715 [G19-039-XFM134.500] CKT 1 | 10.5188 | 7.0154 | 6915.3718 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 12.2899 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 12.2899 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.5135 | 0.2613 | 161.3497 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.5135 | 0.2613 | 161.3497 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 17.5741 | 0.3179 | 217.8775 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.0712 | 0.1921 | 92.1454 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.0712 | 0.2253 | 125.3465 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 9.0949 | 0.1707 | 70.6638 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 34.6549 | 0.6191 | 519.0651 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640088 [BPS SUB7 115.00] TO BUS 640076 [BEATRCE7 115.00] CKT 1 & 2 | 10.5135 | 7.0335 | 6933.487 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 12.2759 | 0.2996 | 199.597 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 12.2759 | 0.2996 | 199.597 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.4979 | 0.2614 | 161.378 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.4979 | 0.2614 | 161.378 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 17.5792 | 0.3179 | 217.878 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.0587 | 0.1918 | 91.8012 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.0587 | 0.2249 | 124.883 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 9.1004 | 0.1697 | 69.6523 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 35.2134 | 0.6186 | 518.5702 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640119 [COL.COG7 115.00] TO BUS 640122 [COL.DRY7 115.00] CKT 1 & 2 | 10.4979 | 7.0011 | 6901.1022 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 12.2885 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 12.2885 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.5127 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.5127 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 17.5648 | 0.3179 | 217.8974 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.0701 | 0.1921 | 92.0997 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.0701 | 0.2253 | 125.2848 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 9.0968 | 0.1706 | 70.5837 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 35.2184 | 0.6186 | 518.5535 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 2 | 10.5127 | 7.0308 | 6930.7509 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 12.2885 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 12.2885 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.5127 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.5127 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 17.5649 | 0.3179 | 217.8973 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.0701 | 0.1921 | 92.0999 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.0701 | 0.2253 | 125.2851 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 9.0967 | 0.1706 | 70.5841 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 35.2184 | 0.6186 | 518.5535 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 1 & 3 | 10.5127 | 7.0308 | 6930.7687 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2907 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 12.2907 | 0.2996 | 199.5699 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5152 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5152 | 0.2613 | 161.3484 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 17.5703 | 0.3179 | 217.8788 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.0719 | 0.1921 | 92.0998 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.0719 | 0.2253 | 125.2849 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 9.0966 | 0.1706 | 70.6262 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 34.7019 | 0.619 | 519.0458 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640153 [CRETE__7 115.00] TO BUS 640278 [SHELDON7 115.00] CKT 1 | 10.5152 | 7.0306 | 6930.5524 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 12.2886 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 12.2886 | 0.2996 | 199.5705 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.5128 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.5128 | 0.2613 | 161.3487 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 17.566 | 0.3179 | 217.8959 | 231 | 243.3 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-131 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.0701 | 0.1921 | 92.0995 | 221.4 | 251.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-132 | Antelope - Hoskins 345 kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.0701 | 0.2253 | 125.2846 | 201.6 | 226.8 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-039 | Columbus Southeast-Rising City 115kV | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 9.0968 | 0.1706 | 70.5833 | 174.5 | 199.26 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-041 | 115kV Monolith Substation | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 35.2189 | 0.6186 | 518.5539 | 78 | 89.1 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2019-073 | Shell Creek-Hoskins 345kv Line | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640286 [N.PLATT4 230.00] CKT 2 & 3 | 10.5128 | 7.0307 | 6930.7125 | 100 | 113.4 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.2882 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-068 | Antelope - Hoskins 345 kV Substation | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 12.2882 | 0.2996 | 199.5706 | 151.2 | 170 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.5113 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-083 | Shell Creek-Hoskins 345kv Line Break | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 10.5113 | 0.2613 | 161.349 | 125 | 141 | PASS | PASS
02 NEBRASKA | 25WP | TC | GEN-2018-125 | New switching station on Gentleman to Sweetwater 345kV line | OPEN LINE FROM BUS 640278 [SHELDON7 115.00] TO BUS 640591 [MONOLITH 7 115.00] CKT 1 & 2 | 17.5782 | 0.3179 | 217.8757 | 231 | 243.3 | PASS | PASS