Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09193 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09185 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0944 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09409 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09518 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0921 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09203 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09206 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0921 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09183 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09232 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09214 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09497 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09138 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09204 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09214 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0944 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0933 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09163 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09182 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09182 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09193 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09193 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09497 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09541 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09575 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09232 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09208 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09497 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09541 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09575 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09232 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09208 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09228 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09207 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09216 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09222 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09459 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09708 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09216 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09222 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09459 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09708 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08721 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0916 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09356 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09138 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09348 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19618 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19618 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19618 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19618 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19618 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15126 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15286 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15177 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15126 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15983 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15212 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15131 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15137 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15272 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15099 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15076 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15298 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15223 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15242 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15133 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15149 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1513 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15131 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15106 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14245 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15123 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15128 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15155 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15175 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15088 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15326 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15156 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15156 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15093 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15093 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15083 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15083 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15087 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15087 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1516 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15082 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15337 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15244 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14471 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14471 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14832 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15123 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15133 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15046 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15252 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14911 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13842 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15184 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15155 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16194 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15869 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15961 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17026 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15482 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15598 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15176 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18967 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15805 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18949 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15276 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15223 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15136 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15403 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16372 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14979 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15804 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15598 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15288 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15309 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15733 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17434 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15369 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15386 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15733 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15524 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15636 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14245 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15017 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15017 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14992 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13946 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14957 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16928 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15298 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15096 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15037 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15097 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15092 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15108 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15106 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15368 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15336 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15449 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15135 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1506 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15125 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15136 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15368 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15255 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15086 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15475 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1551 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15475 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1551 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1515 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15138 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15144 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15384 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15641 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15138 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15144 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15384 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15641 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14659 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15082 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15244 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1506 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15236 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-011 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05536 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15126 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15286 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15177 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15126 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15983 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15212 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15131 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15137 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15272 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15099 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15076 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15298 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15223 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15242 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15133 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15149 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1513 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15131 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15106 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14245 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13857 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15123 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15128 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15155 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15175 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15089 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15088 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15326 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15156 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15156 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15093 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15093 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15083 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15083 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15087 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15087 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1516 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15082 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15337 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15244 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14471 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14471 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14832 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15123 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15133 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15046 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15827 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15252 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14911 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13842 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1514 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15184 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15155 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16194 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15869 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15961 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15148 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17026 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15482 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15433 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15598 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15176 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18967 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15805 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18949 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15276 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15223 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15136 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15403 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16372 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14979 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15804 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15598 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15288 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15309 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15733 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17434 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15369 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15386 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15733 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15186 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15524 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15636 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14245 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15269 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15112 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15017 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15017 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15147 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15115 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14992 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.13946 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14957 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15094 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15101 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16928 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15298 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15096 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15102 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15037 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15097 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15092 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15108 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15106 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15368 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15336 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15449 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15124 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15127 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15132 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15443 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15135 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1506 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15125 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15136 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15103 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15117 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15368 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15255 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15086 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15104 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15116 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15114 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15475 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1551 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15118 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15122 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15427 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15475 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1551 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15441 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15154 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15113 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15367 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1515 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15119 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1512 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15105 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15129 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15138 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15144 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15384 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15641 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15138 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15144 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15384 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15641 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14659 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15082 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15244 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15121 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1506 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.15236 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-056 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08082 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17725 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17849 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17765 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17774 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17818 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17733 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17724 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17677 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17824 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17727 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17015 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.177 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17716 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17743 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17763 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17677 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17676 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17914 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17681 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17681 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17671 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17671 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17675 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17675 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17748 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1767 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18029 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17925 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17834 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17062 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17062 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17421 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17721 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17634 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17842 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17499 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16437 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17717 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17773 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17743 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17682 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18715 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18671 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18702 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17689 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.195 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18151 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19503 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18095 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17759 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18077 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17713 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18087 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17824 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18118 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19896 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18209 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19237 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19503 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17063 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16984 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18527 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16753 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16688 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18527 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18153 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18275 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17015 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17912 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17912 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1713 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1787 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17684 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17698 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17956 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17924 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18036 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17693 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17649 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17713 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17725 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17956 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17843 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17674 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18063 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18098 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18028 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17718 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18063 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18098 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18028 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17718 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17738 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17717 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17726 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17732 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17972 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18229 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17726 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17732 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17972 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18229 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17247 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1767 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17834 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17649 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17825 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 05NR | 0 | 26L | N/A | FROM->TO | None |  |  |  |  | None
Thermal | 05NR | 1 | 26L | N/A | FROM->TO | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00ALL | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 26SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 26WP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 26SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 26WP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8847 | -0.0208 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9071 | 0.8844 | -0.0227 | 0.9193 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9071 | 0.8844 | -0.0227 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9071 | 0.8844 | -0.0227 | 0.9193 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9071 | 0.8844 | -0.0227 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9071 | 0.8844 | -0.0227 | 0.9193 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | CHESTER-ER8 | 0.9114 | 0.8896 | -0.0218 | 0.9193 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | COLTON-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8853 | 0.8636 | -0.0217 | 0.8996 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8853 | 0.8636 | -0.0217 | 0.8996 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8853 | 0.8636 | -0.0217 | 0.8996 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8853 | 0.8636 | -0.0217 | 0.8996 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8853 | 0.8636 | -0.0217 | 0.8996 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8915 | 0.8689 | -0.0226 | 0.8996 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8854 | 0.8638 | -0.0216 | 0.8996 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8869 | 0.8635 | -0.0234 | 0.8996 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8869 | 0.8635 | -0.0234 | 0.8996 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8869 | 0.8635 | -0.0234 | 0.8996 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8869 | 0.8635 | -0.0234 | 0.8996 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8869 | 0.8635 | -0.0234 | 0.8996 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8854 | 0.8636 | -0.0218 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | DOLTON-ER8 | 0.8852 | 0.8605 | -0.0247 | 0.8996 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9111 | 0.8901 | -0.021 | 0.9251 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9111 | 0.8901 | -0.021 | 0.9251 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9111 | 0.8901 | -0.021 | 0.9251 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8803 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8803 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8803 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8803 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8803 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.9251 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9034 | 0.8803 | -0.0231 | 0.9251 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9034 | 0.8803 | -0.0231 | 0.9251 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9034 | 0.8803 | -0.0231 | 0.9251 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9034 | 0.8803 | -0.0231 | 0.9251 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9034 | 0.8803 | -0.0231 | 0.9251 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8859 | -0.022 | 0.9251 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9019 | 0.8804 | -0.0215 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9079 | 0.8856 | -0.0223 | 0.9251 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | FEDORA-ER8 | 0.9018 | 0.8773 | -0.0245 | 0.9251 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | FEDORA-ER8 | 0.9111 | 0.8901 | -0.021 | 0.9251 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | FEDORA-ER8 | 0.9111 | 0.8901 | -0.021 | 0.9251 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9019 | 0.8806 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9111 | 0.8898 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9111 | 0.8898 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9111 | 0.8898 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9111 | 0.8898 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9111 | 0.8898 | -0.0213 | 0.916 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9111 | 0.8901 | -0.021 | 0.916 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9127 | 0.8898 | -0.0229 | 0.916 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9127 | 0.8898 | -0.0229 | 0.916 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9127 | 0.8898 | -0.0229 | 0.916 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9127 | 0.8898 | -0.0229 | 0.916 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9127 | 0.8898 | -0.0229 | 0.916 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.8953 | -0.0218 | 0.916 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9111 | 0.8899 | -0.0212 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.9171 | 0.895 | -0.0221 | 0.916 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARDCI-ER8 | 0.911 | 0.8868 | -0.0242 | 0.916 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8797 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8797 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8797 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8797 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8797 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9013 | 0.88 | -0.0213 | 0.9154 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9029 | 0.8797 | -0.0232 | 0.9154 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9029 | 0.8797 | -0.0232 | 0.9154 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9029 | 0.8797 | -0.0232 | 0.9154 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9029 | 0.8797 | -0.0232 | 0.9154 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9029 | 0.8797 | -0.0232 | 0.9154 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9073 | 0.8853 | -0.022 | 0.9154 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9013 | 0.8798 | -0.0215 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9074 | 0.885 | -0.0224 | 0.9154 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HOWARD-ER8 | 0.9012 | 0.8767 | -0.0245 | 0.9154 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.8981 | -0.0233 | 0.9351 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | HUMBOLT-ER8 | 0.9214 | 0.898 | -0.0234 | 0.9351 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | HUMBOLT-ER8 | 0.9214 | 0.898 | -0.0234 | 0.9351 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | HUMBOLT-ER8 | 0.9214 | 0.898 | -0.0234 | 0.9351 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | HUMBOLT-ER8 | 0.9214 | 0.898 | -0.0234 | 0.9351 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | HUMBOLT-ER8 | 0.9214 | 0.898 | -0.0234 | 0.9351 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8798 | 0.8569 | -0.0229 | 0.8881 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8518 | -0.0218 | 0.8881 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8752 | 0.8515 | -0.0237 | 0.8881 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8752 | 0.8515 | -0.0237 | 0.8881 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8752 | 0.8515 | -0.0237 | 0.8881 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8752 | 0.8515 | -0.0237 | 0.8881 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8752 | 0.8515 | -0.0237 | 0.8881 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8736 | 0.8515 | -0.0221 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | INDMARIN-ER8 | 0.8735 | 0.8484 | -0.0251 | 0.8881 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8945 | -0.0229 | 0.9193 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8945 | -0.0229 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8945 | -0.0229 | 0.9193 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8945 | -0.0229 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8945 | -0.0229 | 0.9193 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.13076 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.12797 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.08312 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.03265 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.12797 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9199 | 0.8998 | -0.0201 | 0.9193 | 0.9 | 1.05 | 0.13403 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.13076 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.12797 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.08312 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.03265 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.12797 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9173 | 0.8957 | -0.0216 | 0.9193 | 0.9 | 1.05 | 0.13403 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8944 | -0.023 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9193 | 0.8941 | -0.0252 | 0.9193 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9193 | 0.8941 | -0.0252 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9193 | 0.8941 | -0.0252 | 0.9193 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9193 | 0.8941 | -0.0252 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9193 | 0.8941 | -0.0252 | 0.9193 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8966 | -0.024 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9174 | 0.8942 | -0.0232 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9206 | 0.8957 | -0.0249 | 0.9193 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LOOMIS-ER8 | 0.9179 | 0.8916 | -0.0263 | 0.9193 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | LYONS-ER8 | 0.9208 | 0.8974 | -0.0234 | 0.9345 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8558 | -0.0219 | 0.8922 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8558 | -0.0219 | 0.8922 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8558 | -0.0219 | 0.8922 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8558 | -0.0219 | 0.8922 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8558 | -0.0219 | 0.8922 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.884 | 0.8611 | -0.0229 | 0.8922 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8778 | 0.8561 | -0.0217 | 0.8922 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8794 | 0.8557 | -0.0237 | 0.8922 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8794 | 0.8557 | -0.0237 | 0.8922 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8794 | 0.8557 | -0.0237 | 0.8922 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8794 | 0.8557 | -0.0237 | 0.8922 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8794 | 0.8557 | -0.0237 | 0.8922 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8778 | 0.8558 | -0.022 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MARION-ER8 | 0.8777 | 0.8527 | -0.025 | 0.8922 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8993 | -0.0206 | 0.9335 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8993 | -0.0206 | 0.9335 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8993 | -0.0206 | 0.9335 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8993 | -0.0206 | 0.9335 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8993 | -0.0206 | 0.9335 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.92 | 0.8996 | -0.0204 | 0.9335 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9215 | 0.8993 | -0.0222 | 0.9335 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9215 | 0.8993 | -0.0222 | 0.9335 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9215 | 0.8993 | -0.0222 | 0.9335 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9215 | 0.8993 | -0.0222 | 0.9335 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9215 | 0.8993 | -0.0222 | 0.9335 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.92 | 0.8993 | -0.0207 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MONTROSE-ER8 | 0.9199 | 0.8964 | -0.0235 | 0.9335 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8848 | -0.0207 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9071 | 0.8845 | -0.0226 | 0.9193 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9071 | 0.8845 | -0.0226 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9071 | 0.8845 | -0.0226 | 0.9193 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9071 | 0.8845 | -0.0226 | 0.9193 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9071 | 0.8845 | -0.0226 | 0.9193 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9114 | 0.8899 | -0.0215 | 0.9193 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9055 | 0.8845 | -0.021 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9115 | 0.8896 | -0.0219 | 0.9193 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CHST-ER8 | 0.9054 | 0.8815 | -0.0239 | 0.9193 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-CLTN-ER8 | 0.9212 | 0.8978 | -0.0234 | 0.9348 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9101 | 0.8892 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9101 | 0.8892 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9101 | 0.8892 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9101 | 0.8892 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9101 | 0.8892 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9101 | 0.8895 | -0.0206 | 0.9239 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9102 | 0.8895 | -0.0207 | 0.9239 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9102 | 0.8895 | -0.0207 | 0.9239 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9102 | 0.8895 | -0.0207 | 0.9239 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9102 | 0.8895 | -0.0207 | 0.9239 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9102 | 0.8895 | -0.0207 | 0.9239 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9117 | 0.8892 | -0.0225 | 0.9239 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9117 | 0.8892 | -0.0225 | 0.9239 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9117 | 0.8892 | -0.0225 | 0.9239 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9117 | 0.8892 | -0.0225 | 0.9239 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9117 | 0.8892 | -0.0225 | 0.9239 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8947 | -0.0213 | 0.9239 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.9102 | 0.8893 | -0.0209 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.916 | 0.8943 | -0.0217 | 0.9239 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-HMPA-ER8 | 0.91 | 0.8863 | -0.0237 | 0.9239 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.8561 | -0.0219 | 0.8925 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.8561 | -0.0219 | 0.8925 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.8561 | -0.0219 | 0.8925 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.8561 | -0.0219 | 0.8925 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.8561 | -0.0219 | 0.8925 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8843 | 0.8614 | -0.0229 | 0.8925 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8781 | 0.8564 | -0.0217 | 0.8925 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8797 | 0.856 | -0.0237 | 0.8925 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8797 | 0.856 | -0.0237 | 0.8925 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8797 | 0.856 | -0.0237 | 0.8925 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8797 | 0.856 | -0.0237 | 0.8925 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8797 | 0.856 | -0.0237 | 0.8925 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.8781 | 0.8561 | -0.022 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-INDM-ER8 | 0.878 | 0.853 | -0.025 | 0.8925 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9224 | 0.8994 | -0.023 | 0.9243 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9224 | 0.8994 | -0.023 | 0.9243 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9224 | 0.8994 | -0.023 | 0.9243 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9224 | 0.8994 | -0.023 | 0.9243 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9224 | 0.8994 | -0.023 | 0.9243 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9224 | 0.8996 | -0.0228 | 0.9243 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9225 | 0.8996 | -0.0229 | 0.9243 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9225 | 0.8996 | -0.0229 | 0.9243 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9225 | 0.8996 | -0.0229 | 0.9243 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9225 | 0.8996 | -0.0229 | 0.9243 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9225 | 0.8996 | -0.0229 | 0.9243 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9243 | 0.8993 | -0.025 | 0.9243 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9243 | 0.8993 | -0.025 | 0.9243 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9243 | 0.8993 | -0.025 | 0.9243 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9243 | 0.8993 | -0.025 | 0.9243 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9243 | 0.8993 | -0.025 | 0.9243 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.9225 | 0.8994 | -0.0231 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-LMIS-ER8 | 0.923 | 0.8968 | -0.0262 | 0.9243 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9068 | 0.8858 | -0.021 | 0.9206 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9068 | 0.8858 | -0.021 | 0.9206 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9068 | 0.8858 | -0.021 | 0.9206 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9068 | 0.8858 | -0.021 | 0.9206 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9068 | 0.8858 | -0.021 | 0.9206 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9068 | 0.8861 | -0.0207 | 0.9206 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9069 | 0.8861 | -0.0208 | 0.9206 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9069 | 0.8861 | -0.0208 | 0.9206 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9069 | 0.8861 | -0.0208 | 0.9206 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9069 | 0.8861 | -0.0208 | 0.9206 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9069 | 0.8861 | -0.0208 | 0.9206 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9084 | 0.8858 | -0.0226 | 0.9206 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9084 | 0.8858 | -0.0226 | 0.9206 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9084 | 0.8858 | -0.0226 | 0.9206 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9084 | 0.8858 | -0.0226 | 0.9206 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9084 | 0.8858 | -0.0226 | 0.9206 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9127 | 0.8913 | -0.0214 | 0.9206 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9068 | 0.8859 | -0.0209 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9128 | 0.891 | -0.0218 | 0.9206 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-MDCY-ER8 | 0.9067 | 0.8829 | -0.0238 | 0.9206 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9087 | 0.8877 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9087 | 0.8877 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9087 | 0.8877 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9087 | 0.8877 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9087 | 0.8877 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9087 | 0.888 | -0.0207 | 0.9225 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9088 | 0.888 | -0.0208 | 0.9225 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9088 | 0.888 | -0.0208 | 0.9225 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9088 | 0.888 | -0.0208 | 0.9225 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9088 | 0.888 | -0.0208 | 0.9225 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9088 | 0.888 | -0.0208 | 0.9225 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9103 | 0.8877 | -0.0226 | 0.9225 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9103 | 0.8877 | -0.0226 | 0.9225 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9103 | 0.8877 | -0.0226 | 0.9225 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9103 | 0.8877 | -0.0226 | 0.9225 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9103 | 0.8877 | -0.0226 | 0.9225 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8932 | -0.0215 | 0.9225 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9088 | 0.8878 | -0.021 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9147 | 0.8929 | -0.0218 | 0.9225 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-NMAR-ER8 | 0.9086 | 0.8848 | -0.0238 | 0.9225 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-PARK-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | MOS-SALM-ER8 | 0.9224 | 0.8989 | -0.0235 | 0.9361 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8888 | -0.0206 | 0.9232 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8888 | -0.0206 | 0.9232 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8888 | -0.0206 | 0.9232 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8888 | -0.0206 | 0.9232 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8888 | -0.0206 | 0.9232 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9232 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9232 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9232 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9232 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9232 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9232 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8939 | -0.0214 | 0.9232 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9153 | 0.8936 | -0.0217 | 0.9232 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | ORLAND-ER8 | 0.9093 | 0.8855 | -0.0238 | 0.9232 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8875 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8875 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8875 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8875 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8875 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9085 | 0.8878 | -0.0207 | 0.9222 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.91 | 0.8875 | -0.0225 | 0.9222 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.91 | 0.8875 | -0.0225 | 0.9222 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.91 | 0.8875 | -0.0225 | 0.9222 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.91 | 0.8875 | -0.0225 | 0.9222 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.91 | 0.8875 | -0.0225 | 0.9222 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8929 | -0.0215 | 0.9222 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9085 | 0.8876 | -0.0209 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9144 | 0.8926 | -0.0218 | 0.9222 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKERCI-ER8 | 0.9084 | 0.8846 | -0.0238 | 0.9222 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9093 | 0.8884 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9094 | 0.8887 | -0.0207 | 0.9231 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9109 | 0.8884 | -0.0225 | 0.9231 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9152 | 0.8939 | -0.0213 | 0.9231 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9094 | 0.8885 | -0.0209 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9153 | 0.8935 | -0.0218 | 0.9231 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | PARKER-ER8 | 0.9092 | 0.8855 | -0.0237 | 0.9231 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SALEM-ER8 | 0.922 | 0.8985 | -0.0235 | 0.9357 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW170-ER8 | 0.9224 | 0.8991 | -0.0233 | 0.936 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | XLSW4X1-ER8 | 0.9224 | 0.8988 | -0.0236 | 0.9361 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.8957 | -0.021 | 0.9305 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.8957 | -0.021 | 0.9305 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.8957 | -0.021 | 0.9305 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.8957 | -0.021 | 0.9305 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.8957 | -0.021 | 0.9305 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.896 | -0.0207 | 0.9305 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9182 | 0.8957 | -0.0225 | 0.9305 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9182 | 0.8957 | -0.0225 | 0.9305 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9182 | 0.8957 | -0.0225 | 0.9305 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9182 | 0.8957 | -0.0225 | 0.9305 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9182 | 0.8957 | -0.0225 | 0.9305 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9167 | 0.8958 | -0.0209 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8928 | -0.0238 | 0.9305 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SPENCER-ER8 | 0.9166 | 0.8927 | -0.0239 | 0.9305 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SPENCER-ER8 | 0.9166 | 0.8927 | -0.0239 | 0.9305 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SPENCER-ER8 | 0.9166 | 0.8927 | -0.0239 | 0.9305 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SPENCER-ER8 | 0.9166 | 0.8927 | -0.0239 | 0.9305 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SPENCER-ER8 | 0.9166 | 0.8927 | -0.0239 | 0.9305 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.896 | -0.0209 | 0.9308 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.896 | -0.0209 | 0.9308 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.896 | -0.0209 | 0.9308 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.896 | -0.0209 | 0.9308 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.896 | -0.0209 | 0.9308 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.917 | 0.8963 | -0.0207 | 0.9308 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9185 | 0.896 | -0.0225 | 0.9308 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9185 | 0.896 | -0.0225 | 0.9308 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9185 | 0.896 | -0.0225 | 0.9308 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9185 | 0.896 | -0.0225 | 0.9308 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9185 | 0.896 | -0.0225 | 0.9308 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.917 | 0.896 | -0.021 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-SPENC-ER8 | 0.9169 | 0.893 | -0.0239 | 0.9308 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8906 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8906 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8906 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8906 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8906 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9119 | 0.8909 | -0.021 | 0.9258 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9134 | 0.8906 | -0.0228 | 0.9258 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9134 | 0.8906 | -0.0228 | 0.9258 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9134 | 0.8906 | -0.0228 | 0.9258 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9134 | 0.8906 | -0.0228 | 0.9258 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9134 | 0.8906 | -0.0228 | 0.9258 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8961 | -0.0218 | 0.9258 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9119 | 0.8907 | -0.0212 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9179 | 0.8958 | -0.0221 | 0.9258 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-FEDOR-ER8 | 0.9118 | 0.8876 | -0.0242 | 0.9258 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9014 | 0.8799 | -0.0215 | 0.9156 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9014 | 0.8799 | -0.0215 | 0.9156 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9014 | 0.8799 | -0.0215 | 0.9156 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9014 | 0.8799 | -0.0215 | 0.9156 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9014 | 0.8799 | -0.0215 | 0.9156 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9014 | 0.8802 | -0.0212 | 0.9156 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9015 | 0.8802 | -0.0213 | 0.9156 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9015 | 0.8802 | -0.0213 | 0.9156 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9015 | 0.8802 | -0.0213 | 0.9156 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9015 | 0.8802 | -0.0213 | 0.9156 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9015 | 0.8802 | -0.0213 | 0.9156 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.903 | 0.8798 | -0.0232 | 0.9156 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.903 | 0.8798 | -0.0232 | 0.9156 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.903 | 0.8798 | -0.0232 | 0.9156 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.903 | 0.8798 | -0.0232 | 0.9156 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.903 | 0.8798 | -0.0232 | 0.9156 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8855 | -0.022 | 0.9156 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9015 | 0.8799 | -0.0216 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9075 | 0.8851 | -0.0224 | 0.9156 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW-HOWAR-ER8 | 0.9013 | 0.8768 | -0.0245 | 0.9156 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8913 | -0.0209 | 0.9259 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8913 | -0.0209 | 0.9259 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8913 | -0.0209 | 0.9259 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8913 | -0.0209 | 0.9259 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8913 | -0.0209 | 0.9259 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8916 | -0.0206 | 0.9259 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9137 | 0.8913 | -0.0224 | 0.9259 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9137 | 0.8913 | -0.0224 | 0.9259 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9137 | 0.8913 | -0.0224 | 0.9259 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9137 | 0.8913 | -0.0224 | 0.9259 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9137 | 0.8913 | -0.0224 | 0.9259 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8967 | -0.0214 | 0.9259 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9122 | 0.8914 | -0.0208 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9181 | 0.8964 | -0.0217 | 0.9259 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW145-ER8 | 0.9121 | 0.8884 | -0.0237 | 0.9259 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8894 | -0.0208 | 0.924 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8894 | -0.0208 | 0.924 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8894 | -0.0208 | 0.924 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8894 | -0.0208 | 0.924 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8894 | -0.0208 | 0.924 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9103 | 0.8896 | -0.0207 | 0.924 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9118 | 0.8893 | -0.0225 | 0.924 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9118 | 0.8893 | -0.0225 | 0.924 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9118 | 0.8893 | -0.0225 | 0.924 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9118 | 0.8893 | -0.0225 | 0.924 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9118 | 0.8893 | -0.0225 | 0.924 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13076 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.08312 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.03265 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.12797 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8948 | -0.0214 | 0.924 | 0.9 | 1.05 | 0.13403 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9103 | 0.8894 | -0.0209 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 704 #:: FT2 IN SD. BREAKER FAULT (3392):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13076 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.08312 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.03265 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13403 | P23:345:UMZW:# 705 #:: FT2 IN SD. BREAKER FAULT (3396):EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13076 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.08312 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.03265 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.12797 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9162 | 0.8945 | -0.0217 | 0.924 | 0.9 | 1.05 | 0.13403 | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW162-ER8 | 0.9102 | 0.8864 | -0.0238 | 0.924 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.8999 | -0.0206 | 0.9341 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.8999 | -0.0206 | 0.9341 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.8999 | -0.0206 | 0.9341 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.8999 | -0.0206 | 0.9341 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.8999 | -0.0206 | 0.9341 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9221 | 0.8999 | -0.0222 | 0.9341 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9221 | 0.8999 | -0.0222 | 0.9341 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9221 | 0.8999 | -0.0222 | 0.9341 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9221 | 0.8999 | -0.0222 | 0.9341 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9221 | 0.8999 | -0.0222 | 0.9341 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW130-ER8 | 0.9205 | 0.897 | -0.0235 | 0.9341 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8687 | -0.0215 | 0.9045 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8687 | -0.0215 | 0.9045 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8687 | -0.0215 | 0.9045 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8687 | -0.0215 | 0.9045 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8687 | -0.0215 | 0.9045 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8964 | 0.8739 | -0.0225 | 0.9045 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8903 | 0.8689 | -0.0214 | 0.9045 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8919 | 0.8686 | -0.0233 | 0.9045 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8919 | 0.8686 | -0.0233 | 0.9045 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8919 | 0.8686 | -0.0233 | 0.9045 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8919 | 0.8686 | -0.0233 | 0.9045 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8919 | 0.8686 | -0.0233 | 0.9045 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8903 | 0.8687 | -0.0216 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW144-ER8 | 0.8902 | 0.8656 | -0.0246 | 0.9045 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8657 | -0.0215 | 0.9014 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8657 | -0.0215 | 0.9014 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8657 | -0.0215 | 0.9014 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8657 | -0.0215 | 0.9014 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8657 | -0.0215 | 0.9014 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12752 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.07988 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.13078 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12752 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.07988 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12473 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.13078 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.13076 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.08312 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-074 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.03265 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.12797 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8933 | 0.8708 | -0.0225 | 0.9014 | 0.9 | 1.05 | 0.13403 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8658 | -0.0214 | 0.9014 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6230 #: GRP IN SD. OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 AND 652832-652532-
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12752 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.07988 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.13078 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8888 | 0.8654 | -0.0234 | 0.9014 | 0.9 | 1.05 | 0.12752 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8888 | 0.8654 | -0.0234 | 0.9014 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8888 | 0.8654 | -0.0234 | 0.9014 | 0.9 | 1.05 | 0.07988 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8888 | 0.8654 | -0.0234 | 0.9014 | 0.9 | 1.05 | 0.12473 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8888 | 0.8654 | -0.0234 | 0.9014 | 0.9 | 1.05 | 0.13078 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8872 | 0.8655 | -0.0217 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2425 #:: GI IN NE. GI 1196 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Voltage | 01ALL | 2 | 23SP | GEN-2018-067 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12752 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-069 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2018-070 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.07988 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-023 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.12473 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01ALL | 2 | 23SP | GEN-2019-037 | SW156-ER8 | 0.8871 | 0.8624 | -0.0247 | 0.9014 | 0.9 | 1.05 | 0.13078 | P45:345:UMZW:# 1328 #: GI IN NE.
Voltage | 01NR | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 26WP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531359 BEELER 3 115 | 0.9206 | 0.8948 | 0.0258 | 0.9578 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531360 JAGGER 3 115 | 0.9159 | 0.8923 | 0.0236 | 0.9612 | 0.9 | 1.05 | 0.0336 | 531360 JAGGER 3 115 531362 MANNGT 3 115 1
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531360 JAGGER 3 115 | 0.9112 | 0.8853 | 0.0259 | 0.9677 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531360 JAGGER 3 115 | 0.8998 | 0.8731 | 0.0267 | 0.9612 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531360 JAGGER 3 115 | 0.916 | 0.8924 | 0.0236 | 0.9612 | 0.9 | 1.05 | 0.0336 | P12:115:SUNC:JAGGER-SCOTTCITY:::HV:
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531361 DIGHTON3 115 | 0.9153 | 0.8917 | 0.0236 | 0.9607 | 0.9 | 1.05 | 0.0336 | 531360 JAGGER 3 115 531362 MANNGT 3 115 1
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531361 DIGHTON3 115 | 0.9105 | 0.8847 | 0.0258 | 0.9671 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531361 DIGHTON3 115 | 0.8992 | 0.8725 | 0.0267 | 0.9607 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531361 DIGHTON3 115 | 0.9153 | 0.8918 | 0.0235 | 0.9607 | 0.9 | 1.05 | 0.0336 | P12:115:SUNC:JAGGER-SCOTTCITY:::HV:
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531362 MANNGT 3 115 | 0.9092 | 0.8833 | 0.0259 | 0.9739 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531362 MANNGT 3 115 | 0.8978 | 0.8711 | 0.0267 | 0.9678 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531363 MANNING3 115 | 0.9082 | 0.8822 | 0.026 | 0.9728 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531363 MANNING3 115 | 0.8967 | 0.87 | 0.0267 | 0.9668 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531495 LIBERTYT 115 | 0.9223 | 0.899 | 0.0233 | 0.9563 | 0.9 | 1.05 | 0.0336 | 531360 JAGGER 3 115 531362 MANNGT 3 115 1
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531495 LIBERTYT 115 | 0.9204 | 0.8949 | 0.0255 | 0.9635 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531495 LIBERTYT 115 | 0.9091 | 0.8829 | 0.0262 | 0.9563 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531495 LIBERTYT 115 | 0.9224 | 0.8991 | 0.0233 | 0.9563 | 0.9 | 1.05 | 0.0336 | P12:115:SUNC:JAGGER-SCOTTCITY:::HV:
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531496 LIBERTY3 115 | 0.9172 | 0.8937 | 0.0235 | 0.9514 | 0.9 | 1.05 | 0.0336 | 531360 JAGGER 3 115 531362 MANNGT 3 115 1
Voltage | 03ALL | 2 | 23SP | GEN-2019-014 | 531496 LIBERTY3 115 | 0.9152 | 0.8896 | 0.0256 | 0.9586 | 0.9 | 1.05 | 0.0338 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531496 LIBERTY3 115 | 0.9039 | 0.8774 | 0.0265 | 0.9514 | 0.9 | 1.05 | 0.0336 | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1
Voltage | 03ALL | 2 | 26SP | GEN-2019-014 | 531496 LIBERTY3 115 | 0.9173 | 0.8938 | 0.0235 | 0.9514 | 0.9 | 1.05 | 0.0336 | P12:115:SUNC:JAGGER-SCOTTCITY:::HV:
Voltage | 03ALL | 2 | 26WP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0918 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-014 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.2871 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.1267 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.1507 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0918 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.1135 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-054 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0858 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.1135 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0968 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0968 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2019-068 | 539801 THISTLE7 345 | 0.9835 | 0.9462 | 0.0373 | 0.9738 | 0.95 | 1.05 | 0.0858 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Voltage | 03ALL | 2 | 26WP | GEN-2018-093 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0436 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2018-108 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.075 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0715 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2018-128 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0362 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-001 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0508 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.2146 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.1372 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0715 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.1544 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-054 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0855 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.1544 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.1759 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-062 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0384 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.1759 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-068 | 539801 THISTLE7 345 | 0.9838 | 0.946 | 0.0378 | 0.9738 | 0.95 | 1.05 | 0.0855 | P23:345:SUNC:HLC_BRK188:::EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0918 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-014 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.2871 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.1267 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.1507 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0918 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.1135 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-054 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0858 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.1135 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0968 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0968 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-068 | 539801 THISTLE7 345 | 0.9828 | 0.9454 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0858 | P42:345:SPS:CARPENTER:OR335:SLG:EHV:
Voltage | 03ALL | 2 | 26WP | GEN-2019-014 | 539801 THISTLE7 345 | 0.9836 | 0.9462 | 0.0374 | 0.9738 | 0.95 | 1.05 | 0.0303 | P42:345:SPS:HITCHLAND:1R30:SLG:EHV:
Voltage | 03ALL | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 26L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | 26L | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_6 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_7 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_9 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_10 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_11 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 b.2. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_12 | 3 Phase fault on N ENGLN7 115.00 (661070) 115 kV Bus a. Apply fault at the N ENGLN7 115.00 (661070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 b.2. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_13 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_14 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_15 | 3 Phase fault on HESKETT4 230.00 (661042) 230 kV Bus a. Apply fault at the HESKETT4 230.00 (661042) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESKETT4 (661042) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_16 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_17 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_18 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_19 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_20 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_21 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_22 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_23 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_25 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_27 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_28 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_29 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_30 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_31 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_32 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_34 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_35 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_36 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_37 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_38 | 3 Phase fault on POPLK_5 161.00 (681544) 161 kV Bus a. Apply fault at the POPLK_5 161.00 (681544) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.2. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.5. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.6. POPLK_5 (681544) 161.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_39 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.3. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_40 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_41 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_42 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_43 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_44 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_45 | 3 Phase fault on ADAMS 5 161.00 (635056) 161 kV Bus a. Apply fault at the ADAMS 5 161.00 (635056) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_46 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_47 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_48 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_49 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_50 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_51 | 3 Phase fault on MCKSBRG 5 161.00 (635645) 161 kV Bus a. Apply fault at the MCKSBRG 5 161.00 (635645) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKSBRG 5 (635645) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_52 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_53 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_54 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_55 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_56 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_57 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_58 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_59 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_60 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_61 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_62 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_63 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_64 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_65 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_66 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_67 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_68 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_69 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_70 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_71 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_72 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_73 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_74 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_75 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_76 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_77 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_78 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_79 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.3. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_80 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_81 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_82 | 3 Phase fault on PICKCITY-RR7115.00 (659543) 115 kV Bus a. Apply fault at the PICKCITY-RR7115.00 (659543) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_83 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_84 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_85 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_86 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_87 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_88 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_89 | 3 Phase fault on SHIRLEY TAP 115.00 (652395) 115 kV Bus a. Apply fault at the SHIRLEY TAP 115.00 (652395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_90 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_91 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_92 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_93 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_94 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_95 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_96 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_97 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_98 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_99 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_100 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_101 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_102 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_103 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_104 | 3 Phase fault on ROUGHRDR-BE7115.00 (659184) 115 kV Bus a. Apply fault at the ROUGHRDR-BE7115.00 (659184) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_105 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_106 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_107 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_108 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_109 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_110 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_111 | 3 Phase fault on DEVAUL -MG7115.00 (655747) 115 kV Bus a. Apply fault at the DEVAUL -MG7115.00 (655747) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. DEVAUL 8 (652257) 69.0 kV to DEVALTP -MG8 (655744) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_112 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.2. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.3. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.4. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.5. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.6. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.7. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.8. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.9. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.11. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_113 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.3. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_114 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_115 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_116 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_117 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_118 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_119 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_120 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_121 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_122 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_123 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_124 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_125 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_126 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_127 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_128 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_129 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_130 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_131 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_132 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_133 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_134 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_135 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_136 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_137 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_138 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_139 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_140 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_141 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_142 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_143 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_144 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_145 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_146 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_147 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_148 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_149 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_150 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_151 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_152 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_153 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_154 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_155 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_156 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_157 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_158 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_159 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_160 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_161 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_162 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_163 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_164 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_165 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_166 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_167 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.5. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_168 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_169 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_170 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_171 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_172 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_173 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_174 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_175 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_176 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_177 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_178 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_179 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_181 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_182 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_183 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_184 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_185 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_186 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_187 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_188 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_189 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_190 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_191 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_192 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_193 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_194 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_195 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_196 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_197 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_198 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_199 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_200 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_201 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_202 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_203 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_204 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_205 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_206 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_207 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_208 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_209 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_210 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_211 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_212 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to DICKINS2-BE7 (659195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_213 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_214 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_215 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_216 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_217 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_218 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_219 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_224 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_225 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_226 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_227 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_228 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_229 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_230 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_232 | 3 Phase fault on J1754 POI 230.00 (47544) 230 kV Bus a. Apply fault at the J1754 POI 230.00 (47544) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_233 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_234 | 3 Phase fault on HD HV 5 161.00 (628909) 161 kV Bus a. Apply fault at the HD HV 5 161.00 (628909) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD HV 5 (628909) 161.0 kV to HD WIND 5 (628910) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_235 | 3 Phase fault on HD WIND 5 161.00 (628910) 161 kV Bus a. Apply fault at the HD WIND 5 161.00 (628910) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_236 | 3 Phase fault on HD WIND 5 161.00 (628910) 161 kV Bus a. Apply fault at the HD WIND 5 161.00 (628910) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_237 | 3 Phase fault on EXIRAREC 8 69.000 (629902) 69 kV Bus a. Apply fault at the EXIRAREC 8 69.000 (629902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXIRAREC 8 (629902) 69.0 kV to ANITA 8 (630009) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_238 | 3 Phase fault on ANITA 8 69.000 (630009) 69 kV Bus a. Apply fault at the ANITA 8 69.000 (630009) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANITA 8 (630009) 69.0 kV to CASEY R (630396) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_239 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_240 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_241 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_242 | 3 Phase fault on DOONTAP8 69.000 (635377) 69 kV Bus a. Apply fault at the DOONTAP8 69.000 (635377) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOONTAP8 (635377) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_243 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_244 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_245 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_246 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_247 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_248 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_249 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_250 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_251 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_252 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to CRAIG 8 (635392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_253 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_254 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_255 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_256 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_257 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_258 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_259 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_260 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_261 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to PR BRZ 4 (648506) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_262 | 3 Phase fault on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_263 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_264 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_265 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_266 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_267 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_268 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_269 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_270 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_271 | 3 Phase fault on SHIRLEY TAP 115.00 (652395) 115 kV Bus a. Apply fault at the SHIRLEY TAP 115.00 (652395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_272 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_273 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_274 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_275 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_276 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_277 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_278 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_279 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_280 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_281 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_282 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_283 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_284 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_285 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_286 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_287 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_288 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_289 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_290 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_291 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_292 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_293 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_294 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_295 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_296 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_297 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25S | Transfer | GROUP1_P1_FAULT_298 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25S | Transfer | GROUP1_P1_FAULT_299 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_300 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_301 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_302 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_303 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_304 | 3 Phase fault on MT WEST4 230.00 (652450) 230 kV Bus a. Apply fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_305 | 3 Phase fault on MT WEST4 230.00 (652450) 230 kV Bus a. Apply fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_306 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_307 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_308 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_309 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to ND.SUN._-PP4 (659400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_310 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to LNGBUTTE-RR4 (659550) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_311 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_312 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_313 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_314 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_315 | 3 Phase fault on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_316 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_317 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to PRVLNG16 (654457) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_318 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_319 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_320 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_321 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_322 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_323 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_324 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_325 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_326 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_327 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_328 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_329 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_330 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_331 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_332 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_333 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_334 | 3 Phase fault on DEVAUL -MG7115.00 (655747) 115 kV Bus a. Apply fault at the DEVAUL -MG7115.00 (655747) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_335 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_336 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to ROUGHRDR-MG7 (655750) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_337 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NRWSTMDN-MG7 (655751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_338 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_339 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_340 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_341 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_342 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_343 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_344 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_345 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_346 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_347 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_348 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_349 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_350 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_351 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_352 | 3 Phase fault on ROUGHRIDER 4230.00 (657741) 230 kV Bus a. Apply fault at the ROUGHRIDER 4230.00 (657741) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROUGHRIDER 4 (657741) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_353 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_354 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_355 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_356 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_357 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_358 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_359 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_360 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_361 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_362 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_363 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_364 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_365 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_366 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_367 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_368 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to WDICKSN7 (661024) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_369 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_370 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_371 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_372 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_373 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_374 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_375 | 3 Phase fault on DICKINS2-BE7115.00 (659195) 115 kV Bus a. Apply fault at the DICKINS2-BE7115.00 (659195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_376 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_377 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_378 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_379 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_380 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_381 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_382 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_383 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_384 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_385 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_386 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_387 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_388 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_389 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_390 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_391 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE4 (659339) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_392 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_393 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_394 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_395 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_396 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_397 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_398 | 3 Phase fault on DAGLUM__-BE4230.00 (659448) 230 kV Bus a. Apply fault at the DAGLUM__-BE4230.00 (659448) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAGLUM__-BE4 (659448) 230.0 kV to BRADYWND 4 (659450) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_399 | 3 Phase fault on LNGBUTTE-RR7115.00 (659551) 115 kV Bus a. Apply fault at the LNGBUTTE-RR7115.00 (659551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGBUTTE-RR7 (659551) 115.0 kV to RAIDER__-RR7 (659553) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_400 | 3 Phase fault on RAIDER__-RR7115.00 (659553) 115 kV Bus a. Apply fault at the RAIDER__-RR7115.00 (659553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAIDER__-RR7 (659553) 115.0 kV to REDTRAIL-RR7 (659554) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_401 | 3 Phase fault on RAIDER__-RR7115.00 (659553) 115 kV Bus a. Apply fault at the RAIDER__-RR7115.00 (659553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAIDER__-RR7 (659553) 115.0 kV to RICHRDTN-RR7 (659555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_402 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_403 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_404 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_405 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_406 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_407 | 3 Phase fault on K319EWOL-NI869.000 (659867) 69 kV Bus a. Apply fault at the K319EWOL-NI869.000 (659867) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K319EWOL-NI8 (659867) 69.0 kV to L9 MANNI-NI8 (659868) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_408 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_409 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_410 | 3 Phase fault on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_411 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_412 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_413 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_414 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_415 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K207OC N-NI8 (659943) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_416 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_417 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_418 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_419 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_420 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_421 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_422 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_423 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_424 | 3 Phase fault on BEULAH 7 115.00 (661008) 115 kV Bus a. Apply fault at the BEULAH 7 115.00 (661008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_425 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_426 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to NAPOLEON SW4 (661091) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_427 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_428 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_429 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_430 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_431 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_432 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_433 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_434 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_435 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_436 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_437 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_438 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_439 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_440 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_441 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_442 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_443 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_444 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_445 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_446 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_447 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_448 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_449 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_450 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_451 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_452 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_453 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_454 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_455 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_456 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DICKNSON 9 (560122) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_457 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_458 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_459 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_460 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_461 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_462 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_463 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_464 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_465 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to RHAME___-BE7 (659267) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_466 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_467 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_468 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_469 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_470 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_471 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_472 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_473 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_474 | 3 Phase fault on LNGBUTTE-RR4230.00 (659550) 230 kV Bus a. Apply fault at the LNGBUTTE-RR4230.00 (659550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGBUTTE-RR4 (659550) 230.0 kV to LNGBUTTE-RR7 (659551) 115.0 kV to LNGBUTTE-RR9 (659552) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_475 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_476 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_477 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to MANDAN 7 (661054) 115.0 kV to MANDAN 9 (661908) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_15 | 3 Phase fault on HESKETT4 230.00 (661042) 230 kV Bus a. Apply fault at the HESKETT4 230.00 (661042) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESKETT4 (661042) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_21 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_22 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_25 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_71 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_73 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_79 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.3. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_80 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_81 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_82 | 3 Phase fault on PICKCITY-RR7115.00 (659543) 115 kV Bus a. Apply fault at the PICKCITY-RR7115.00 (659543) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_92 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_93 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_94 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_100 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_106 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_119 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_120 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_125 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_126 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_127 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_128 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_129 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_133 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_134 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_135 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_137 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_138 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_139 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_140 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_141 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_165 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_168 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_170 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_173 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_176 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_177 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_178 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_186 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_202 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_203 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_205 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_206 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_207 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_211 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_213 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_218 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_226 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_227 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_228 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_229 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_230 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_231 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_232 | 3 Phase fault on J1754 POI 230.00 (47544) 230 kV Bus a. Apply fault at the J1754 POI 230.00 (47544) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_233 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_268 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_269 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_292 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_293 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_294 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_295 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_296 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_306 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_307 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_314 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_333 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_352 | 3 Phase fault on ROUGHRIDER 4230.00 (657741) 230 kV Bus a. Apply fault at the ROUGHRIDER 4230.00 (657741) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROUGHRIDER 4 (657741) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_355 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_356 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_359 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_360 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_361 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_362 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_363 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_364 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_366 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_370 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_383 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_384 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_395 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_396 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_397 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_424 | 3 Phase fault on BEULAH 7 115.00 (661008) 115 kV Bus a. Apply fault at the BEULAH 7 115.00 (661008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_426 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to NAPOLEON SW4 (661091) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_436 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_437 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_443 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_447 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_451 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_452 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_453 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_454 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_455 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_459 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_460 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_461 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_462 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_463 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_477 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to MANDAN 7 (661054) 115.0 kV to MANDAN 9 (661908) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Base | GROUP1_P1_FAULT_297 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25S | Base | GROUP1_P1_FAULT_298 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25S | Base | GROUP1_P1_FAULT_365 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed
01 - North | 25W | Transfer | GROUP1_P1_FAULT_1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_6 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_7 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_9 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_10 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_11 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 b.2. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_12 | 3 Phase fault on N ENGLN7 115.00 (661070) 115 kV Bus a. Apply fault at the N ENGLN7 115.00 (661070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 b.2. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_13 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_14 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_15 | 3 Phase fault on HESKETT4 230.00 (661042) 230 kV Bus a. Apply fault at the HESKETT4 230.00 (661042) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESKETT4 (661042) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_16 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_17 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_18 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_19 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_20 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_21 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_22 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_23 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_25 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_27 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_28 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_29 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_30 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Oscillations observed in the voltage ride through of G18-067 | Reclosing Removed Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_31 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_32 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_33 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_34 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_35 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_36 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_37 | 3 Phase fault on POPLK_5 161.00 (681544) 161 kV Bus a. Apply fault at the POPLK_5 161.00 (681544) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.2. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.5. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.6. POPLK_5 (681544) 161.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_38 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.3. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_39 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_40 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25W | Transfer | GROUP1_P1_FAULT_41 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_42 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_43 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_44 | 3 Phase fault on ADAMS 5 161.00 (635056) 161 kV Bus a. Apply fault at the ADAMS 5 161.00 (635056) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_45 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25W | Transfer | GROUP1_P1_FAULT_46 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_47 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_48 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_49 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_50 | 3 Phase fault on MCKSBRG 5 161.00 (635645) 161 kV Bus a. Apply fault at the MCKSBRG 5 161.00 (635645) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKSBRG 5 (635645) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_51 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_52 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_53 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_54 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_55 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_56 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_57 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_58 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_59 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_60 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed
01 - North | 25W | Transfer | GROUP1_P1_FAULT_61 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_62 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_63 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_64 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_65 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_66 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_67 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_68 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_69 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_70 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_71 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_72 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_73 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_74 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_75 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_76 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_77 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_78 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.3. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_79 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_80 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_81 | 3 Phase fault on PICKCITY-RR7115.00 (659543) 115 kV Bus a. Apply fault at the PICKCITY-RR7115.00 (659543) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_82 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_83 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_84 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_85 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_86 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_87 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_88 | 3 Phase fault on SHIRLEY TAP 115.00 (652395) 115 kV Bus a. Apply fault at the SHIRLEY TAP 115.00 (652395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_89 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_90 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_91 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_92 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_93 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_94 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_95 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_96 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_97 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_98 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_99 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_100 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_101 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_102 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_103 | 3 Phase fault on ROUGHRDR-BE7115.00 (659184) 115 kV Bus a. Apply fault at the ROUGHRDR-BE7115.00 (659184) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_104 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_105 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_106 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_107 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_108 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_109 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_110 | 3 Phase fault on DEVAUL -MG7115.00 (655747) 115 kV Bus a. Apply fault at the DEVAUL -MG7115.00 (655747) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. DEVAUL 8 (652257) 69.0 kV to DEVALTP -MG8 (655744) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_111 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.2. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.3. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.4. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.5. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.6. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.7. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.8. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.9. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.11. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_112 | 3 Phase fault on ANITA 5 161.00 (631070) 161 kV Bus a. Apply fault at the ANITA 5 161.00 (631070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.3. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_113 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_114 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_115 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_116 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_117 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_118 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_119 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_120 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_121 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_122 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_123 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_124 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_125 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_126 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_127 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_128 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_129 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_130 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_131 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_132 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_133 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_134 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_135 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_136 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_137 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_138 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_139 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_140 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_141 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_142 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_143 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_144 | 3 Phase fault on CRESTON5 161.00 (652560) 161 kV Bus a. Apply fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON5 (652560) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_145 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_146 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_147 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_148 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_149 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_150 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_151 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_152 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_153 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_154 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_155 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_156 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_157 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_158 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_159 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_160 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_161 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_162 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_163 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_164 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_165 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_166 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.5. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_167 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_168 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_169 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_170 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_171 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_172 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_173 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_174 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_175 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_176 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_177 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_178 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_179 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_180 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_181 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_182 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_183 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_184 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_185 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_186 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_187 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_188 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_189 | 3 Phase fault on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_190 | 3 Phase fault on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_191 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_193 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_194 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_195 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_196 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_197 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_198 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_199 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_200 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_201 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_202 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_203 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_204 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_205 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_206 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_207 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_208 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_209 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_210 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_211 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to DICKINS2-BE7 (659195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_212 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_213 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_214 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_215 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_216 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_217 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_218 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_223 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_224 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_225 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_226 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_227 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_228 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_229 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_230 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_231 | 3 Phase fault on J1754 POI 230.00 (47544) 230 kV Bus a. Apply fault at the J1754 POI 230.00 (47544) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_232 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_233 | 3 Phase fault on HD HV 5 161.00 (628909) 161 kV Bus a. Apply fault at the HD HV 5 161.00 (628909) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD HV 5 (628909) 161.0 kV to HD WIND 5 (628910) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_234 | 3 Phase fault on HD WIND 5 161.00 (628910) 161 kV Bus a. Apply fault at the HD WIND 5 161.00 (628910) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_235 | 3 Phase fault on HD WIND 5 161.00 (628910) 161 kV Bus a. Apply fault at the HD WIND 5 161.00 (628910) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_236 | 3 Phase fault on EXIRAREC 8 69.000 (629902) 69 kV Bus a. Apply fault at the EXIRAREC 8 69.000 (629902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXIRAREC 8 (629902) 69.0 kV to ANITA 8 (630009) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_237 | 3 Phase fault on ANITA 8 69.000 (630009) 69 kV Bus a. Apply fault at the ANITA 8 69.000 (630009) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANITA 8 (630009) 69.0 kV to CASEY R (630396) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_238 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_239 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_240 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_241 | 3 Phase fault on DOONTAP8 69.000 (635377) 69 kV Bus a. Apply fault at the DOONTAP8 69.000 (635377) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOONTAP8 (635377) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_242 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_243 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_244 | 3 Phase fault on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_245 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_246 | 3 Phase fault on INWOODT8 69.000 (635383) 69 kV Bus a. Apply fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INWOODT8 (635383) 69.0 kV to NORTHWST-NI8 (659894) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_247 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_248 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_249 | 3 Phase fault on SXRIVER8 69.000 (635386) 69 kV Bus a. Apply fault at the SXRIVER8 69.000 (635386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXRIVER8 (635386) 69.0 kV to ALCESTR8 (635387) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_250 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_251 | 3 Phase fault on IRETON 8 69.000 (635390) 69 kV Bus a. Apply fault at the IRETON 8 69.000 (635390) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETON 8 (635390) 69.0 kV to CRAIG 8 (635392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_252 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_253 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_254 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_255 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_256 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_257 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_258 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_259 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_260 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to PR BRZ 4 (648506) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_261 | 3 Phase fault on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_262 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_263 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_264 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_265 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_266 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_267 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_268 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_269 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_270 | 3 Phase fault on SHIRLEY TAP 115.00 (652395) 115 kV Bus a. Apply fault at the SHIRLEY TAP 115.00 (652395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_271 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_272 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_273 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_274 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_275 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_276 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_277 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_278 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_279 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_280 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_281 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_282 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_283 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_284 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_285 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_286 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_287 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_288 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_289 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_290 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_291 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_292 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_293 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_294 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_295 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_296 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25W | Transfer | GROUP1_P1_FAULT_297 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time to 3.5 Cycles Removed Reclosing
01 - North | 25W | Transfer | GROUP1_P1_FAULT_298 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_299 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_300 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_301 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_302 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_303 | 3 Phase fault on MT WEST4 230.00 (652450) 230 kV Bus a. Apply fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_304 | 3 Phase fault on MT WEST4 230.00 (652450) 230 kV Bus a. Apply fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_305 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_306 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_307 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_308 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to ND.SUN._-PP4 (659400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_309 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to LNGBUTTE-RR4 (659550) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_310 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_311 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_312 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_313 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_314 | 3 Phase fault on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_315 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_316 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to PRVLNG16 (654457) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_317 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_318 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_319 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_320 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_321 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_322 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_323 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_324 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_325 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_326 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_327 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_328 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_329 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_330 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_331 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_332 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_333 | 3 Phase fault on DEVAUL -MG7115.00 (655747) 115 kV Bus a. Apply fault at the DEVAUL -MG7115.00 (655747) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_334 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_335 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to ROUGHRDR-MG7 (655750) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_336 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NRWSTMDN-MG7 (655751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_337 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_338 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_339 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_340 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_341 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_342 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_343 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_344 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_345 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_346 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_347 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_348 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_349 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_350 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_351 | 3 Phase fault on ROUGHRIDER 4230.00 (657741) 230 kV Bus a. Apply fault at the ROUGHRIDER 4230.00 (657741) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROUGHRIDER 4 (657741) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_352 | 3 Phase fault on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_353 | 3 Phase fault on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_354 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_355 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_356 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_357 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_358 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_359 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_360 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_361 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_362 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_363 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_364 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed
01 - North | 25W | Transfer | GROUP1_P1_FAULT_365 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_366 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_367 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to WDICKSN7 (661024) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_368 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_369 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_370 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_371 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_372 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_373 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_374 | 3 Phase fault on DICKINS2-BE7115.00 (659195) 115 kV Bus a. Apply fault at the DICKINS2-BE7115.00 (659195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_375 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_376 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_377 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_378 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_379 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_380 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_381 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_382 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_383 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_384 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_385 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_386 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_387 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_388 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_389 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_390 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE4 (659339) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_391 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_392 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_393 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_394 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_395 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_396 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_397 | 3 Phase fault on DAGLUM__-BE4230.00 (659448) 230 kV Bus a. Apply fault at the DAGLUM__-BE4230.00 (659448) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAGLUM__-BE4 (659448) 230.0 kV to BRADYWND 4 (659450) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_398 | 3 Phase fault on LNGBUTTE-RR7115.00 (659551) 115 kV Bus a. Apply fault at the LNGBUTTE-RR7115.00 (659551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGBUTTE-RR7 (659551) 115.0 kV to RAIDER__-RR7 (659553) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_399 | 3 Phase fault on RAIDER__-RR7115.00 (659553) 115 kV Bus a. Apply fault at the RAIDER__-RR7115.00 (659553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAIDER__-RR7 (659553) 115.0 kV to REDTRAIL-RR7 (659554) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_400 | 3 Phase fault on RAIDER__-RR7115.00 (659553) 115 kV Bus a. Apply fault at the RAIDER__-RR7115.00 (659553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAIDER__-RR7 (659553) 115.0 kV to RICHRDTN-RR7 (659555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_401 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_402 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_403 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_404 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_405 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_406 | 3 Phase fault on K319EWOL-NI869.000 (659867) 69 kV Bus a. Apply fault at the K319EWOL-NI869.000 (659867) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K319EWOL-NI8 (659867) 69.0 kV to L9 MANNI-NI8 (659868) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_407 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_408 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_409 | 3 Phase fault on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_410 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_411 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_412 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_413 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_414 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K207OC N-NI8 (659943) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_415 | 3 Phase fault on L1______-NI869.000 (659902) 69 kV Bus a. Apply fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_416 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_417 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_418 | 3 Phase fault on L3______-NI869.000 (659904) 69 kV Bus a. Apply fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L3______-NI8 (659904) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_419 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_420 | 3 Phase fault on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_421 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_422 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_423 | 3 Phase fault on BEULAH 7 115.00 (661008) 115 kV Bus a. Apply fault at the BEULAH 7 115.00 (661008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_424 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_425 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to NAPOLEON SW4 (661091) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_426 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_427 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_428 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_429 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_430 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_431 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_432 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_433 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_434 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_435 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_436 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_437 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_438 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_439 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_440 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_441 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_442 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_443 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_444 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_445 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_446 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_447 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_448 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_449 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_450 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_451 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_452 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_453 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_454 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_455 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DICKNSON 9 (560122) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_456 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_457 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_458 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_459 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_460 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_461 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_462 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_463 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_464 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to RHAME___-BE7 (659267) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_465 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_466 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_467 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_468 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_469 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_470 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_471 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_472 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_473 | 3 Phase fault on LNGBUTTE-RR4230.00 (659550) 230 kV Bus a. Apply fault at the LNGBUTTE-RR4230.00 (659550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGBUTTE-RR4 (659550) 230.0 kV to LNGBUTTE-RR7 (659551) 115.0 kV to LNGBUTTE-RR9 (659552) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_474 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_475 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_476 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to MANDAN 7 (661054) 115.0 kV to MANDAN 9 (661908) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.10. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.11. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.6. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.6. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.7. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.8. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.5. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on UTICAJC7 115.00 (652626) 115 kV Bus a. Apply Fault at the UTICAJC7 115.00 (652626) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to MENNO JCT 7 (660007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 b.4. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 b.4. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.5. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC7 (652626) 115.0 kV to NAPA JCT 7 (660026) 115.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.5. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.6. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.7. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.8. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Oscillations observed in the voltage ride through of G18-067 | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on COYOTE 3 345.00 (661016) 345 kV Bus a. Apply Fault at the COYOTE 3 345.00 (661016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 b.5. COYOTE1G (661015) 24.0 kV to COYOTE 3 (661016) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on COYOTE 3 345.00 (661016) 345 kV Bus a. Apply Fault at the COYOTE 3 345.00 (661016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 b.5. COYOTE1G (661015) 24.0 kV to COYOTE 3 (661016) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.4. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.4. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.5. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.6. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.7. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.3. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. MOS-PARK-ER8 (655143) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.3. TEA-ER8 (655322) 69.0 kV to VFODNES-ER8 (655469) 69.0 kV Transmission Circuit #1 b.4. VFODNES4 (652398) 230.0 kV to VFODNES-ER8 (655469) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to VFODNES-ER7 (655468) 115.0 kV to VFODNES1-ER9 (655470) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #2 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.3. DENISON4 (652567) 230.0 kV to GEN-2017-222 (760515) 230.0 kV Transmission Circuit #1 b.4. DENISON4 (652567) 230.0 kV to GEN-2018-074 (763098) 230.0 kV Transmission Circuit #1 b.5. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.3. J15_____-NI8 (659921) 69.0 kV to GEN-2019-019 (763593) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.3. J15_____-NI8 (659921) 69.0 kV to GEN-2019-019 (763593) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.3. J15_____-NI8 (659921) 69.0 kV to GEN-2019-019 (763593) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.3. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.9. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.3. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.9. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.3. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.9. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.3. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.9. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.3. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.4. J15_____-NI8 (659921) 69.0 kV to GEN-2019-019 (763593) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-004 (587030) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.3. BASIN___-BE4 (659199) 230.0 kV to GEN-2019-037 (763703) 345.0 kV Transmission Circuit #1 b.4. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.3. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.4. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.5. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 b.6. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.7. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.8. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.4. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 b.3. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 b.4. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.5. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.6. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.4. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.4. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.5. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.4. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.4. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.5. BELFELD4 (652425) 230.0 kV to BELFELD3 (652424) 345.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.6. BELFELD4 (652425) 230.0 kV to BELFELD3 (652424) 345.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.4. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.6. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.7. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.8. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.9. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.10. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.11. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.3. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to GEN-2017-222 (760515) 230.0 kV Transmission Circuit #1 b.3. DENISON4 (652567) 230.0 kV to GEN-2018-074 (763098) 230.0 kV Transmission Circuit #1 b.4. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.5. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.6. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply Fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.4. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.5. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on MANNINGTAP 869.000 (656267) 69 kV Bus a. Apply Fault at the MANNINGTAP 869.000 (656267) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.3. MANNINGTAP 8 (656267) 69.0 kV to L9 MANNI-NI8 (659868) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on DENISONWEST869.000 (658030) 69 kV Bus a. Apply Fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.3. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.4. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.5. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 b.5. EXIRA 5 (652603) 161.0 kV to EXIRA 3G (658002) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply Fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply Fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply Fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 b.2. HUDSON 8 (635385) 69.0 kV to SXRIVER8 (635386) 69.0 kV Transmission Circuit #1 b.3. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on IRETONT8 69.000 (635391) 69 kV Bus a. Apply Fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 b.2. IRETON 8 (635390) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 b.3. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.3. J1CENTER-NI8 (659907) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.4. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on K217HWDN-NI869.000 (659942) 69 kV Bus a. Apply Fault at the K217HWDN-NI869.000 (659942) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on LOS 230 (659106) 230 kV Bus a. Apply Fault at the LOS 230 (659106) 230 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.4. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.7. GEN-2016-004 (587030) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.8. BASIN___-BE4 (659199) 230.0 kV to GEN-2019-037 (763703) 345.0 kV Transmission Circuit #1 b.9. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 b.10. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on BISON 3 345.00 (601067) 345 kV Bus a. Apply Fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.2. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER19 (620359) 13.8 kV Three Winding #1 b.3. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER29 (620360) 13.8 kV Three Winding #2 b.6. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on COURT FDR2 934.500 (606098) 34.5 kV Bus a. Apply Fault at the COURT FDR2 934.500 (606098) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.3. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.4. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.7. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.8. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.13. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.18. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.20. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.21. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.22. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.23. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.24. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.25. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.26. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_332 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_333 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_334 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_335 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_336 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_337 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_338 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Base | GROUP1_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_3 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_5 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_8 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_15 | 3 Phase fault on HESKETT4 230.00 (661042) 230 kV Bus a. Apply fault at the HESKETT4 230.00 (661042) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESKETT4 (661042) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_21 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_22 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_25 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_70 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_72 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_78 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.3. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_79 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_80 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_81 | 3 Phase fault on PICKCITY-RR7115.00 (659543) 115 kV Bus a. Apply fault at the PICKCITY-RR7115.00 (659543) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_91 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_92 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_93 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_99 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_105 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_118 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_119 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_124 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_125 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_126 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_127 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_128 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_132 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_133 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_134 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_136 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_137 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_138 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_139 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_140 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_164 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_167 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_169 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_172 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_175 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_176 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_177 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_185 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_201 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_202 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_204 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_205 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_206 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_210 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_212 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_217 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_225 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_226 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_227 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_228 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_229 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_230 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_231 | 3 Phase fault on J1754 POI 230.00 (47544) 230 kV Bus a. Apply fault at the J1754 POI 230.00 (47544) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_232 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_267 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_268 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_291 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_292 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_293 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_294 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_295 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_305 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_306 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_313 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_332 | 3 Phase fault on SW.MINOT-CP7115.00 (655657) 115 kV Bus a. Apply fault at the SW.MINOT-CP7115.00 (655657) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW.MINOT-CP7 (655657) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_351 | 3 Phase fault on ROUGHRIDER 4230.00 (657741) 230 kV Bus a. Apply fault at the ROUGHRIDER 4230.00 (657741) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROUGHRIDER 4 (657741) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_354 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_355 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_358 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_359 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_360 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_361 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_362 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_363 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_365 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_369 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_382 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_383 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_394 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_395 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_396 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_423 | 3 Phase fault on BEULAH 7 115.00 (661008) 115 kV Bus a. Apply fault at the BEULAH 7 115.00 (661008) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_425 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to NAPOLEON SW4 (661091) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_435 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_436 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_442 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_446 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_450 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_451 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_452 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_453 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_454 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_458 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_459 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_460 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_461 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_462 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_476 | 3 Phase fault on MANDAN 4 230.00 (661053) 230 kV Bus a. Apply fault at the MANDAN 4 230.00 (661053) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDAN 4 (661053) 230.0 kV to MANDAN 7 (661054) 115.0 kV to MANDAN 9 (661908) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.10. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.11. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.6. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.6. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.7. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.8. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.6. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.7. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.8. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.6. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in power output of GARISN5G | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P1_FAULT_30 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Oscillations observed in the voltage ride through of G18-067 | Reduced Clearing Time Removed Reclosing
01 - North | 25W | Base | GROUP1_P1_FAULT_40 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed
01 - North | 25W | Base | GROUP1_P1_FAULT_45 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Removed Reclosing Reduced Clearing Time
01 - North | 25W | Base | GROUP1_P1_FAULT_60 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed
01 - North | 25W | Base | GROUP1_P1_FAULT_296 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time Removed Reclosing
01 - North | 25W | Base | GROUP1_P1_FAULT_297 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reduced Clearing Time Removed Reclosing
01 - North | 25W | Base | GROUP1_P1_FAULT_364 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Issues in recovery causing simulation crash | Reclosing Removed Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Base | GROUP1_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Oscillations observed in the voltage ride through of G18-067 | Operational steady state fixes (existing caps/taps/gen set points)
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_3 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_4 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_5 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_6 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_7 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_8 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_9 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_10 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_11 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_12 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_13 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_14 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_15 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_16 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_17 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_18 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_19 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_20 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_21 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_22 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_23 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_24 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_25 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_26 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_27 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_28 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_29 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_30 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_31 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_32 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_33 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_34 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_35 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_36 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P1_FAULT_37 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_37 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_38 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_39 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_40 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_41 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_42 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_43 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_44 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_45 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_46 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_47 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_48 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_49 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_50 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_51 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_52 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_53 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_54 | 3 Phase fault on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_55 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_56 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_57 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_58 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_59 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_60 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_61 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_62 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_63 | 3 Phase fault on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_64 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_65 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_66 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.4. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_67 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_68 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_69 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_70 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.3. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_71 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P1_FAULT_72 | 3 Phase fault on KEYSTON3 (640252) 345kV Bus a. Apply fault at the KEYSTON3 (640252) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.31. KEYSTON3 (640252) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_72 | 3 Phase fault on KEYSTON3 (640252) 345kV Bus a. Apply fault at the KEYSTON3 (640252) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.31. KEYSTON3 (640252) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_73 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_74 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_75 | 3 Phase fault on STEGALL-LNX3230.00 (652873) 230 kV Bus a. Apply fault at the STEGALL-LNX3230.00 (652873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_76 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_77 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_78 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_79 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_80 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_81 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_82 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_83 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_84 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_85 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.3. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_88 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_89 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_90 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_91 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_92 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_93 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_94 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_95 | 3 Phase fault on CRAWFRD7 115.00 (640147) 115 kV Bus a. Apply fault at the CRAWFRD7 115.00 (640147) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHADRON7 (640109) 115.0 kV to CRAWFRD7 (640147) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD7 (640147) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_96 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_97 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_98 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_99 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_100 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_101 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_102 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_106 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_107 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_108 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_109 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_110 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_111 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_112 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_113 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_114 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_115 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_116 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_117 | 3 Phase fault on VICTRYH4 230.00 (640396) 230 kV Bus a. Apply fault at the VICTRYH4 230.00 (640396) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTRYH7 (640397) 115.0 kV to VICTRYH4 (640396) 230.0 kV to VICTR10G (640399) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_118 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 7 (640530) 115.0 kV to BOBCAT.C 3 (640529) 345.0 kV to BOBCAT.C 9 (640531) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_119 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_120 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.4. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.4. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_132 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_133 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_134 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_135 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_136 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_137 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_138 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_139 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_140 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_141 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_142 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_143 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_145 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_146 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_147 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_148 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_149 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_150 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_151 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_152 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_153 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_154 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_155 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_156 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_157 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_158 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_159 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_162 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_163 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_164 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_165 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_166 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_167 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_168 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_169 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_170 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_171 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_172 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_173 | 3 Phase fault on S1244 5 161.00 (646244) 161 kV Bus a. Apply fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_174 | 3 Phase fault on S1297 5 161.00 (646297) 161 kV Bus a. Apply fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.2. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_175 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_176 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_177 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_178 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_179 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_180 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_181 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_182 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_183 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_184 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 b.4. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_185 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_186 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_187 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_188 | 3 Phase fault on S968 8 69.000 (647968) 69 kV Bus a. Apply fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_189 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_190 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_191 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_192 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_193 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_194 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_195 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_196 | 3 Phase fault on S993 8 69.000 (647993) 69 kV Bus a. Apply fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.3. MGLN TP8 (647112) 69.0 kV to MAGELLN8 (647113) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.5. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_197 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_198 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_199 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_200 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_201 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_202 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_203 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_204 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_205 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_206 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_207 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_208 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_209 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_210 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.4. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_211 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_212 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_213 | 3 Phase fault on S6866 8 69.000 (647866) 69 kV Bus a. Apply fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_214 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_215 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_216 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_217 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_218 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_219 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_220 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_221 | 3 Phase fault on STEGALL-LNX3230.00 (652873) 230 kV Bus a. Apply fault at the STEGALL-LNX3230.00 (652873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL-LNX3 (652873) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_222 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_223 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_224 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.3. STEGALL_-MB9 (659167) 13.8 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_225 | 3 Phase fault on DH_CS_EA-TS4230.00 (659829) 230 kV Bus a. Apply fault at the DH_CS_EA-TS4230.00 (659829) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEYW4 (652584) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.2. NB WEST4 (652585) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.3. DH_CS_EA-TS4 (659829) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_226 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_227 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_228 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_229 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_230 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_231 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.4. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_232 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_233 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_234 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 b.4. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_235 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_236 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_237 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_238 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_239 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_240 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_241 | 3 Phase fault on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_242 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_243 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_244 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_245 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_246 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_247 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_248 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_249 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_250 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_251 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_252 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_253 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_254 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_255 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_256 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_257 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_258 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_259 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_260 | 3 Phase fault on AUBURN 8 69.000 (640062) 69 kV Bus a. Apply fault at the AUBURN 8 69.000 (640062) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_261 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_262 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_263 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_264 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_265 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_266 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_267 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_268 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_269 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_270 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_271 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_272 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_273 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_274 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_275 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_276 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_277 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_278 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_279 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_280 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_281 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_282 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_283 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_284 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_285 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_286 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_287 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_288 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_289 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_290 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_291 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_292 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_293 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_294 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_295 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_296 | 3 Phase fault on KELLY 7 115.00 (640134) 115 kV Bus a. Apply fault at the KELLY 7 115.00 (640134) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_297 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_298 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_299 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_300 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_301 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_302 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_303 | 3 Phase fault on COOPER_602 869.000 (640143) 69 kV Bus a. Apply fault at the COOPER_602 869.000 (640143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_304 | 3 Phase fault on CRAWFRD7 115.00 (640147) 115 kV Bus a. Apply fault at the CRAWFRD7 115.00 (640147) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD7 (640147) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_305 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_306 | 3 Phase fault on CRESTON7 115.00 (640151) 115 kV Bus a. Apply fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_307 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_308 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_309 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_310 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_311 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P1_FAULT_312 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_312 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_313 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_314 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_315 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_317 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_318 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_319 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_320 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_321 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_322 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_323 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_324 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_325 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_326 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_327 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_329 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_330 | 3 Phase fault on HUMBOLT7 115.00 (640235) 115 kV Bus a. Apply fault at the HUMBOLT7 115.00 (640235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_331 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_332 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_333 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_334 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_335 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_336 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_337 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_338 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_339 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_340 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_341 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_342 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_343 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_344 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_345 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_346 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_347 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_348 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_349 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_350 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_351 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_352 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_353 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_354 | 3 Phase fault on REDWILO7 115.00 (640326) 115 kV Bus a. Apply fault at the REDWILO7 115.00 (640326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_355 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_356 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_357 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_358 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_359 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to BOBCAT.C 7 (640530) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_360 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_361 | 3 Phase fault on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_362 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_363 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_364 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_365 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_366 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_367 | 3 Phase fault on VICTRYH4 230.00 (640396) 230 kV Bus a. Apply fault at the VICTRYH4 230.00 (640396) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTRYH4 (640396) 230.0 kV to STEGALL4 (652573) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_368 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_369 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_370 | 3 Phase fault on ANTELOPE 3 (640520) 345.0 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_371 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_372 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to UPSTREAM.W 7 (643254) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_373 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_374 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_375 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_376 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_377 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_378 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_379 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_380 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_381 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_382 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_383 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_384 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_385 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_386 | 3 Phase fault on MGLN TP8 69.000 (647112) 69 kV Bus a. Apply fault at the MGLN TP8 69.000 (647112) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_387 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_388 | 3 Phase fault on S963 8 69.000 (647963) 69 kV Bus a. Apply fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_389 | 3 Phase fault on S963 8 69.000 (647963) 69 kV Bus a. Apply fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_390 | 3 Phase fault on S964 8 69.000 (647964) 69 kV Bus a. Apply fault at the S964 8 69.000 (647964) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_391 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_392 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_393 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_394 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_395 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_396 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_397 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_398 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to DH_CS_EA-TS4 (659829) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_399 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_400 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_401 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_402 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_403 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_404 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_405 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_406 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_409 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_410 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_411 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_412 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_413 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_414 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_415 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_416 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_417 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_418 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_419 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_420 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_421 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_422 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_423 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_424 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_425 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_426 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_427 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_428 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_429 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_430 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_431 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_432 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_433 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_434 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_435 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_436 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_437 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_438 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_439 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 b.5. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 b.5. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 b.5. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. GR ISLD T5 9 (643070) 13.8 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.5. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.6. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.6. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.5. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.5. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.6. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.7. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.6. G.I.T219 (640203) 13.8 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.7. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.5. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.6. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.7. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.5. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.3. S1255 5 (646255) 161.0 kV to S3455 3 (645455) 345.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455T19 (648255) 13.8 kV to S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV Three Winding #1 b.5. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.6. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV to WEBSTER5 (636001) 161.0 kV to WEBS1XT9 (636002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV to Fixed Shunt Device # b.3. IRVINGTON3 (635999) 345.0 kV to WEBSTER3 (636000) 345.0 kV Transmission Circuit #1 b.4. KOSSUTH 3 (635369) 345.0 kV to IRVINGTON3 (635999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B3 9 (635403) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to None Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-033 (763681) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-029 (763659) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-033 (763681) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-029 (763659) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Base | GROUP2_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Base | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.4. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to GEN-2019-041 (763725) 115.0 kV Transmission Circuit #1 b.3. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.6. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on MONOLITH 7 115.00 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 115.00 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to GEN-2019-041 (763725) 115.0 kV Transmission Circuit #1 b.3. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.4. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.4. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.6. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.7. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.8. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.9. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.10. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.11. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.3. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 4.5 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 4.5 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_3 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_4 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_5 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_6 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_7 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_8 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_9 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_10 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_11 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_12 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_13 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_14 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_15 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_16 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_17 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_18 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_19 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_20 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_21 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_22 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_23 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_24 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_25 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_26 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_27 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_28 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_29 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_30 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_31 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_32 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_33 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_34 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_35 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_36 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_37 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_37 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_38 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_39 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_40 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_41 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_42 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_43 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_44 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_45 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_46 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_47 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_48 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_49 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_50 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_51 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_52 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_53 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_54 | 3 Phase fault on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_55 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_56 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_57 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_58 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_59 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_60 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_61 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_62 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_63 | 3 Phase fault on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_64 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_65 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_66 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.4. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_67 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_68 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_69 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_70 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.3. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_71 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_72 | 3 Phase fault on KEYSTON3 (640252) 345kV Bus a. Apply fault at the KEYSTON3 (640252) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.31. KEYSTON3 (640252) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_72 | 3 Phase fault on KEYSTON3 (640252) 345kV Bus a. Apply fault at the KEYSTON3 (640252) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.31. KEYSTON3 (640252) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_73 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_74 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_75 | 3 Phase fault on STEGALL-LNX3230.00 (652873) 230 kV Bus a. Apply fault at the STEGALL-LNX3230.00 (652873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_76 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_77 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_78 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_79 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_80 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_81 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_82 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_83 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_84 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_85 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.3. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_88 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_89 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_90 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_91 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_92 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_93 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_94 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_95 | 3 Phase fault on CRAWFRD7 115.00 (640147) 115 kV Bus a. Apply fault at the CRAWFRD7 115.00 (640147) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHADRON7 (640109) 115.0 kV to CRAWFRD7 (640147) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD7 (640147) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_96 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_97 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_98 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_99 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_100 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_101 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_102 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_106 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_107 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_108 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_109 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_110 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_111 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_112 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_113 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_114 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_115 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_116 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_117 | 3 Phase fault on VICTRYH4 230.00 (640396) 230 kV Bus a. Apply fault at the VICTRYH4 230.00 (640396) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTRYH7 (640397) 115.0 kV to VICTRYH4 (640396) 230.0 kV to VICTR10G (640399) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_118 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 7 (640530) 115.0 kV to BOBCAT.C 3 (640529) 345.0 kV to BOBCAT.C 9 (640531) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_119 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_120 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.4. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.4. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_132 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_133 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_134 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_135 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_136 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_137 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_138 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_139 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_140 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_141 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_142 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_143 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_145 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_146 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_147 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_148 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_149 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_150 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_151 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_152 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_153 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_154 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_155 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_156 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_157 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_158 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_159 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_162 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_163 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_164 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_165 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_166 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_167 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_168 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_169 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_170 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_171 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_172 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_173 | 3 Phase fault on S1244 5 161.00 (646244) 161 kV Bus a. Apply fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_174 | 3 Phase fault on S1297 5 161.00 (646297) 161 kV Bus a. Apply fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.2. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_175 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_176 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_177 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_178 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_179 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_180 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_181 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_182 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_183 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_184 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 b.4. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_185 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_186 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_187 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_188 | 3 Phase fault on S968 8 69.000 (647968) 69 kV Bus a. Apply fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_189 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_190 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_191 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_192 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_193 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_194 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_195 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_196 | 3 Phase fault on S993 8 69.000 (647993) 69 kV Bus a. Apply fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.3. MGLN TP8 (647112) 69.0 kV to MAGELLN8 (647113) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.5. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_197 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_198 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_199 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_200 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_201 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_202 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_203 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_204 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_205 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_206 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_207 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_208 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_209 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_210 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.4. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_211 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_212 | 3 Phase fault on W BROCK8 69.000 (647111) 69 kV Bus a. Apply fault at the W BROCK8 69.000 (647111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_213 | 3 Phase fault on S6866 8 69.000 (647866) 69 kV Bus a. Apply fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_214 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_215 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_216 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_217 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_218 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_219 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_220 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_221 | 3 Phase fault on STEGALL-LNX3230.00 (652873) 230 kV Bus a. Apply fault at the STEGALL-LNX3230.00 (652873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL-LNX3 (652873) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_222 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_223 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_224 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.3. STEGALL_-MB9 (659167) 13.8 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_225 | 3 Phase fault on DH_CS_EA-TS4230.00 (659829) 230 kV Bus a. Apply fault at the DH_CS_EA-TS4230.00 (659829) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEYW4 (652584) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.2. NB WEST4 (652585) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.3. DH_CS_EA-TS4 (659829) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_226 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_227 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_228 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_229 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_230 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_231 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.4. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_232 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_233 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_234 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 b.2. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 b.3. MORRILL_-TS9 (659820) 34.5 kV to MORRILL7 (653312) 115.0 kV Two Winding #1 b.4. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_235 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_236 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_237 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_237 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_238 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_239 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_240 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_241 | 3 Phase fault on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_242 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_243 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_244 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_245 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_246 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_247 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_248 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_249 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_250 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_251 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_252 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_253 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_254 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_255 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_256 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_257 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_258 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_259 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_260 | 3 Phase fault on AUBURN 8 69.000 (640062) 69 kV Bus a. Apply fault at the AUBURN 8 69.000 (640062) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_261 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_262 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_263 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_264 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_265 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_266 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_267 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_268 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_269 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_270 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_271 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_272 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_273 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_274 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_275 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_276 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_277 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_278 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_279 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_280 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_281 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_282 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_283 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_284 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_285 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_286 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_287 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_288 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_289 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_290 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_291 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_292 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_293 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_294 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_295 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_296 | 3 Phase fault on KELLY 7 115.00 (640134) 115 kV Bus a. Apply fault at the KELLY 7 115.00 (640134) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_297 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_298 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_299 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_300 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_301 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_302 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_303 | 3 Phase fault on COOPER_602 869.000 (640143) 69 kV Bus a. Apply fault at the COOPER_602 869.000 (640143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_304 | 3 Phase fault on CRAWFRD7 115.00 (640147) 115 kV Bus a. Apply fault at the CRAWFRD7 115.00 (640147) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD7 (640147) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_305 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_306 | 3 Phase fault on CRESTON7 115.00 (640151) 115 kV Bus a. Apply fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_307 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_308 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_309 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_310 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_311 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_312 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_312 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_313 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_313 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_314 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_315 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_317 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_318 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_319 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_320 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_321 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_322 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_323 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_324 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_325 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_326 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_327 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_329 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_330 | 3 Phase fault on HUMBOLT7 115.00 (640235) 115 kV Bus a. Apply fault at the HUMBOLT7 115.00 (640235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_331 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_332 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_333 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_334 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_335 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_336 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_337 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_338 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_339 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_340 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_341 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_342 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_343 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_344 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_345 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_346 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_347 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_348 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_349 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_350 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_351 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_352 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_353 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_354 | 3 Phase fault on REDWILO7 115.00 (640326) 115 kV Bus a. Apply fault at the REDWILO7 115.00 (640326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_355 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_356 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_357 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_358 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to VICTRYH7 (640397) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_359 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to BOBCAT.C 7 (640530) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_360 | 3 Phase fault on SCOTBLF7 115.00 (640338) 115 kV Bus a. Apply fault at the SCOTBLF7 115.00 (640338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTBLF7 (640338) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_361 | 3 Phase fault on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_362 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_363 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_364 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_365 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_366 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_367 | 3 Phase fault on VICTRYH4 230.00 (640396) 230 kV Bus a. Apply fault at the VICTRYH4 230.00 (640396) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTRYH4 (640396) 230.0 kV to STEGALL4 (652573) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_368 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_369 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_370 | 3 Phase fault on ANTELOPE 3 (640520) 345.0 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345.0 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P1_FAULT_371 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_371 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_372 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to UPSTREAM.W 7 (643254) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_373 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_374 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_375 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_376 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_377 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_378 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_379 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_380 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_381 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_382 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_383 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_384 | 3 Phase fault on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_385 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_386 | 3 Phase fault on MGLN TP8 69.000 (647112) 69 kV Bus a. Apply fault at the MGLN TP8 69.000 (647112) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_387 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_388 | 3 Phase fault on S963 8 69.000 (647963) 69 kV Bus a. Apply fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_389 | 3 Phase fault on S963 8 69.000 (647963) 69 kV Bus a. Apply fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_390 | 3 Phase fault on S964 8 69.000 (647964) 69 kV Bus a. Apply fault at the S964 8 69.000 (647964) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_391 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_392 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_393 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_394 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_395 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_396 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_397 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_398 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to DH_CS_EA-TS4 (659829) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_399 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to SNAKECK_-TS7 (659814) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_400 | 3 Phase fault on MORRILL7 115.00 (653312) 115 kV Bus a. Apply fault at the MORRILL7 115.00 (653312) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRILL7 (653312) 115.0 kV to GERINGT_-TS7 (659821) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_401 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_402 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_403 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_404 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_405 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_406 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_409 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_410 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_411 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_412 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_413 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_414 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_415 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_416 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_417 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_418 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_419 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_420 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_421 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_422 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_423 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_424 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_425 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_426 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_427 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_428 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_429 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_430 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_431 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_432 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_433 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_434 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_435 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_436 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_437 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_438 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_439 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 b.5. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 b.5. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. GR ISLD T5 9 (643070) 13.8 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.5. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.6. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.6. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.5. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.5. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.6. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.7. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.6. G.I.T219 (640203) 13.8 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.7. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.5. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.6. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.7. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.5. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.5. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1254T19 (648254) 13.8 kV to S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV Three Winding #1 b.7. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.8. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.9. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.3. S1255 5 (646255) 161.0 kV to S3455 3 (645455) 345.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455T19 (648255) 13.8 kV to S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV Three Winding #1 b.5. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 b.5. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.6. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 b.4. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.5. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.6. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to G19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV to WEBSTER5 (636001) 161.0 kV to WEBS1XT9 (636002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV to Fixed Shunt Device # b.3. IRVINGTON3 (635999) 345.0 kV to WEBSTER3 (636000) 345.0 kV Transmission Circuit #1 b.4. KOSSUTH 3 (635369) 345.0 kV to IRVINGTON3 (635999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B3 9 (635403) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to None Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-033 (763681) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-029 (763659) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-033 (763681) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV to GEN-2019-029 (763659) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to GEN19-029 TAP (763666) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillation observed in response of Gen-19-029 and Gentleman Units 1 and 2 | Addition of second circuit between Gentleman and Keystone Addition of second circuit between Keystone and G19-029 tap
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non dampening oscillation observed in response of G16-074 | Addition of 150 MVAr Cap Bank at Redwillow 345 kV Substation Addition of 80 MVAr STATCOM at Sweetwater 345 kV Substation Operational steady state fixes (existing caps/taps/gen set points) | Retuning of G16-074 Electrical Control Model to allow for reactive support.
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.3. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.4. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to GEN-2019-041 (763725) 115.0 kV Transmission Circuit #1 b.3. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.6. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on MONOLITH 7 115.00 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 115.00 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to GEN-2019-041 (763725) 115.0 kV Transmission Circuit #1 b.3. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.4. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.4. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.6. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.7. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.8. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.9. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.10. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.11. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.3. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 4.5 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT01-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT01-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT02-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT02-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT03-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT03-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT04-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to POSTROCK7 (530583) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT04-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to POSTROCK7 (530583) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT05-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to SPEARVL6 (539695) 230 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT05-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to SPEARVL6 (539695) 230 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT06-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to SPRVL 3 (539759) 115 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT06-3PH | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to SPRVL 3 (539759) 115 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT07-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT07-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT08-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT08-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT09-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to CIMWD2 7 (531504) 345 kV Transmission Circuit #1 b.2. UNIT CIMARON_WTG1 (531605) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | FLT09-3PH will cause line relay trip on Finney - Holcomb 345kV line and destablize GEN-2018-030 and GEN-2008-018 | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25W | Transfer | G3_FLT09-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to CIMWD2 7 (531504) 345 kV Transmission Circuit #1 b.2. UNIT CIMARON_WTG1 (531605) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | FLT09-3PH will cause line relay trip on Finney - Holcomb 345kV line and destablize GEN-2018-030 and GEN-2008-018 | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25S | Transfer | G3_FLT1001-3PH | 3 Phase fault on G18-063-TAP (762992) 69 kV Bus a. Apply fault at the G18-063-TAP (762992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-063-TAP (762992) 69 kV to KELHYS 2 (541273) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1001-3PH | 3 Phase fault on G18-063-TAP (762992) 69 kV Bus a. Apply fault at the G18-063-TAP (762992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-063-TAP (762992) 69 kV to KELHYS 2 (541273) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1001-SB | Single Phase Fault with Stuck Breaker on KELHYS 2 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 (541273) 69 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69 kV to G18-063-TAP (762992) 69 kV Transmission Circuit #1 b.1. KELHYS 2 (541273) 69 kV to SEDPLT 2 (541275) 69 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1001-SB | Single Phase Fault with Stuck Breaker on KELHYS 2 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 (541273) 69 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69 kV to G18-063-TAP (762992) 69 kV Transmission Circuit #1 b.1. KELHYS 2 (541273) 69 kV to SEDPLT 2 (541275) 69 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1002-3PH | 3 Phase fault on G18-063-TAP (762992) 69 kV Bus a. Apply fault at the G18-063-TAP (762992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-063-TAP (762992) 69 kV to SEDN 2 (541271) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1002-3PH | 3 Phase fault on G18-063-TAP (762992) 69 kV Bus a. Apply fault at the G18-063-TAP (762992) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-063-TAP (762992) 69 kV to SEDN 2 (541271) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1002-SB | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to G18-063-TAP (762992) 69 kV Transmission Circuit #1 b.2. SEDN 2 (541271) 69 kV to SEDALIA5 (541209) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1002-SB | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to G18-063-TAP (762992) 69 kV Transmission Circuit #1 b.2. SEDN 2 (541271) 69 kV to SEDALIA5 (541209) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1003-3PH | 3 Phase fault on KELHYS 2 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69 kV to SEDPLT 2 (541275) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1003-3PH | 3 Phase fault on KELHYS 2 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69 kV to SEDPLT 2 (541275) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT100-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to G19-053/055 (763846) 230 kV Transmission Circuit #1 b.2. UNIT G19-053-GEN1 (763849) 0.7 kV #1 b.3. UNIT G19-055-GEN1 (763871) 0.6 kV #1 b.4. UNIT G19-055-GEN2 (763872) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT100-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to G19-053/055 (763846) 230 kV Transmission Circuit #1 b.2. UNIT G19-053-GEN1 (763849) 0.7 kV #1 b.3. UNIT G19-055-GEN1 (763871) 0.6 kV #1 b.4. UNIT G19-055-GEN2 (763872) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1003-SB | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1003-SB | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1004-3PH | 3 Phase fault on SEDPLT 2 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69 kV to COLECMP2 (541276) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1004-3PH | 3 Phase fault on SEDPLT 2 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69 kV to COLECMP2 (541276) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1005-3PH | 3 Phase fault on SEDPLT 2 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69 kV to PITTCRN2 (541274) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1005-3PH | 3 Phase fault on SEDPLT 2 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69 kV to PITTCRN2 (541274) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1006-3PH | 3 Phase fault on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to LAMONTETP (541535) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1006-3PH | 3 Phase fault on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to LAMONTETP (541535) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1006-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to G16-111-TAP (587884) 345 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1006-SB | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to G16-111-TAP (587884) 345 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1007-3PH | 3 Phase fault on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to SEDALIA5 (541209) 161 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1007-3PH | 3 Phase fault on SEDN 2 (541271) 69 kV Bus a. Apply fault at the SEDN 2 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69 kV to SEDALIA5 (541209) 161 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1008-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDS 2 (541272) 69 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1008-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDS 2 (541272) 69 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1008-SB | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to 45TH ST4 (533074) 138 kV Transmission Circuit #1 b.1. EVANS S4 (533041) 138 kV to LAKERDG4 (533053) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1008-SB | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to 45TH ST4 (533074) 138 kV Transmission Circuit #1 b.1. EVANS S4 (533041) 138 kV to LAKERDG4 (533053) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1009-3PH | 3 Phase fault on SEDS 2 (541272) 69 kV Bus a. Apply fault at the SEDS 2 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69 kV to PITTCRN2 (541274) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1009-3PH | 3 Phase fault on SEDS 2 (541272) 69 kV Bus a. Apply fault at the SEDS 2 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69 kV to PITTCRN2 (541274) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1009-SB | Single Phase Fault with Stuck Breaker on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161 kV to NRAYMORETP 5 (541231) 161 kV Transmission Circuit #1 b.2. NRAYMORE (541317) 161 kV to LVISTA 5 (542998) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1009-SB | Single Phase Fault with Stuck Breaker on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161 kV to NRAYMORETP 5 (541231) 161 kV Transmission Circuit #1 b.2. NRAYMORE (541317) 161 kV to LVISTA 5 (542998) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1010-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDEAST5 (541241) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1010-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDEAST5 (541241) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1010-SB | Single Phase Fault with Stuck Breaker on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161 kV to NRAYMORETP 5 (541231) 161 kV Transmission Circuit #1 b.2. KCSOUTH5 (541245) 161 kV to LNGVW 5 (541224) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1010-SB | Single Phase Fault with Stuck Breaker on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161 kV to NRAYMORETP 5 (541231) 161 kV Transmission Circuit #1 b.2. KCSOUTH5 (541245) 161 kV to LNGVW 5 (541224) 161 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1011-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to 5SEDALA (300117) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1011-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to 5SEDALA (300117) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1011-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GRNTWD 7 (515646) 345 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345 kV to RENFROW4 (515544) 138 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1011-SB | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GRNTWD 7 (515646) 345 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345 kV to RENFROW4 (515544) 138 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1012-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to 5GEORGE (300082) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1012-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to 5GEORGE (300082) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1012-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G16-153-TAP (588364) 345 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345 kV to VIOLA 4 (533075) 138 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 Trip generators FR2W1WF1 (533125),FR2W2WF1 (533126), FR3WTG1 (578533), FR2E1WF1 (533123), FR2E2WF1 (533124) Trip generator G16-153-GEN1 (588363),G17-086-GEN1 (589243) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1012-SB | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G16-153-TAP (588364) 345 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345 kV to VIOLA 4 (533075) 138 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 Trip generators FR2W1WF1 (533125),FR2W2WF1 (533126), FR3WTG1 (578533), FR2E1WF1 (533123), FR2E2WF1 (533124) Trip generator G16-153-GEN1 (588363),G17-086-GEN1 (589243) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1013-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDLIAW_CAP5 (541146) 161 kV Transmission Circuit #R c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1013-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to SEDLIAW_CAP5 (541146) 161 kV Transmission Circuit #R c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT101-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT101-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1013-SB | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to GRANTCO4 (515546) 138 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138 kV to RENFROW7 (515543) 345 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1013-SB | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to GRANTCO4 (515546) 138 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138 kV to RENFROW7 (515543) 345 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1014-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to WAFBE_SW5 (541337) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1014-3PH | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161 kV to WAFBE_SW5 (541337) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1014-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to WOODRNG7 (514715) 345 kV Transmission Circuit #1 b.1. HUNTERS7 (515476) 345 kV to CHSHLMV7 (515477) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1014-SB | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to WOODRNG7 (514715) 345 kV Transmission Circuit #1 b.1. HUNTERS7 (515476) 345 kV to CHSHLMV7 (515477) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1015-3PH | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161 kV to 5OVERTON 2 (345411) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1015-3PH | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161 kV to 5OVERTON 2 (345411) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1016-3PH | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161 kV to NUCOR5 (541395) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1016-3PH | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161 kV to NUCOR5 (541395) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1017-3PH | 3 Phase fault on 5SEDALA (300117) 161 kV Bus a. Apply fault at the 5SEDALA (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161 kV to 2SEDALI (300541) 69 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1017-3PH | 3 Phase fault on 5SEDALA (300117) 161 kV Bus a. Apply fault at the 5SEDALA (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161 kV to 2SEDALI (300541) 69 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1017-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1017-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1018-3PH | 3 Phase fault on 5SEDALA (300117) 161 kV Bus a. Apply fault at the 5SEDALA (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161 kV to WINDSR 5 (541217) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1018-3PH | 3 Phase fault on 5SEDALA (300117) 161 kV Bus a. Apply fault at the 5SEDALA (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161 kV to WINDSR 5 (541217) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1018-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. Thistle7 (539801) to DGRASSE7 (515852) 345kV CKT 2 line b.1. Thistle7 (539801) to CLARKCOUNTY7 (539800) 345kV CKT 1 line | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1018-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. Thistle7 (539801) to DGRASSE7 (515852) 345kV CKT 2 line b.1. Thistle7 (539801) to CLARKCOUNTY7 (539800) 345kV CKT 1 line | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1019-3PH | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161 kV to 5NORTONTP (301567) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1019-3PH | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161 kV to 5NORTONTP (301567) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1019-SB | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to 5MORGAN (300101) 161 kV Transmission Circuit #1 b.1. DAD368 5 (547478) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1019-SB | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to 5MORGAN (300101) 161 kV Transmission Circuit #1 b.1. DAD368 5 (547478) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1020-3PH | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161 kV to 2GEORGE (300531) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1020-3PH | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161 kV to 2GEORGE (300531) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1020-SB | Single Phase Fault with Stuck Breaker on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 b.2. CPK446 5 (547499) 161 kV to CPK446 2 (547618) 69 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1020-SB | Single Phase Fault with Stuck Breaker on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 b.2. CPK446 5 (547499) 161 kV to CPK446 2 (547618) 69 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1021-3PH | 3 Phase fault on WAFBE_SW5 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161 kV to WAFBW_SW5 (541335) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1021-3PH | 3 Phase fault on WAFBE_SW5 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161 kV to WAFBW_SW5 (541335) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1021-SB | Single Phase Fault with Stuck Breaker on BOL431 5 (547493) 161 kV Bus a. Apply fault at the BOL431 5 (547493) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BOL431 5 (547493) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 b.1. BOL431 5 (547493) 161 kV to BOL 73 5 (547464) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1021-SB | Single Phase Fault with Stuck Breaker on BOL431 5 (547493) 161 kV Bus a. Apply fault at the BOL431 5 (547493) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BOL431 5 (547493) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 b.1. BOL431 5 (547493) 161 kV to BOL 73 5 (547464) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1022-3PH | 3 Phase fault on WAFBE_SW5 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161 kV to WAFBE5 (541338) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1022-3PH | 3 Phase fault on WAFBE_SW5 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161 kV to WAFBE5 (541338) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1022-SB | Single Phase Fault with Stuck Breaker on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 5MORGANXF2 (301622) 161 kV Transmission Circuit #1 b.1. 5MORGAN (300101) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1022-SB | Single Phase Fault with Stuck Breaker on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 5MORGANXF2 (301622) 161 kV Transmission Circuit #1 b.1. 5MORGAN (300101) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1023-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to EVANS S4 (533041) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1023-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to EVANS S4 (533041) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT102-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT102-3PH | 3 Phase fault on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1023-SB | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to SAXMAN 3 (530711) 115 kV Transmission Circuit #1 b.1. LYONS 3 (530620) 115 kV to WHEATLD3 (533439) 115 kV Transmission Circuit #1 Trip generators S1,S2,S3,S4,S5,S6,S7 on bus LYONS 3 (530620). | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1023-SB | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to SAXMAN 3 (530711) 115 kV Transmission Circuit #1 b.1. LYONS 3 (530620) 115 kV to WHEATLD3 (533439) 115 kV Transmission Circuit #1 Trip generators S1,S2,S3,S4,S5,S6,S7 on bus LYONS 3 (530620). | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1024-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to LAKERDG4 (533053) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1024-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to LAKERDG4 (533053) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1024-SB | Single Phase Fault with Stuck Breaker on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to MON383 5 (547480) 161 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161 kV to AUR124 2 (547537) 69 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1024-SB | Single Phase Fault with Stuck Breaker on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to MON383 5 (547480) 161 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161 kV to AUR124 2 (547537) 69 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1025-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to 45TH ST4 (533074) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1025-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to 45TH ST4 (533074) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1025-SB | Single Phase Fault with Stuck Breaker on RDS295 5 (547473) 161 kV Bus a. Apply fault at the RDS295 5 (547473) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161 kV to G19-035-TAP (763696) 161 kV Transmission Circuit #1 b.1. RDS295 5 (547473) 161 kV to 5REEDSP (301521) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1025-SB | Single Phase Fault with Stuck Breaker on RDS295 5 (547473) 161 kV Bus a. Apply fault at the RDS295 5 (547473) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161 kV to G19-035-TAP (763696) 161 kV Transmission Circuit #1 b.1. RDS295 5 (547473) 161 kV to 5REEDSP (301521) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1026-3PH | 3 Phase fault on 45TH ST4 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 45TH ST4 (533074) 138 kV to COWSKIN4 (533038) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1026-3PH | 3 Phase fault on 45TH ST4 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 45TH ST4 (533074) 138 kV to COWSKIN4 (533038) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1026-SB | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPS 5 (541211) 161 kV Transmission Circuit #1 b.1. BLSPE 5 (541205) 161 kV to GRAINVL5 (541226) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1026-SB | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPS 5 (541211) 161 kV Transmission Circuit #1 b.1. BLSPE 5 (541205) 161 kV to GRAINVL5 (541226) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1027-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138 kV to CENTENN4 (533034) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1027-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138 kV to CENTENN4 (533034) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1027-SB | Single Phase Fault with Stuck Breaker on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to BLSPE 5 (541205) 161 kV Transmission Circuit #1 b.1. DUNCAN 5 (541235) 161 kV to SIBLEYPL (541250) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1027-SB | Single Phase Fault with Stuck Breaker on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to BLSPE 5 (541205) 161 kV Transmission Circuit #1 b.1. DUNCAN 5 (541235) 161 kV to SIBLEYPL (541250) 161 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1028-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138 kV to COWSKIN2 (533788) 69 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1028-3PH | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138 kV to COWSKIN2 (533788) 69 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1028-SB | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #1 b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1028-SB | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #1 b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1029-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138 kV to HOOVERN4 (533049) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1029-3PH | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKERDG4 (533053) 138 kV to HOOVERN4 (533049) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1029-SB | Single Phase Fault with Stuck Breaker on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 4 (533039) 138 kV Transmission Circuit #Z1 b.2. ELPASOE4 (533059) 138 kV to 47TH ST4 (533058) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1029-SB | Single Phase Fault with Stuck Breaker on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 4 (533039) 138 kV Transmission Circuit #Z1 b.2. ELPASOE4 (533059) 138 kV to 47TH ST4 (533058) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1030-3PH | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138 kV to HOOVERS4 (533050) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1030-3PH | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138 kV to HOOVERS4 (533050) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1030-SB | Single Phase Fault with Stuck Breaker on BU11PON4 (533032) 138 kV Bus a. Apply fault at the BU11PON4 (533032) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138 kV to WEAVER 4 (532991) 138 kV Transmission Circuit #1 b.1. BU11PON4 (533032) 138 kV to G19-062-TAP (763917) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1030-SB | Single Phase Fault with Stuck Breaker on BU11PON4 (533032) 138 kV Bus a. Apply fault at the BU11PON4 (533032) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138 kV to WEAVER 4 (532991) 138 kV Transmission Circuit #1 b.1. BU11PON4 (533032) 138 kV to G19-062-TAP (763917) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1031-3PH | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138 kV to HOOVERN2 (533805) 69 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1031-3PH | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138 kV to HOOVERN2 (533805) 69 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1031-SB | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to SPRNGDL4 (533067) 138 kV Transmission Circuit #1 b.1. WEAVER 4 (532991) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1031-SB | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to SPRNGDL4 (533067) 138 kV Transmission Circuit #1 b.1. WEAVER 4 (532991) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1032-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1032-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1033-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT3 (532725) 18 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1033-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT3 (532725) 18 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT103-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT103-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1034-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1034-3PH | 3 Phase fault on EVANS S4 (533041) 138 kV Bus a. Apply fault at the EVANS S4 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1035-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to SG12COL4 (533065) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1035-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to SG12COL4 (533065) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1036-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SG12COL4 (533065) 138 kV to BENTLEY4 (533015) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1036-3PH | 3 Phase fault on SG12COL4 (533065) 138 kV Bus a. Apply fault at the SG12COL4 (533065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SG12COL4 (533065) 138 kV to BENTLEY4 (533015) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1037-3PH | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138 kV to WWUPLNT4 (533016) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1037-3PH | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138 kV to WWUPLNT4 (533016) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1038-3PH | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138 kV to HALSTD 4 (533011) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1038-3PH | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138 kV to HALSTD 4 (533011) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1039-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to MAIZE 4 (533054) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1039-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to MAIZE 4 (533054) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT10-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to CIMRRN 7 (531502) 345 kV Transmission Circuit #1 b.2. CIMARON-GEN1 (531603) 0.7 kV Trip Bus b.3. UNIT CIMARON-GEN1 (531603) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT10-3PH | 3 Phase fault on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to CIMRRN 7 (531502) 345 kV Transmission Circuit #1 b.2. CIMARON-GEN1 (531603) 0.7 kV Trip Bus b.3. UNIT CIMARON-GEN1 (531603) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | FLT10-3PH will cause line relay trip on Finney - Holcomb 345kV line in 25W case and destablize GEN-2018-030 and GEN-2008-018 | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25S | Transfer | G3_FLT1040-3PH | 3 Phase fault on MAIZE 4 (533054) 138 kV Bus a. Apply fault at the MAIZE 4 (533054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIZE 4 (533054) 138 kV to CHISHLM4 (533035) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1040-3PH | 3 Phase fault on MAIZE 4 (533054) 138 kV Bus a. Apply fault at the MAIZE 4 (533054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIZE 4 (533054) 138 kV to CHISHLM4 (533035) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1041-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to 17TH 4 (533064) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1041-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to 17TH 4 (533064) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1042-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to CHISHLM2 (533786) 69 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1042-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to CHISHLM2 (533786) 69 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1043-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to PARKCTY4 (533052) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1043-3PH | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138 kV to PARKCTY4 (533052) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1044-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1044-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1045-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1045-3PH | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138 kV to WICHITA7 (532796) 345 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1051-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to ROSEHIL7 (532794) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1051-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to ROSEHIL7 (532794) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1052-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to WOLFCRK7 (532797) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1052-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to WOLFCRK7 (532797) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1053-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to WOLFCRK7 (532797) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1053-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to WOLFCRK7 (532797) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT105-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPRVILL-EHVB (539117) 230 kV Transmission Circuit #Z1 b.2. UNIT SVWF2 1 (539136) 0.6 kV #1 b.3. UNIT SVWF1 1 (539116) 0.6 kV #1 b.4. UNIT SVWF3 1 (539120) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT105-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPRVILL-EHVB (539117) 230 kV Transmission Circuit #Z1 b.2. UNIT SVWF2 1 (539136) 0.6 kV #1 b.3. UNIT SVWF1 1 (539116) 0.6 kV #1 b.4. UNIT SVWF3 1 (539120) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1054-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to BENTON 4 (532986) 138 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1054-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to BENTON 4 (532986) 138 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1055-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to BENTON 4 (532986) 138 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1055-3PH | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345 kV to BENTON 4 (532986) 138 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT106-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPERVIL7 (531469) 345 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT106-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPERVIL7 (531469) 345 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1067-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1067-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1068-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to G16-111-TAP (587884) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1068-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to G16-111-TAP (587884) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1070-3PH | 3 Phase fault on G14-001-TAP (562476) 345 kV Bus a. Apply fault at the G14-001-TAP (562476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G14-001-TAP (562476) 345 kV to EMPEC 7 (532768) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1070-3PH | 3 Phase fault on G14-001-TAP (562476) 345 kV Bus a. Apply fault at the G14-001-TAP (562476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G14-001-TAP (562476) 345 kV to EMPEC 7 (532768) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1071-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G16-153-TAP (588364) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1071-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G16-153-TAP (588364) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1073-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G18-128-TAP (763421) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1073-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to G18-128-TAP (763421) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT107-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPEARVL3 (539694) 115 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT107-3PH | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPEARVL3 (539694) 115 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1074-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to RENFROW7 (515543) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1074-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to RENFROW7 (515543) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1075-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to VIOLA 4 (533075) 138 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1075-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to VIOLA 4 (533075) 138 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1076-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to LATHAMS7 (532800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1076-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to LATHAMS7 (532800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1077-3PH | 3 Phase fault on G16-111-TAP (587884) 345 kV Bus a. Apply fault at the G16-111-TAP (587884) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-111-TAP (587884) 345 kV to SUMMIT 7 (532773) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1077-3PH | 3 Phase fault on G16-111-TAP (587884) 345 kV Bus a. Apply fault at the G16-111-TAP (587884) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-111-TAP (587884) 345 kV to SUMMIT 7 (532773) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1079-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to GEN-2018-054 (760116) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1079-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to GEN-2018-054 (760116) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1080-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to NRAYMORE (541317) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1080-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to NRAYMORE (541317) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1081-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to KCSOUTH5 (541245) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1081-3PH | 3 Phase fault on NRAYMORETP 5 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161 kV to KCSOUTH5 (541245) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1082-3PH | 3 Phase fault on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161 kV to LVISTA 5 (542998) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1082-3PH | 3 Phase fault on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161 kV to LVISTA 5 (542998) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1083-3PH | 3 Phase fault on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161 kV to LNGVW 5 (541224) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1083-3PH | 3 Phase fault on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161 kV to LNGVW 5 (541224) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT108-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to HEIZER 6 (530680) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT108-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to HEIZER 6 (530680) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1084-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to BUNKRDG5 (543008) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1084-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to BUNKRDG5 (543008) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1085-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to FROSTRD5 (541220) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1085-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to FROSTRD5 (541220) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1086-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to WINJT N5 (543009) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1086-3PH | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161 kV to WINJT N5 (543009) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1087-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to HOOKRD 5 (541249) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1087-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to HOOKRD 5 (541249) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1088-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to GRDVWE 5 (541223) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1088-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to GRDVWE 5 (541223) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1089-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to WSTELEC5 (541222) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1089-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to WSTELEC5 (541222) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1090-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to LNGVW 2 (541282) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1090-3PH | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161 kV to LNGVW 2 (541282) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1091-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GEN-2017-203 (760809) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1091-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GEN-2017-203 (760809) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1092-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GRNTWD 7 (515646) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1092-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to GRNTWD 7 (515646) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1093-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to HUNTERS7 (515476) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1093-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to HUNTERS7 (515476) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT109-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT109-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1094-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to G18-128-TAP (763421) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1094-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to G18-128-TAP (763421) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1095-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to RENFROW4 (515544) 138 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1095-3PH | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345 kV to RENFROW4 (515544) 138 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1096-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1096-3PH | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1098-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1098-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1100-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to GEN-2018-128 (763417) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1100-3PH | 3 Phase fault on G18-128-TAP (763421) 345 kV Bus a. Apply fault at the G18-128-TAP (763421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-128-TAP (763421) 345 kV to GEN-2018-128 (763417) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1101-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to G15-052T (560053) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1101-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to G15-052T (560053) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1102-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to ROSEHIL4 (533062) 138 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1102-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to ROSEHIL4 (533062) 138 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT110-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT110-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1107-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to WOODRNG7 (514715) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1107-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to WOODRNG7 (514715) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1108-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to CHSHLMV7 (515477) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1108-3PH | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345 kV to CHSHLMV7 (515477) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1109-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to SUMNER 4 (532984) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1109-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to SUMNER 4 (532984) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1110-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to CLEARWT4 (533036) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1110-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to CLEARWT4 (533036) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1111-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to GILL 4 (533047) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1111-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to GILL 4 (533047) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1112-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to CONWAY (539009) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1112-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to CONWAY (539009) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1113-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to MILAN_GOAB (539008) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1113-3PH | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138 kV to MILAN_GOAB (539008) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1114-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to MDFRDTP4 (515569) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1114-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to MDFRDTP4 (515569) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1115-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to GRANTCO4 (515546) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1115-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to GRANTCO4 (515546) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1116-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to WFEC_RNFRO4 (520409) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1116-3PH | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138 kV to WFEC_RNFRO4 (520409) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1117-3PH | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 (515569) 138 kV to RDRUNNR4 (515426) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1117-3PH | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 (515569) 138 kV to RDRUNNR4 (515426) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1118-3PH | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 (515569) 138 kV to MEDFORD4 (522397) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1118-3PH | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 (515569) 138 kV to MEDFORD4 (522397) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1119-3PH | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138 kV to RCKFALL4 (515427) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1119-3PH | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138 kV to RCKFALL4 (515427) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1120-3PH | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138 kV to COYOTE 4 (515581) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1120-3PH | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138 kV to COYOTE 4 (515581) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1121-3PH | 3 Phase fault on COYOTE 4 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138 kV to CHIKASI4 (514757) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1121-3PH | 3 Phase fault on COYOTE 4 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138 kV to CHIKASI4 (514757) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1122-3PH | 3 Phase fault on COYOTE 4 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138 kV to BLUFCRK4 (520447) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1122-3PH | 3 Phase fault on COYOTE 4 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138 kV to BLUFCRK4 (520447) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1123-3PH | 3 Phase fault on WFEC_RNFRO4 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFEC_RNFRO4 (520409) 138 kV to WAKTASW4 (520434) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1123-3PH | 3 Phase fault on WFEC_RNFRO4 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFEC_RNFRO4 (520409) 138 kV to WAKTASW4 (520434) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT112-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT112-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1124-3PH | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138 kV to WAKTASB4 (520452) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1124-3PH | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138 kV to WAKTASB4 (520452) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1125-3PH | 3 Phase fault on GRANTCO4 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO4 (515546) 138 kV to GRANTCO2 (515547) 69 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1125-3PH | 3 Phase fault on GRANTCO4 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO4 (515546) 138 kV to GRANTCO2 (515547) 69 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1126-3PH | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138 kV to WAKITA 2 (521085) 69 kV to WAKITA_13.8 (520435) 13 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1126-3PH | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138 kV to WAKITA 2 (521085) 69 kV to WAKITA_13.8 (520435) 13 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT113-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to GRTBEND3 (539678) 115 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT113-3PH | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to GRTBEND3 (539678) 115 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1135-3PH | 3 Phase fault on NINN1WF7 (532784) 345 kV Bus a. Apply fault at the NINN1WF7 (532784) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NINN1WF7 (532784) 345 kV to N1 LV 1 (534000) 34.5 kV to N1 WFTX1 (534030) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1135-3PH | 3 Phase fault on NINN1WF7 (532784) 345 kV Bus a. Apply fault at the NINN1WF7 (532784) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NINN1WF7 (532784) 345 kV to N1 LV 1 (534000) 34.5 kV to N1 WFTX1 (534030) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1136-3PH | 3 Phase fault on NINN1WF7 (532784) 345 kV Bus a. Apply fault at the NINN1WF7 (532784) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NINN1WF7 (532784) 345 kV to PRATTWF7 (532785) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1136-3PH | 3 Phase fault on NINN1WF7 (532784) 345 kV Bus a. Apply fault at the NINN1WF7 (532784) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NINN1WF7 (532784) 345 kV to PRATTWF7 (532785) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1137-3PH | 3 Phase fault on PRATTWF7 (532785) 345 kV Bus a. Apply fault at the PRATTWF7 (532785) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRATTWF7 (532785) 345 kV to P1 LV 1 (534003) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1137-3PH | 3 Phase fault on PRATTWF7 (532785) 345 kV Bus a. Apply fault at the PRATTWF7 (532785) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRATTWF7 (532785) 345 kV to P1 LV 1 (534003) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT11-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT11-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1149-3PH | 3 Phase fault on G14-001-TAP (562476) 345 kV Bus a. Apply fault at the G14-001-TAP (562476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G14-001-TAP (562476) 345 kV to GEN-2014-001 (583850) 345 kV Transmission Circuit #1 Trip generators G14-001-GEN1 (583853), G14-001-GEN2 (583856) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1149-3PH | 3 Phase fault on G14-001-TAP (562476) 345 kV Bus a. Apply fault at the G14-001-TAP (562476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G14-001-TAP (562476) 345 kV to GEN-2014-001 (583850) 345 kV Transmission Circuit #1 Trip generators G14-001-GEN1 (583853), G14-001-GEN2 (583856) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1151-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to DAD368 2 (547585) 69 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1151-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to DAD368 2 (547585) 69 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1152-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to 5MORGAN (300101) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1152-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to 5MORGAN (300101) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1153-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to BOL431 5 (547493) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1153-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to BOL431 5 (547493) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1154-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1154-3PH | 3 Phase fault on DAD368 5 (547478) 161 kV Bus a. Apply fault at the DAD368 5 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1155-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 5MORGANXF2 (301622) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1155-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 5MORGANXF2 (301622) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1156-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to BROOKLINE 5 (549969) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1156-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to BROOKLINE 5 (549969) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1157-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to STOCKTN5 (505498) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1157-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to STOCKTN5 (505498) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1158-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 2MORGAN (300782) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1158-3PH | 3 Phase fault on 5MORGAN (300101) 161 kV Bus a. Apply fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161 kV to 2MORGAN (300782) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1159-3PH | 3 Phase fault on BOL431 5 (547493) 161 kV Bus a. Apply fault at the BOL431 5 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL431 5 (547493) 161 kV to BOL 73 5 (547464) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1159-3PH | 3 Phase fault on BOL431 5 (547493) 161 kV Bus a. Apply fault at the BOL431 5 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL431 5 (547493) 161 kV to BOL 73 5 (547464) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1160-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to AUR124 5 (547468) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1160-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to AUR124 5 (547468) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1161-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to CPK446 2 (547618) 69 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1161-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to CPK446 2 (547618) 69 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1162-3PH | 3 Phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161 kV to 7MORGAN (300045) 345 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1162-3PH | 3 Phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161 kV to 7MORGAN (300045) 345 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1163-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to BROOKLINE 7 (549984) 345 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1163-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to BROOKLINE 7 (549984) 345 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1164-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to JTEC 5 (549954) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1164-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to JTEC 5 (549954) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1165-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1165-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1166-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1166-3PH | 3 Phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1167-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1167-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1168-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to 5COLLINS (300816) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1168-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to 5COLLINS (300816) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1169-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to 5STKAEC (300118) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1169-3PH | 3 Phase fault on STOCKTN5 (505498) 161 kV Bus a. Apply fault at the STOCKTN5 (505498) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKTN5 (505498) 161 kV to 5STKAEC (300118) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1170-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to MON383 5 (547480) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1170-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to MON383 5 (547480) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1171-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to G19-035-TAP (763696) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1171-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to G19-035-TAP (763696) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1172-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345 kV to 7MORGAN (300045) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1172-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345 kV to 7MORGAN (300045) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1173-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345 kV to FLINTCR7 (506935) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1173-3PH | 3 Phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345 kV to FLINTCR7 (506935) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT117-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to SPRVL 3 (539759) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT117-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to SPRVL 3 (539759) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1174-3PH | 3 Phase fault on SAXMAN 3 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1174-3PH | 3 Phase fault on SAXMAN 3 (530711) 115 kV Bus a. Apply fault at the SAXMAN 3 (530711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAXMAN 3 (530711) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1175-3PH | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to WHEATLD3 (533439) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1175-3PH | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to WHEATLD3 (533439) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1176-3PH | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to RICE 3 (530623) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1176-3PH | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115 kV to RICE 3 (530623) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1179-3PH | 3 Phase fault on BUSHTON3 (530681) 115 kV Bus a. Apply fault at the BUSHTON3 (530681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHTON3 (530681) 115 kV to ELLSWTH3 (539662) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1179-3PH | 3 Phase fault on BUSHTON3 (530681) 115 kV Bus a. Apply fault at the BUSHTON3 (530681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHTON3 (530681) 115 kV to ELLSWTH3 (539662) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1180-3PH | 3 Phase fault on WHEATLD3 (533439) 115 kV Bus a. Apply fault at the WHEATLD3 (533439) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEATLD3 (533439) 115 kV to WMCPHER3 (533438) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1180-3PH | 3 Phase fault on WHEATLD3 (533439) 115 kV Bus a. Apply fault at the WHEATLD3 (533439) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEATLD3 (533439) 115 kV to WMCPHER3 (533438) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1181-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT1181-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT1182-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to MCPHER 3 (533428) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT1182-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to MCPHER 3 (533428) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT1183-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to CORONAD3 (533394) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT1183-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to CORONAD3 (533394) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT118-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to SPEARVL3 (539694) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT118-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to SPEARVL3 (539694) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1184-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to MANVILE3 (533426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT1184-3PH | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115 kV to MANVILE3 (533426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT119-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.2. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT119-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.2. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1196-3PH | 3 Phase fault on G19-035-TAP (763696) 161 kV Bus a. Apply fault at the G19-035-TAP (763696) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-035-TAP (763696) 161 kV to AUR124 5 (547468) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1196-3PH | 3 Phase fault on G19-035-TAP (763696) 161 kV Bus a. Apply fault at the G19-035-TAP (763696) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-035-TAP (763696) 161 kV to AUR124 5 (547468) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1197-3PH | 3 Phase fault on G19-035-TAP (763696) 161 kV Bus a. Apply fault at the G19-035-TAP (763696) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-035-TAP (763696) 161 kV to RDS295 5 (547473) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1197-3PH | 3 Phase fault on G19-035-TAP (763696) 161 kV Bus a. Apply fault at the G19-035-TAP (763696) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-035-TAP (763696) 161 kV to RDS295 5 (547473) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1198-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to AUR124 2 (547537) 69 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1198-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to AUR124 2 (547537) 69 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1199-3PH | 3 Phase fault on RDS295 5 (547473) 161 kV Bus a. Apply fault at the RDS295 5 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161 kV to 5REEDSP (301521) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1199-3PH | 3 Phase fault on RDS295 5 (547473) 161 kV Bus a. Apply fault at the RDS295 5 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161 kV to 5REEDSP (301521) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1200-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1200-3PH | 3 Phase fault on AUR124 5 (547468) 161 kV Bus a. Apply fault at the AUR124 5 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161 kV to CPK446 5 (547499) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1202-3PH | 3 Phase fault on 5REEDSP (301521) 161 kV Bus a. Apply fault at the 5REEDSP (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161 kV to BRN412 5 (547488) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1202-3PH | 3 Phase fault on 5REEDSP (301521) 161 kV Bus a. Apply fault at the 5REEDSP (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161 kV to BRN412 5 (547488) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1203-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1203-3PH | 3 Phase fault on CPK446 5 (547499) 161 kV Bus a. Apply fault at the CPK446 5 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161 kV to DAD368 5 (547478) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT120-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT120-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1204-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to LAR382 5 (547479) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1204-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to LAR382 5 (547479) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1205-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to TIP292 5 (547472) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1205-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to TIP292 5 (547472) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1207-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to MON383 2 (547591) 69 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1207-3PH | 3 Phase fault on MON383 5 (547480) 161 kV Bus a. Apply fault at the MON383 5 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161 kV to MON383 2 (547591) 69 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1208-3PH | 3 Phase fault on 5REEDSP (301521) 161 kV Bus a. Apply fault at the 5REEDSP (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161 kV to 2REEDSP (300725) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1208-3PH | 3 Phase fault on 5REEDSP (301521) 161 kV Bus a. Apply fault at the 5REEDSP (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161 kV to 2REEDSP (300725) 69 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1209-3PH | 3 Phase fault on DUNCNRD2 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69 kV to DUNCAN 5 (541235) 161 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1209-3PH | 3 Phase fault on DUNCNRD2 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69 kV to DUNCAN 5 (541235) 161 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1210-3PH | 3 Phase fault on DUNCNRD2 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69 kV to LAKCTYK2 (543093) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1210-3PH | 3 Phase fault on DUNCNRD2 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69 kV to LAKCTYK2 (543093) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1211-3PH | 3 Phase fault on LAKCTYK2 (543093) 69 kV Bus a. Apply fault at the LAKCTYK2 (543093) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYK2 (543093) 69 kV to BLUSPRG2 (543088) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1211-3PH | 3 Phase fault on LAKCTYK2 (543093) 69 kV Bus a. Apply fault at the LAKCTYK2 (543093) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYK2 (543093) 69 kV to BLUSPRG2 (543088) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1212-3PH | 3 Phase fault on BLUSPRG2 (543088) 69 kV Bus a. Apply fault at the BLUSPRG2 (543088) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUSPRG2 (543088) 69 kV to LAKCTY 2 (543092) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1212-3PH | 3 Phase fault on BLUSPRG2 (543088) 69 kV Bus a. Apply fault at the BLUSPRG2 (543088) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUSPRG2 (543088) 69 kV to LAKCTY 2 (543092) 69 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1213-3PH | 3 Phase fault on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to SIBLEYPL (541250) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1213-3PH | 3 Phase fault on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to SIBLEYPL (541250) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT121-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT121-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1214-3PH | 3 Phase fault on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to BLSPE 5 (541205) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1214-3PH | 3 Phase fault on DUNCAN 5 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161 kV to BLSPE 5 (541205) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1215-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to HLLMRK 5 (541215) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1215-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to HLLMRK 5 (541215) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1216-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to ECKLES-161 (548808) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1216-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to ECKLES-161 (548808) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1217-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to ORRICK 5 (541244) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1217-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to ORRICK 5 (541244) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1218-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1218-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 5 (541202) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1219-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 2 (541263) 69 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1219-3PH | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161 kV to SIBLEY 2 (541263) 69 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1220-3PH | 3 Phase fault on HLLMRK 5 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161 kV to LBRTYWT5 (541247) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1220-3PH | 3 Phase fault on HLLMRK 5 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161 kV to LBRTYWT5 (541247) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1221-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to BLUMILS5 (543004) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1221-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to BLUMILS5 (543004) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1222-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to 5MOCITYB1 (301563) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1222-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to 5MOCITYB1 (301563) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1223-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to 5LEVASY (300320) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1223-3PH | 3 Phase fault on ECKLES-161 (548808) 161 kV Bus a. Apply fault at the ECKLES-161 (548808) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ECKLES-161 (548808) 161 kV to 5LEVASY (300320) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT122-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FORD 3 (539758) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT122-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FORD 3 (539758) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1224-3PH | 3 Phase fault on ORRICK 5 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161 kV to RICHMND5 (541236) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1224-3PH | 3 Phase fault on ORRICK 5 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161 kV to RICHMND5 (541236) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1225-3PH | 3 Phase fault on SIBLEY 5 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161 kV to SIBLEY 7 (541201) 345 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1225-3PH | 3 Phase fault on SIBLEY 5 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161 kV to SIBLEY 7 (541201) 345 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1226-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPS 5 (541211) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1226-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPS 5 (541211) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1227-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to GRAINVL5 (541226) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1227-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to GRAINVL5 (541226) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1228-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPW 5 (541237) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1228-3PH | 3 Phase fault on BLSPE 5 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161 kV to BLSPW 5 (541237) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1229-3PH | 3 Phase fault on BLSPS 5 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPS 5 (541211) 161 kV to PRALEE 5 (541206) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1229-3PH | 3 Phase fault on BLSPS 5 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPS 5 (541211) 161 kV to PRALEE 5 (541206) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1230-3PH | 3 Phase fault on GRAINVL5 (541226) 161 kV Bus a. Apply fault at the GRAINVL5 (541226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161 kV to OAKGRV 5 (541227) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1230-3PH | 3 Phase fault on GRAINVL5 (541226) 161 kV Bus a. Apply fault at the GRAINVL5 (541226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161 kV to OAKGRV 5 (541227) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1231-3PH | 3 Phase fault on BLSPW 5 (541237) 161 kV Bus a. Apply fault at the BLSPW 5 (541237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPW 5 (541237) 161 kV to LKWOOD 5 (541238) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1231-3PH | 3 Phase fault on BLSPW 5 (541237) 161 kV Bus a. Apply fault at the BLSPW 5 (541237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPW 5 (541237) 161 kV to LKWOOD 5 (541238) 161 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1232-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to KETCHEM7 (541500) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1232-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to KETCHEM7 (541500) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1233-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to HAWTH 7 (542972) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1233-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to HAWTH 7 (542972) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT123-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to GEN-2019-044 (763758) 115 kV Transmission Circuit #1 b.2. UNIT G19-044-GEN1 (763761) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT123-3PH | 3 Phase fault on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to GEN-2019-044 (763758) 115 kV Transmission Circuit #1 b.2. UNIT G19-044-GEN1 (763761) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1234-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to SIB REA1 (541414) 345 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1234-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to SIB REA1 (541414) 345 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1235-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to PHILL 7 (541200) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1235-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to PHILL 7 (541200) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1236-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to 7OVERTON (345408) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1236-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345 kV to 7OVERTON (345408) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1237-3PH | 3 Phase fault on G19-062-TAP (763917) 138 kV Bus a. Apply fault at the G19-062-TAP (763917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-062-TAP (763917) 138 kV to BU11PON4 (533032) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1237-3PH | 3 Phase fault on G19-062-TAP (763917) 138 kV Bus a. Apply fault at the G19-062-TAP (763917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-062-TAP (763917) 138 kV to BU11PON4 (533032) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1238-3PH | 3 Phase fault on G19-062-TAP (763917) 138 kV Bus a. Apply fault at the G19-062-TAP (763917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-062-TAP (763917) 138 kV to ELPASOE4 (533059) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1238-3PH | 3 Phase fault on G19-062-TAP (763917) 138 kV Bus a. Apply fault at the G19-062-TAP (763917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-062-TAP (763917) 138 kV to ELPASOE4 (533059) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1239-3PH | 3 Phase fault on BU11PON4 (533032) 138 kV Bus a. Apply fault at the BU11PON4 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138 kV to WEAVER 4 (532991) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1239-3PH | 3 Phase fault on BU11PON4 (533032) 138 kV Bus a. Apply fault at the BU11PON4 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138 kV to WEAVER 4 (532991) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT12-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to IRONWOOD WF7 (539815) 345 kV Transmission Circuit #1 b.2. UNIT IRONWD-WTG1 (539106) 0.7 kV #1 b.3. UNIT IRONWD-WTG3 (539110) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT12-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to IRONWOOD WF7 (539815) 345 kV Transmission Circuit #1 b.2. UNIT IRONWD-WTG1 (539106) 0.7 kV #1 b.3. UNIT IRONWD-WTG3 (539110) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1240-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to WEAVER 2 (533604) 69 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1240-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to WEAVER 2 (533604) 69 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1241-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to SPRNGDL4 (533067) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1241-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to SPRNGDL4 (533067) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1242-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to ANDOVER4 (533026) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1242-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to ANDOVER4 (533026) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1243-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to TALLGRS4 (532993) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1243-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to TALLGRS4 (532993) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT124-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to POSTROCK7 (530583) 345 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT124-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to POSTROCK7 (530583) 345 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1244-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1244-3PH | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1245-3PH | 3 Phase fault on SPRNGDL4 (533067) 138 kV Bus a. Apply fault at the SPRNGDL4 (533067) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNGDL4 (533067) 138 kV to BEECHTP4 (533028) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1245-3PH | 3 Phase fault on SPRNGDL4 (533067) 138 kV Bus a. Apply fault at the SPRNGDL4 (533067) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNGDL4 (533067) 138 kV to BEECHTP4 (533028) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1246-3PH | 3 Phase fault on ANDOVER4 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER4 (533026) 138 kV to NOEASTE4 (533060) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1246-3PH | 3 Phase fault on ANDOVER4 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER4 (533026) 138 kV to NOEASTE4 (533060) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1247-3PH | 3 Phase fault on TALLGRS4 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALLGRS4 (532993) 138 kV to BUTLERS4 (532989) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1247-3PH | 3 Phase fault on TALLGRS4 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALLGRS4 (532993) 138 kV to BUTLERS4 (532989) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1248-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 2 (533793) 69 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1248-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 2 (533793) 69 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1249-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to 47TH ST4 (533058) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1249-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to 47TH ST4 (533058) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1250-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to FARBER 4 (533042) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1250-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to FARBER 4 (533042) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1251-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 4 (533039) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1251-3PH | 3 Phase fault on ELPASOE4 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASOE4 (533059) 138 kV to ELPASO 4 (533039) 138 kV Transmission Circuit #Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1252-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1252-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1253-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to STEARMN4 (533068) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1253-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to STEARMN4 (533068) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT125-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to BUCKEYE_230 (530702) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT125-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to BUCKEYE_230 (530702) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1254-3PH | 3 Phase fault on STEARMN4 (533068) 138 kV Bus a. Apply fault at the STEARMN4 (533068) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEARMN4 (533068) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1254-3PH | 3 Phase fault on STEARMN4 (533068) 138 kV Bus a. Apply fault at the STEARMN4 (533068) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEARMN4 (533068) 138 kV to ROSEHIL4 (533062) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1255-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1255-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1256-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1256-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1257-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1257-3PH | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138 kV to ROSEHIL7 (532794) 345 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1258-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1258-3PH | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1263-3PH | 3 Phase fault on MEDFORD4 (522397) 138 kV Bus a. Apply fault at the MEDFORD4 (522397) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD4 (522397) 138 kV to PONDCRK4 (522398) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1263-3PH | 3 Phase fault on MEDFORD4 (522397) 138 kV Bus a. Apply fault at the MEDFORD4 (522397) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD4 (522397) 138 kV to PONDCRK4 (522398) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT126-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to KNOLL N 6 (530558) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT126-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to KNOLL N 6 (530558) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1264-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1264-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1265-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to REDNGTN7 (515875) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1265-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to REDNGTN7 (515875) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1266-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to SKELTON7 (515990) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1266-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to SKELTON7 (515990) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1267-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to GEN-2017-164 (762321) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1267-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to GEN-2017-164 (762321) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1268-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) 138 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1268-3PH | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) 138 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1269-3PH | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7 (515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 (515477) 345 kV to CHSHMVW1 (515484) 34.5 kV to CHSHMVWT (515485) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1269-3PH | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7 (515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 (515477) 345 kV to CHSHMVW1 (515484) 34.5 kV to CHSHMVWT (515485) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1270-3PH | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7 (515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 (515477) 345 kV to CHSHMVE1 (515479) 34.5 kV to CHSHMVET (515482) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1270-3PH | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7 (515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 (515477) 345 kV to CHSHMVE1 (515479) 34.5 kV to CHSHMVET (515482) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT127-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to KNOLL S 6 (530720) 230 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT127-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to KNOLL S 6 (530720) 230 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1277-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to GEN-2016-153 (588360) 345 kV Transmission Circuit #1 Trip generator G16-153-GEN1 (588363) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1277-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to GEN-2016-153 (588360) 345 kV Transmission Circuit #1 Trip generator G16-153-GEN1 (588363) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1280-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1280-3PH | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345 kV to RENO 3 (533416) 115 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT128-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT128-3PH | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1287-3PH | 3 Phase fault on G16-111-TAP (587884) 345 kV Bus a. Apply fault at the G16-111-TAP (587884) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-111-TAP (587884) 345 kV to GEN-2016-111 (587880) 345 kV Transmission Circuit #1 Trip generator G16-111-GEN1 (587883) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1287-3PH | 3 Phase fault on G16-111-TAP (587884) 345 kV Bus a. Apply fault at the G16-111-TAP (587884) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-111-TAP (587884) 345 kV to GEN-2016-111 (587880) 345 kV Transmission Circuit #1 Trip generator G16-111-GEN1 (587883) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1288-3PH | 3 Phase fault on BOL 73 5 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161 kV to BOL 73 2 (547528) 69 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1288-3PH | 3 Phase fault on BOL 73 5 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161 kV to BOL 73 2 (547528) 69 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1289-3PH | 3 Phase fault on 47TH ST4 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138 kV to 64TH 4 (533066) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1289-3PH | 3 Phase fault on 47TH ST4 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138 kV to 64TH 4 (533066) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1290-3PH | 3 Phase fault on FARBER 4 (533042) 138 kV Bus a. Apply fault at the FARBER 4 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138 kV to SC10BEL4 (533063) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1290-3PH | 3 Phase fault on FARBER 4 (533042) 138 kV Bus a. Apply fault at the FARBER 4 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138 kV to SC10BEL4 (533063) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1292-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to 59TH ST4 (533029) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1292-3PH | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138 kV to 59TH ST4 (533029) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1293-3PH | 3 Phase fault on STEARMN4 (533068) 138 kV Bus a. Apply fault at the STEARMN4 (533068) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEARMN4 (533068) 138 kV to BOEINGE4 (533030) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1293-3PH | 3 Phase fault on STEARMN4 (533068) 138 kV Bus a. Apply fault at the STEARMN4 (533068) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEARMN4 (533068) 138 kV to BOEINGE4 (533030) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT129-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to POSTROCK6 (530584) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT129-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to POSTROCK6 (530584) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1294-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to FR2EAST7 (532792) 345 kV Transmission Circuit #1 Trip generators FR2W1WF1 (533125),FR2W2WF1 (533126), FR3WTG1 (578533), FR2E1WF1 (533123), FR2E2WF1 (533124) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1294-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to FR2EAST7 (532792) 345 kV Transmission Circuit #1 Trip generators FR2W1WF1 (533125),FR2W2WF1 (533126), FR3WTG1 (578533), FR2E1WF1 (533123), FR2E2WF1 (533124) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT1296-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to GEN-2017-086 (589240) 345 kV Transmission Circuit #1 Trip generator G17-086-GEN1 (589243) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT1296-3PH | 3 Phase fault on G16-153-TAP (588364) 345 kV Bus a. Apply fault at the G16-153-TAP (588364) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-153-TAP (588364) 345 kV to GEN-2017-086 (589240) 345 kV Transmission Circuit #1 Trip generator G17-086-GEN1 (589243) c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT130-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT130-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT131-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to SHAYS_230 (530610) 230 kV Transmission Circuit #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT131-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to SHAYS_230 (530610) 230 kV Transmission Circuit #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT132-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to S HAYS 3 (530553) 115 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT132-3PH | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to S HAYS 3 (530553) 115 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT133-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT133-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT13-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to GEN-2008-124 (579480) 345 kV Transmission Circuit #1 b.2. UNIT G08-124-GEN1 (579483) 0.7 kV #1 b.3. UNIT G08-124-GEN2 (579486) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT13-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to GEN-2008-124 (579480) 345 kV Transmission Circuit #1 b.2. UNIT G08-124-GEN1 (579483) 0.7 kV #1 b.3. UNIT G08-124-GEN2 (579486) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT134-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to LAXTAP 3 (530602) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT134-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to LAXTAP 3 (530602) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT135-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HZRNGPL3 (530609) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT135-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HZRNGPL3 (530609) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT136-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 6 (530680) 230 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT136-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 6 (530680) 230 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT137-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 2 (530563) 69 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT137-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 2 (530563) 69 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT138-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 2 (530563) 69 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT138-3PH | 3 Phase fault on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to HEIZER 2 (530563) 69 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT139-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to HEIZER 3 (530601) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT139-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to HEIZER 3 (530601) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT140-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT140-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT141-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GBENDTP3 (539666) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT141-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GBENDTP3 (539666) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT142-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to ELLSWTP3 (539642) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT142-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to ELLSWTP3 (539642) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT143-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to OTISSUB3 (539684) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT143-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to OTISSUB3 (539684) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT14-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to GEN-2019-030 (763670) 345 kV Transmission Circuit #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.3. UNIT G19-030-GEN2 (763676) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT14-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to GEN-2019-030 (763670) 345 kV Transmission Circuit #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.3. UNIT G19-030-GEN2 (763676) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT144-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND1 (539677) 13.8 kV Two Winding #1 b.2. UNIT GRTBEND1 (539677) 13.8 kV #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT144-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND1 (539677) 13.8 kV Two Winding #1 b.2. UNIT GRTBEND1 (539677) 13.8 kV #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT145-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND6 (539679) 230 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT145-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND6 (539679) 230 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT146-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT146-3PH | 3 Phase fault on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT147-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to G19-054/068 (763857) 230 kV Transmission Circuit #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.4. UNIT G19-068-GEN1 (763970) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT147-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to G19-054/068 (763857) 230 kV Transmission Circuit #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.4. UNIT G19-068-GEN1 (763970) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT148-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT148-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT149-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT149-3PH | 3 Phase fault on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT150-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.4. UNIT G19-068-GEN1 (763970) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT150-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.4. UNIT G19-068-GEN1 (763970) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT151-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT151-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.3. UNIT G19-054-GEN2 (763861) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT152-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-068-XFM1 (763968) 34.5 kV Two Winding #1 b.2. UNIT G19-068-GEN1 (763970) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT152-3PH | 3 Phase fault on G19-054/068 (763857) 230 kV Bus a. Apply fault at the G19-054/068 (763857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-054/068 (763857) 230 kV to G19-068-XFM1 (763968) 34.5 kV Two Winding #1 b.2. UNIT G19-068-GEN1 (763970) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT153-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT153-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT15-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT15-3PH | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT154-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT154-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT155-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to EMCPHER6 (532872) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT155-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to EMCPHER6 (532872) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT156-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to CIRCLE 3 (533413) 115 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT156-3PH | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to CIRCLE 3 (533413) 115 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT157-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT157-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT158-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to SUMMIT 6 (532873) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT158-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to SUMMIT 6 (532873) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT159-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to EMCPHER3 (533417) 115 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT159-3PH | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to EMCPHER3 (533417) 115 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT160-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to REFINRY3 (533427) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT160-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to REFINRY3 (533427) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT161-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to MANVILE3 (533426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT161-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to MANVILE3 (533426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT162-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to EMCPHER6 (532872) 230 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT162-3PH | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to EMCPHER6 (532872) 230 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT163-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to BUFLOCRK6 (530688) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT163-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to BUFLOCRK6 (530688) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT16-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT16-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT164-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT164-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT165-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to RICE 3 (530623) 115 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT165-3PH | 3 Phase fault on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to RICE 3 (530623) 115 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT166-3PH | 3 Phase fault on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT166-3PH | 3 Phase fault on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT167-3PH | 3 Phase fault on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT167-3PH | 3 Phase fault on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT168-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to UNIONRG6 (532874) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT168-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to UNIONRG6 (532874) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT169-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SMOKYHL6 (530592) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT169-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SMOKYHL6 (530592) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT171-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 7 (532773) 345 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT171-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 7 (532773) 345 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT172-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT172-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT173-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT173-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT17-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT17-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT174-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #Z1 b.2. UNIT SVWF3 1 (539120) 0.7 kV #1 b.3. UNIT SVWF1 1 (539116) 0.6 kV #1 b.4. UNIT SVWF2 1 (539136) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT174-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #Z1 b.2. UNIT SVWF3 1 (539120) 0.7 kV #1 b.3. UNIT SVWF1 1 (539116) 0.6 kV #1 b.4. UNIT SVWF2 1 (539136) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT175-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.2. UNIT SVWF1 1 (539116) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT175-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.2. UNIT SVWF1 1 (539116) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT176-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.2. UNIT SVWF2 1 (539136) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT176-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.2. UNIT SVWF2 1 (539136) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT177-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.2. UNIT SVWF3 1 (539120) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT177-3PH | 3 Phase fault on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.2. UNIT SVWF3 1 (539120) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT178-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to ANGUS 3 (530714) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT178-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to ANGUS 3 (530714) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT179-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to CHETOLAH3 (530695) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT179-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to CHETOLAH3 (530695) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT180-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to PFEIFER 3 (530725) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT180-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to PFEIFER 3 (530725) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT181-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to S HAYS6 (530582) 230 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT181-3PH | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to S HAYS6 (530582) 230 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT182-3PH | 3 Phase fault on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT182-3PH | 3 Phase fault on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT183-3PH | 3 Phase fault on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT183-3PH | 3 Phase fault on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.2. UNIT SHAYS_GEN (530614) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT18-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to TRANSFORMER (539813) 345 kV Transmission Circuit #1 b.2. UNIT WTGLVB (539814) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT18-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to TRANSFORMER (539813) 345 kV Transmission Circuit #1 b.2. UNIT WTGLVB (539814) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT184-3PH | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT184-3PH | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT185-3PH | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to HEIZER 3 (530601) 115 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT185-3PH | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to HEIZER 3 (530601) 115 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT186-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT186-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT187-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT187-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT188-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT188-3PH | 3 Phase fault on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT189-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT189-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT190-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to SEWARD 3 (539692) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT190-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to SEWARD 3 (539692) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT191-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT191-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT192-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to ROLLHLS3 (539643) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT192-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to ROLLHLS3 (539643) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT193-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to RUSSELL3 (539701) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT193-3PH | 3 Phase fault on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to RUSSELL3 (539701) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT19-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT19-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT194-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT194-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT195-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT195-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT196-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT196-3PH | 3 Phase fault on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT197-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to G18-116-XFM1 (763330) 34.5 kV Two Winding #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT197-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to G18-116-XFM1 (763330) 34.5 kV Two Winding #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT198-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to G19-051-XFM1 (763824) 34.5 kV Two Winding #1 b.2. UNIT G19-051-GEN1 (763826) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT198-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to G19-051-XFM1 (763824) 34.5 kV Two Winding #1 b.2. UNIT G19-051-GEN1 (763826) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT199-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to GEN-2018-116 (763329) 115 kV Transmission Circuit #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.4. UNIT G19-051-GEN1 (763826) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT199-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to GEN-2018-116 (763329) 115 kV Transmission Circuit #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.4. UNIT G19-051-GEN1 (763826) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT200-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT200-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT201-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT201-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT202-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT202-3PH | 3 Phase fault on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT203-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT203-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT204-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT204-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT205-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to CIRCLE 6 (532871) 230 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT205-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to CIRCLE 6 (532871) 230 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT206-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC GT 3 (533421) 115 kV Transmission Circuit #1 b.2. UNIT HEC GT2 (532696) 13.8 kV #1 b.3. UNIT HEC GT3 (532697) 13.8 kV #1 b.4. UNIT HEC GT4 (532698) 13.8 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT206-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC GT 3 (533421) 115 kV Transmission Circuit #1 b.2. UNIT HEC GT2 (532696) 13.8 kV #1 b.3. UNIT HEC GT3 (532697) 13.8 kV #1 b.4. UNIT HEC GT4 (532698) 13.8 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT207-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to ARKVALJ3 (533412) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT207-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to ARKVALJ3 (533412) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT208-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC 3 (533419) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT208-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC 3 (533419) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT209-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT209-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT210-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT210-3PH | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to RENO 3 (533416) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT212-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.2. UNIT HEC GT2 (532696) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT212-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.2. UNIT HEC GT2 (532696) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT213-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.2. UNIT HEC GT3 (532697) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT213-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.2. UNIT HEC GT3 (532697) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT21-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to GEN-2011-008 (539840) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 b.6. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.7. UNIT G11-008-GEN6 (539853) 0.7 kV #1 b.8. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.9. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT21-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to GEN-2011-008 (539840) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 b.6. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.7. UNIT G11-008-GEN6 (539853) 0.7 kV #1 b.8. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.9. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT214-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.2. UNIT HEC GT4 (532698) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT214-3PH | 3 Phase fault on HEC GT 3 (533421) 115 kV Bus a. Apply fault at the HEC GT 3 (533421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC GT 3 (533421) 115 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.2. UNIT HEC GT4 (532698) 13.8 kV #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT215-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT215-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT216-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to 43LORAN (533440) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT216-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to 43LORAN (533440) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT217-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to HEC 2 (533513) 69 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT217-3PH | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to HEC 2 (533513) 69 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT218-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT218-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT219-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT219-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT220-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to WMCPHER3 (533438) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT220-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to WMCPHER3 (533438) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT221-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to DAVIS 3 (533415) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT221-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to DAVIS 3 (533415) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT222-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to MOUNDRG3 (533429) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT222-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to MOUNDRG3 (533429) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT223-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT223-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT22-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to GEN-2019-058 (763890) 345 kV Transmission Circuit #1 b.2. UNIT G19-058-GEN1 (763893) 0.6 kV #1 b.3. UNIT G19-058-GEN2 (763895) 0.6 kV #1 b.4. UNIT G19-063-GEN1 (763926) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT22-3PH | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to GEN-2019-058 (763890) 345 kV Transmission Circuit #1 b.2. UNIT G19-058-GEN1 (763893) 0.6 kV #1 b.3. UNIT G19-058-GEN2 (763895) 0.6 kV #1 b.4. UNIT G19-063-GEN1 (763926) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT224-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT224-3PH | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT225-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to GEN-2019-014 (763549) 115 kV Transmission Circuit #1 b.2. UNIT G19-014-GEN1 (763552) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT225-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to GEN-2019-014 (763549) 115 kV Transmission Circuit #1 b.2. UNIT G19-014-GEN1 (763552) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT226-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to JONES3 (531379) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT226-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to JONES3 (531379) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT227-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT227-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT228-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT228-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT229-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCGEN1 (531447) 22 kV Two Winding #1 b.2. UNIT HOLCGEN1 (531447) 22 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT229-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCGEN1 (531447) 22 kV Two Winding #1 b.2. UNIT HOLCGEN1 (531447) 22 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT230-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT230-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT231-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCOMB7 (531449) 345 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT231-3PH | 3 Phase fault on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCOMB7 (531449) 345 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT232-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT232-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT233-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to PIONTAP3 (531392) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT233-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to PIONTAP3 (531392) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT234-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to PIERCVL3 (531408) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT234-3PH | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to PIERCVL3 (531408) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT235-3PH | 3 Phase fault on PIERCVL3 (531408) 115 kV Bus a. Apply fault at the PIERCVL3 (531408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIERCVL3 (531408) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT235-3PH | 3 Phase fault on PIERCVL3 (531408) 115 kV Bus a. Apply fault at the PIERCVL3 (531408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIERCVL3 (531408) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT236-3PH | 3 Phase fault on PIERCVL3 (531408) 115 kV Bus a. Apply fault at the PIERCVL3 (531408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIERCVL3 (531408) 115 kV to SANTAFE3 (531213) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT236-3PH | 3 Phase fault on PIERCVL3 (531408) 115 kV Bus a. Apply fault at the PIERCVL3 (531408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIERCVL3 (531408) 115 kV to SANTAFE3 (531213) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT237-3PH | 3 Phase fault on JONES3 (531379) 115 kV Bus a. Apply fault at the JONES3 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT237-3PH | 3 Phase fault on JONES3 (531379) 115 kV Bus a. Apply fault at the JONES3 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT238-3PH | 3 Phase fault on JONES3 (531379) 115 kV Bus a. Apply fault at the JONES3 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115 kV to JAMESON3 (531426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT238-3PH | 3 Phase fault on JONES3 (531379) 115 kV Bus a. Apply fault at the JONES3 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115 kV to JAMESON3 (531426) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT239-3PH | 3 Phase fault on JAMESON3 (531426) 115 kV Bus a. Apply fault at the JAMESON3 (531426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESON3 (531426) 115 kV to JONES3 (531379) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT239-3PH | 3 Phase fault on JAMESON3 (531426) 115 kV Bus a. Apply fault at the JAMESON3 (531426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESON3 (531426) 115 kV to JONES3 (531379) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT240-3PH | 3 Phase fault on JAMESON3 (531426) 115 kV Bus a. Apply fault at the JAMESON3 (531426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESON3 (531426) 115 kV to LOWETAP3 (531425) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT240-3PH | 3 Phase fault on JAMESON3 (531426) 115 kV Bus a. Apply fault at the JAMESON3 (531426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESON3 (531426) 115 kV to LOWETAP3 (531425) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT241-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT241-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT242-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to KSAVWTP3 (531480) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT242-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to KSAVWTP3 (531480) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT243-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to SWNDTAP3 (531476) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT243-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to SWNDTAP3 (531476) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT24-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to G16-050-TAP (560082) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT24-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to G16-050-TAP (560082) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT244-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to GARDNCY2 (531423) 69 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT244-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to GARDNCY2 (531423) 69 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT245-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.2. UNIT S2 GEN 1 (531459) 13.8 kV #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT245-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.2. UNIT S2 GEN 1 (531459) 13.8 kV #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT246-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT246-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT247-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.2. UNIT S4 GEN 1 (531461) 13.2 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT247-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.2. UNIT S4 GEN 1 (531461) 13.2 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT248-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.2. UNIT S5 GEN 1 (531462) 13.2 kV #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT248-3PH | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.2. UNIT S5 GEN 1 (531462) 13.2 kV #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT249-3PH | 3 Phase fault on GARDNCY2 (531423) 69 kV Bus a. Apply fault at the GARDNCY2 (531423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69 kV to GRDNCTY3 (531445) 115 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT249-3PH | 3 Phase fault on GARDNCY2 (531423) 69 kV Bus a. Apply fault at the GARDNCY2 (531423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69 kV to GRDNCTY3 (531445) 115 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT250-3PH | 3 Phase fault on GARDNCY2 (531423) 69 kV Bus a. Apply fault at the GARDNCY2 (531423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69 kV to GC-W 1 (531422) 34.5 kV to GCWHEAT1 (531255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT250-3PH | 3 Phase fault on GARDNCY2 (531423) 69 kV Bus a. Apply fault at the GARDNCY2 (531423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69 kV to GC-W 1 (531422) 34.5 kV to GCWHEAT1 (531255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT251-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT251-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT252-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to IRSKDOL3 (531478) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT252-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to IRSKDOL3 (531478) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT253-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to S. WIND3 (531477) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT253-3PH | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to S. WIND3 (531477) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT25-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT25-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT254-3PH | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSAVWTP3 (531480) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT254-3PH | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSAVWTP3 (531480) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT255-3PH | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSAVWTP3 (531480) 115 kV to DOBSON 3 (531419) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT255-3PH | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSAVWTP3 (531480) 115 kV to DOBSON 3 (531419) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT256-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT256-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT257-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SAT-TAP3 (531442) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT257-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SAT-TAP3 (531442) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT258-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to PNTPR-GOAB3 (531203) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT258-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to PNTPR-GOAB3 (531203) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT259-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SUBLETE3 (531398) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT259-3PH | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SUBLETE3 (531398) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT260-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT260-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT261-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to PK_GOAB3 (531400) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT261-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to PK_GOAB3 (531400) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT262-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to WILLIAM3 (531440) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT262-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to WILLIAM3 (531440) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT263-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to LAKIN3 (531399) 34.5 kV to FLETCHER-T (531500) 13.2 kV Three Winding #1 b.2. UNIT LAKIN3 (531399) 34.5 kV #1 b.3. UNIT LAKIN3 (531399) 34.5 kV #2 b.4. UNIT LAKIN3 (531399) 34.5 kV #3 b.5. UNIT LAKIN3 (531399) 34.5 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT263-3PH | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115 kV to LAKIN3 (531399) 34.5 kV to FLETCHER-T (531500) 13.2 kV Three Winding #1 b.2. UNIT LAKIN3 (531399) 34.5 kV #1 b.3. UNIT LAKIN3 (531399) 34.5 kV #2 b.4. UNIT LAKIN3 (531399) 34.5 kV #3 b.5. UNIT LAKIN3 (531399) 34.5 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT26-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to POSTROCK6 (530584) 230 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT26-3PH | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to POSTROCK6 (530584) 230 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT264-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT264-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT265-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to PIONEER3 (531391) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT265-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to PIONEER3 (531391) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT266-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to PUCKET 3 (531375) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT266-3PH | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to PUCKET 3 (531375) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT267-3PH | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLIAM3 (531440) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT267-3PH | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLIAM3 (531440) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT268-3PH | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLIAM3 (531440) 115 kV to SYRACUS3 (531437) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT268-3PH | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLIAM3 (531440) 115 kV to SYRACUS3 (531437) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT270-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT270-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT271-3PH | 3 Phase fault on GEN-2019-044 (763758) 115 kV Bus a. Apply fault at the GEN-2019-044 (763758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2019-044 (763758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. UNIT G19-044-GEN1 (763761) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT271-3PH | 3 Phase fault on GEN-2019-044 (763758) 115 kV Bus a. Apply fault at the GEN-2019-044 (763758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2019-044 (763758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. UNIT G19-044-GEN1 (763761) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT272-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT272-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT273-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to W-DODGE3 (539699) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT273-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to W-DODGE3 (539699) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT27-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT27-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT274-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to S-DODGE1 (539727) 34.5 kV to S-DODG-T (539930) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT274-3PH | 3 Phase fault on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to S-DODGE1 (539727) 34.5 kV to S-DODG-T (539930) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT275-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT275-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT276-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to GYCOTAP3 (539778) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT276-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to GYCOTAP3 (539778) 115 kV Transmission Circuit #1 b.2. GRAYCNTY_GEN (539123) 0.7 kV Trip Bus b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT277-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to NW-DGTP3 (539628) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT277-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to NW-DGTP3 (539628) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT278-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to W-DODGE1 (539735) 34.5 kV to W-DODG-T (539939) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT278-3PH | 3 Phase fault on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to W-DODGE1 (539735) 34.5 kV to W-DODG-T (539939) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT279-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT279-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT280-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to SSTARTP3 (539763) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT280-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to SSTARTP3 (539763) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT281-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT281-3PH | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT282-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to FORD 3 (539758) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT282-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to FORD 3 (539758) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT283-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to SSTARW 3 (539761) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT283-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to SSTARW 3 (539761) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT28-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT28-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT284-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to GRNBURG3 (539664) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT284-3PH | 3 Phase fault on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to GRNBURG3 (539664) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT285-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT285-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT286-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT286-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT287-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to DCBEEF3 (539645) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT287-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to DCBEEF3 (539645) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT288-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to CRKCK 3 (539783) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT288-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to CRKCK 3 (539783) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Controllers needs to be tuned/validated for 539111[ENSIGN_WTG1 0.6900]1 to avoid unsettled response (hiccup)
03 - Central | 25S | Transfer | G3_FLT289-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 b.2. UNIT FTDDGDV1 (539715) 34.5 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT289-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 b.2. UNIT FTDDGDV1 (539715) 34.5 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT290-3PH | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT290-3PH | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT291-3PH | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115 kV to EDODGE 3 (539740) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT291-3PH | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115 kV to EDODGE 3 (539740) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT292-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT292-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Controllers needs to be tuned/validated for 539111[ENSIGN_WTG1 0.6900]1 to avoid unsettled response (hiccup)
03 - Central | 25S | Transfer | G3_FLT293-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to ENSNGW 3 (539784) 115 kV Transmission Circuit #1 b.2. UNIT ENSIGN_WTG1 (539111) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT293-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to ENSNGW 3 (539784) 115 kV Transmission Circuit #1 b.2. UNIT ENSIGN_WTG1 (539111) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT29-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25W | Transfer | G3_FLT29-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25S | Transfer | G3_FLT294-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to CUDAHY 3 (539659) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT294-3PH | 3 Phase fault on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to CUDAHY 3 (539659) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT295-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to FTDODGP1 (539670) 15 kV Two Winding #1 b.2. UNIT FTDODGP1 (539670) 15 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT295-3PH | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to FTDODGP1 (539670) 15 kV Two Winding #1 b.2. UNIT FTDODGP1 (539670) 15 kV #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT296-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to EMCPHER6 (532872) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT296-3PH | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to EMCPHER6 (532872) 230 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT297-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115 kV to SPERVIL7 (531469) 345 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT297-3PH | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115 kV to SPERVIL7 (531469) 345 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT298-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT298-3PH | 3 Phase fault on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT299-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to GBENDTP3 (539666) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT299-3PH | 3 Phase fault on 2ND-KS 3 (539689) 115 kV Bus a. Apply fault at the 2ND-KS 3 (539689) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ND-KS 3 (539689) 115 kV to GBENDTP3 (539666) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT300-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.4. UNIT G19-051-GEN1 (763826) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT300-3PH | 3 Phase fault on GEN-2018-116 (763329) 115 kV Bus a. Apply fault at the GEN-2018-116 (763329) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-116 (763329) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 b.2. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.3. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.4. UNIT G19-051-GEN1 (763826) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT301-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to DGRASSE7 (515852) 345 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT301-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to DGRASSE7 (515852) 345 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT302-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to MOORLND4 (520999) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT302-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to MOORLND4 (520999) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT303-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT303-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT30-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to HOLCOMB3 (531448) 115 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT30-3PH | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to HOLCOMB3 (531448) 115 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT304-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT304-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT305-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to GEN-2015-095 (585300) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT305-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to GEN-2015-095 (585300) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT306-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to GEN-2019-045 (763769) 138 kV Transmission Circuit #1 b.2. UNIT G19-045-GEN1 (763772) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT306-3PH | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to GEN-2019-045 (763769) 138 kV Transmission Circuit #1 b.2. UNIT G19-045-GEN1 (763772) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT307-3PH | 3 Phase fault on THISTLE4 (539804) 138 kV Bus a. Apply fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THISTLE4 (539804) 138 kV to FLATRDG4 (539638) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT307-3PH | 3 Phase fault on THISTLE4 (539804) 138 kV Bus a. Apply fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THISTLE4 (539804) 138 kV to FLATRDG4 (539638) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT308-3PH | 3 Phase fault on THISTLE4 (539804) 138 kV Bus a. Apply fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THISTLE4 (539804) 138 kV to THISTLE7 (539801) 345 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT308-3PH | 3 Phase fault on THISTLE4 (539804) 138 kV Bus a. Apply fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THISTLE4 (539804) 138 kV to THISTLE7 (539801) 345 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT309-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to THISTLE4 (539804) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT309-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to THISTLE4 (539804) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT310-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to BARBER 4 (539674) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT310-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to BARBER 4 (539674) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT311-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to FLATRWD4 (539631) 138 kV Transmission Circuit #1 b.2. UNIT FLTRDG-WG1 (539114) 0.7 kV #1 b.3. UNIT FLTRDG-WG2 (578521) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT311-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to FLATRWD4 (539631) 138 kV Transmission Circuit #1 b.2. UNIT FLTRDG-WG1 (539114) 0.7 kV #1 b.3. UNIT FLTRDG-WG2 (578521) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT312-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to HARPER 4 (539668) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT312-3PH | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to HARPER 4 (539668) 138 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT31-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT31-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT316-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT316-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT317-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to BUSHTON3 (530681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT317-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to BUSHTON3 (530681) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT318-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to BUSHTONW 3 (530718) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT318-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to BUSHTONW 3 (530718) 115 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT319-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to RICE 6 (530686) 230 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT319-3PH | 3 Phase fault on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to RICE 6 (530686) 230 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT32-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to MINGO 7 (531451) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT32-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to MINGO 7 (531451) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT33-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to SETAB 3 (531464) 115 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT33-3PH | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to SETAB 3 (531464) 115 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT34-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25W | Transfer | G3_FLT34-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25S | Transfer | G3_FLT35-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to BUFF_DUNES 7 (523118) 345 kV Transmission Circuit #1 b.2. UNIT BUFF_DUNES23 (523061) 0.7 kV #1 b.3. UNIT BUFF_DUNES13 (523062) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT35-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to BUFF_DUNES 7 (523118) 345 kV Transmission Circuit #1 b.2. UNIT BUFF_DUNES23 (523061) 0.7 kV #1 b.3. UNIT BUFF_DUNES13 (523062) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT36-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT36-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to G18-030-TAP (762662) 345 kV Transmission Circuit #1 b.2. UNIT G18-030GEN1 (762661) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT37-3PH | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to G18-030-TAP (762662) 345 kV Transmission Circuit #1 b.2. UNIT G18-030GEN1 (762661) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT39-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.3. UNIT G19-030-GEN2 (763676) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT39-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.3. UNIT G19-030-GEN2 (763676) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT40-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT40-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 b.2. UNIT G19-030-GEN1 (763673) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT41-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to G19-030-XFM2 (763674) 34.5 kV Two Winding #1 b.2. UNIT G19-030-GEN2 (763676) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT41-3PH | 3 Phase fault on GEN-2019-030 (763670) 345 kV Bus a. Apply fault at the GEN-2019-030 (763670) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2019-030 (763670) 345 kV to G19-030-XFM2 (763674) 34.5 kV Two Winding #1 b.2. UNIT G19-030-GEN2 (763676) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT42-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 b.6. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.7. UNIT G11-008-GEN6 (539853) 0.7 kV #1 b.8. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.9. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT42-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 b.6. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.7. UNIT G11-008-GEN6 (539853) 0.7 kV #1 b.8. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.9. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT43-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-1 (539841) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT43-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-1 (539841) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN1 (539845) 0.7 kV #1 b.3. UNIT G11-008-GEN2 (539846) 0.7 kV #1 b.4. UNIT G11-008-GEN3 (539847) 0.7 kV #1 b.5. UNIT G11-008-GEN4 (539848) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT44-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-2 (539855) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.3. UNIT G11-008-GEN6 (539853) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT44-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-2 (539855) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN5 (539852) 0.7 kV #1 b.3. UNIT G11-008-GEN6 (539853) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT45-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-3 (539857) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.3. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT45-3PH | 3 Phase fault on GEN-2011-008 (539840) 345 kV Bus a. Apply fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2011-008 (539840) 345 kV to G-2011-008-3 (539857) 345 kV Transmission Circuit #1 b.2. UNIT G11-008-GEN7 (539858) 0.7 kV #1 b.3. UNIT G11-008-GEN8 (539859) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT46-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT46-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT48-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to GEN-2018-049 (762834) 345 kV Transmission Circuit #1 b.2. UNIT G18-049-GEN1 (762837) 0.7 kV #1 b.3. UNIT G18-108-GEN1 (763287) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT48-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to GEN-2018-049 (762834) 345 kV Transmission Circuit #1 b.2. UNIT G18-049-GEN1 (762837) 0.7 kV #1 b.3. UNIT G18-108-GEN1 (763287) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT49-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to GEN-2017-018 (588630) 345 kV Transmission Circuit #1 b.2. UNIT G17-018-GEN1 (588633) 0.6 kV #1 b.3. UNIT G17-018-GEN2 (588637) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT49-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to GEN-2017-018 (588630) 345 kV Transmission Circuit #1 b.2. UNIT G17-018-GEN1 (588633) 0.6 kV #1 b.3. UNIT G17-018-GEN2 (588637) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT500-SB | Single Phase Fault with Stuck Breaker on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #1 b.3. UNIT G19-053-GEN1 (763849) 0.7 kV #1 b.4. UNIT G19-055-GEN1 (763871) 0.6 kV #1 b.5. UNIT G19-055-GEN2 (763872) 0.6 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT500-SB | Single Phase Fault with Stuck Breaker on G19-055-TAP (763850) 230 kV Bus a. Apply fault at the G19-055-TAP (763850) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #1 b.3. UNIT G19-053-GEN1 (763849) 0.7 kV #1 b.4. UNIT G19-055-GEN1 (763871) 0.6 kV #1 b.5. UNIT G19-055-GEN2 (763872) 0.6 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT501-SB | Single Phase Fault with Stuck Breaker on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPRVILL-EHVB (539117) 230 kV Transmission Circuit #Z1 b.2. SPEARVL6 (539695) 230 kV to SPERVIL7 (531469) 345 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. UNIT SVWF2 1 (539136) 0.6 kV #1 b.4. UNIT SVWF1 1 (539116) 0.6 kV #1 b.5. UNIT SVWF3 1 (539120) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT501-SB | Single Phase Fault with Stuck Breaker on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230 kV to SPRVILL-EHVB (539117) 230 kV Transmission Circuit #Z1 b.2. SPEARVL6 (539695) 230 kV to SPERVIL7 (531469) 345 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. UNIT SVWF2 1 (539136) 0.6 kV #1 b.4. UNIT SVWF1 1 (539116) 0.6 kV #1 b.5. UNIT SVWF3 1 (539120) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT502-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT502-SB | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230 kV to G19-055-TAP (763850) 230 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT50-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to DGRASSE7 (515852) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT50-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to DGRASSE7 (515852) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT504-SB | Single Phase Fault with Stuck Breaker on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230 kV to G19-054/068 (763857) 230 kV Transmission Circuit #1 b.3. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.4. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.5. UNIT G19-068-GEN1 (763970) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT504-SB | Single Phase Fault with Stuck Breaker on G19-054-TAP (763862) 230 kV Bus a. Apply fault at the G19-054-TAP (763862) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. G19-054-TAP (763862) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230 kV to G19-054/068 (763857) 230 kV Transmission Circuit #1 b.3. UNIT G19-054-GEN1 (763860) 0.6 kV #1 b.4. UNIT G19-054-GEN2 (763861) 0.6 kV #1 b.5. UNIT G19-068-GEN1 (763970) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT505-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230 kV to CIRCLE 3 (533413) 115 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT505-SB | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230 kV to G19-054-TAP (763862) 230 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230 kV to CIRCLE 3 (533413) 115 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT506-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to BUFLOCRK6 (530688) 230 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230 kV to RICE 3 (530623) 115 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT506-SB | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply fault at the RICE 6 (530686) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230 kV to BUFLOCRK6 (530688) 230 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230 kV to RICE 3 (530623) 115 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT507-SB | Single Phase Fault with Stuck Breaker on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 b.2. BUFLOCRK6 (530688) 230 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT507-SB | Single Phase Fault with Stuck Breaker on BUFLOCRK6 (530688) 230 kV Bus a. Apply fault at the BUFLOCRK6 (530688) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUFLOCRK6 (530688) 230 kV to RICE 6 (530686) 230 kV Transmission Circuit #1 b.2. BUFLOCRK6 (530688) 230 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT508-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230 kV to EMCPHER3 (533417) 115 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT508-SB | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230 kV to CIRCLE 6 (532871) 230 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230 kV to EMCPHER3 (533417) 115 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT509-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SMOKYHL6 (530592) 230 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT509-SB | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230 kV to SMOKYHL6 (530592) 230 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230 kV to SUMMIT 3 (533381) 115 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT510-SB | Single Phase Fault with Stuck Breaker on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to REFINRY3 (533427) 115 kV Transmission Circuit #1 b.2. EMCPHER3 (533417) 115 kV to EMCPHER6 (532872) 230 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT510-SB | Single Phase Fault with Stuck Breaker on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115 kV to REFINRY3 (533427) 115 kV Transmission Circuit #1 b.2. EMCPHER3 (533417) 115 kV to EMCPHER6 (532872) 230 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT511-SB | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115 kV to ELLSWTP3 (539642) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT511-SB | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 (539678) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115 kV to N-GBEND3 (539681) 115 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115 kV to ELLSWTP3 (539642) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT512-SB | Single Phase Fault with Stuck Breaker on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT512-SB | Single Phase Fault with Stuck Breaker on OTISSUB3 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 (539684) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. OTISSUB3 (539684) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. OTISSUB3 (539684) 115 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT513-SB | Single Phase Fault with Stuck Breaker on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115 kV to RUSSELL3 (539701) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT513-SB | Single Phase Fault with Stuck Breaker on ELLSWTP3 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 (539642) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115 kV to RUSSELL3 (539701) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT514-SB | Single Phase Fault with Stuck Breaker on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115 kV to SEWARD 3 (539692) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT514-SB | Single Phase Fault with Stuck Breaker on GBENDTP3 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 (539666) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115 kV to SEWARD 3 (539692) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT515-SB | Single Phase Fault with Stuck Breaker on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. N-GBEND3 (539681) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT515-SB | Single Phase Fault with Stuck Breaker on N-GBEND3 (539681) 115 kV Bus a. Apply fault at the N-GBEND3 (539681) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. N-GBEND3 (539681) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. N-GBEND3 (539681) 115 kV to 24-FREY3 (539661) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT516-SB | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115 kV to HEIZER 6 (530680) 230 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT516-SB | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 (530601) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115 kV to GRTBEND3 (539678) 115 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115 kV to HEIZER 6 (530680) 230 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT517-SB | Single Phase Fault with Stuck Breaker on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230 kV to HEIZER 3 (530601) 115 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT517-SB | Single Phase Fault with Stuck Breaker on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230 kV to HEIZER 3 (530601) 115 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT518-SB | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230 kV to POSTROCK6 (530584) 230 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT518-SB | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230 kV to GRTBEND6 (539679) 230 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230 kV to POSTROCK6 (530584) 230 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT519-SB | Single Phase Fault with Stuck Breaker on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. SHAYS_230 (530610) 230 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.3. UNIT SHAYS_GEN (530614) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT519-SB | Single Phase Fault with Stuck Breaker on SHAYS_230 (530610) 230 kV Bus a. Apply fault at the SHAYS_230 (530610) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SHAYS_230 (530610) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. SHAYS_230 (530610) 230 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.3. UNIT SHAYS_GEN (530614) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT520-SB | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230 kV to BUCKEYE_230 (530702) 230 kV Transmission Circuit #1 b.3. UNIT BUCKE_WTG (530705) 0.7 kV #1 b.4. UNIT BUCKW_WTG (530708) 0.7 kV #1 b.5. UNIT G16-160-GEN1 (588451) 0.5 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT520-SB | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230 kV to S HAYS6 (530582) 230 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230 kV to BUCKEYE_230 (530702) 230 kV Transmission Circuit #1 b.3. UNIT BUCKE_WTG (530705) 0.7 kV #1 b.4. UNIT BUCKW_WTG (530708) 0.7 kV #1 b.5. UNIT G16-160-GEN1 (588451) 0.5 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT521-SB | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to CHETOLAH3 (530695) 115 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115 kV to S HAYS6 (530582) 230 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT521-SB | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115 kV to CHETOLAH3 (530695) 115 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115 kV to S HAYS6 (530582) 230 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT522-SB | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #Z1 b.2. SPRVILL-EHVB (539117) 230 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.3. UNIT SVWF2 1 (539136) 0.6 kV #1 b.4. UNIT SVWF1 1 (539116) 0.6 kV #1 b.5. UNIT SVWF3 1 (539120) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT522-SB | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB (539117) 230 kV Bus a. Apply fault at the SPRVILL-EHVB (539117) 230 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPRVILL-EHVB (539117) 230 kV to SPEARVL6 (539695) 230 kV Transmission Circuit #Z1 b.2. SPRVILL-EHVB (539117) 230 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.3. UNIT SVWF2 1 (539136) 0.6 kV #1 b.4. UNIT SVWF1 1 (539116) 0.6 kV #1 b.5. UNIT SVWF3 1 (539120) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT52-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT52-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT523-SB | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115 kV to GEN-2019-044 (763758) 115 kV Transmission Circuit #1 b.3. UNIT G19-044-GEN1 (763761) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT523-SB | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 (539771) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115 kV to GEN-2019-044 (763758) 115 kV Transmission Circuit #1 b.3. UNIT G19-044-GEN1 (763761) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT524-SB | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC 3 (533419) 115 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115 kV to CIRCLE 6 (532871) 230 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT524-SB | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115 kV to HEC 3 (533419) 115 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115 kV to CIRCLE 6 (532871) 230 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT525-SB | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115 kV to 43LORAN (533440) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT525-SB | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115 kV to CIRCLE 3 (533413) 115 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115 kV to 43LORAN (533440) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT526-SB | Single Phase Fault with Stuck Breaker on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT526-SB | Single Phase Fault with Stuck Breaker on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115 kV to RENO 7 (532771) 345 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT527-SB | Single Phase Fault with Stuck Breaker on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to GEN-2018-116 (763329) 115 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 b.3. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.4. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.5. UNIT G19-051-GEN1 (763826) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT527-SB | Single Phase Fault with Stuck Breaker on 24-FREY3 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 (539661) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115 kV to GEN-2018-116 (763329) 115 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115 kV to 2ND-KS 3 (539689) 115 kV Transmission Circuit #1 b.3. UNIT G18-116-GEN1 (763332) 0.6 kV #1 b.4. UNIT G18-116-GEN2 (763335) 0.6 kV #1 b.5. UNIT G19-051-GEN1 (763826) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT529-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCGEN1 (531447) 22 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115 kV to GEN-2019-014 (763549) 115 kV Transmission Circuit #1 b.3. UNIT HOLCGEN1 (531447) 22 kV #1 b.4. UNIT G19-014-GEN1 (763552) 0.6 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT529-SB | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115 kV to HOLCGEN1 (531447) 22 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115 kV to GEN-2019-014 (763549) 115 kV Transmission Circuit #1 b.3. UNIT HOLCGEN1 (531447) 22 kV #1 b.4. UNIT G19-014-GEN1 (763552) 0.6 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT530-SB | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to KSAVWTP3 (531480) 115 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT530-SB | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115 kV to KSAVWTP3 (531480) 115 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT531-SB | Single Phase Fault with Stuck Breaker on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115 kV to IRSKDOL3 (531478) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT531-SB | Single Phase Fault with Stuck Breaker on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SWNDTAP3 (531476) 115 kV to GRDNCTY3 (531445) 115 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115 kV to IRSKDOL3 (531478) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT532-SB | Single Phase Fault with Stuck Breaker on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115 kV to PIONTAP3 (531392) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT532-SB | Single Phase Fault with Stuck Breaker on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115 kV to HOLCOMB3 (531448) 115 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115 kV to PIONTAP3 (531392) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT533-SB | Single Phase Fault with Stuck Breaker on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SAT-TAP3 (531442) 115 kV Transmission Circuit #1 b.2. PIONTAP3 (531392) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT533-SB | Single Phase Fault with Stuck Breaker on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115 kV to SAT-TAP3 (531442) 115 kV Transmission Circuit #1 b.2. PIONTAP3 (531392) 115 kV to PLYMELL3 (531393) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT534-SB | Single Phase Fault with Stuck Breaker on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 b.2. PK_GOAB3 (531400) 115 kV to PIONEER3 (531391) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT534-SB | Single Phase Fault with Stuck Breaker on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. PK_GOAB3 (531400) 115 kV to FLETCHR3 (531420) 115 kV Transmission Circuit #1 b.2. PK_GOAB3 (531400) 115 kV to PIONEER3 (531391) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT535-SB | Single Phase Fault with Stuck Breaker on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to CRKCK 3 (539783) 115 kV Transmission Circuit #1 b.2. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT535-SB | Single Phase Fault with Stuck Breaker on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115 kV to CRKCK 3 (539783) 115 kV Transmission Circuit #1 b.2. FTDODGE3 (539671) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Controllers needs to be tuned/validated for 539111[ENSIGN_WTG1 0.6900]1 to avoid unsettled response (hiccup)
03 - Central | 25S | Transfer | G3_FLT536-SB | Single Phase Fault with Stuck Breaker on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 b.2. CRKCK 3 (539783) 115 kV to CUDAHY 3 (539659) 115 kV Transmission Circuit #1 b.3. UNIT ENSIGN_WTG1 (539111) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT536-SB | Single Phase Fault with Stuck Breaker on CRKCK 3 (539783) 115 kV Bus a. Apply fault at the CRKCK 3 (539783) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CRKCK 3 (539783) 115 kV to FTDODGE3 (539671) 115 kV Transmission Circuit #1 b.2. CRKCK 3 (539783) 115 kV to CUDAHY 3 (539659) 115 kV Transmission Circuit #1 b.3. UNIT ENSIGN_WTG1 (539111) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT537-SB | Single Phase Fault with Stuck Breaker on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115 kV to SSTARTP3 (539763) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT537-SB | Single Phase Fault with Stuck Breaker on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115 kV to SSTARTP3 (539763) 115 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT538-SB | Single Phase Fault with Stuck Breaker on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to SSTARW 3 (539761) 115 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115 kV to GRNBURG3 (539664) 115 kV Transmission Circuit #1 b.3. UNIT SSWIND 1 (539100) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT538-SB | Single Phase Fault with Stuck Breaker on SSTARTP3 (539763) 115 kV Bus a. Apply fault at the SSTARTP3 (539763) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SSTARTP3 (539763) 115 kV to SSTARW 3 (539761) 115 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115 kV to GRNBURG3 (539664) 115 kV Transmission Circuit #1 b.3. UNIT SSWIND 1 (539100) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT539-SB | Single Phase Fault with Stuck Breaker on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. S-DODGE3 (539688) 115 kV to W-DODGE3 (539699) 115 kV Transmission Circuit #1 b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT539-SB | Single Phase Fault with Stuck Breaker on S-DODGE3 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 (539688) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 b.2. S-DODGE3 (539688) 115 kV to W-DODGE3 (539699) 115 kV Transmission Circuit #1 b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT540-SB | Single Phase Fault with Stuck Breaker on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to GYCOTAP3 (539778) 115 kV Transmission Circuit #1 b.2. W-DODGE3 (539699) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT540-SB | Single Phase Fault with Stuck Breaker on W-DODGE3 (539699) 115 kV Bus a. Apply fault at the W-DODGE3 (539699) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. W-DODGE3 (539699) 115 kV to GYCOTAP3 (539778) 115 kV Transmission Circuit #1 b.2. W-DODGE3 (539699) 115 kV to S-DODGE3 (539688) 115 kV Transmission Circuit #1 b.3. UNIT GRAYCNTY_GEN (539123) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT541-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138 kV to DGRASSE7 (515852) 345 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT541-SB | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138 kV to DGRASSE7 (515852) 345 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT542-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to THISTLE4 (539804) 138 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138 kV to HARPER 4 (539668) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT542-SB | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138 kV to THISTLE4 (539804) 138 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138 kV to HARPER 4 (539668) 138 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to THISTLE4 (539804) 138 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT54-3PH | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345 kV to THISTLE4 (539804) 138 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT543-SB | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115 kV to RICE 6 (530686) 230 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT543-SB | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply fault at the RICE 3 (530623) 115 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115 kV to LYONS 3 (530620) 115 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115 kV to RICE 6 (530686) 230 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT55-3PH | 3 Phase fault on GEN-2018-049 (762834) 345 kV Bus a. Apply fault at the GEN-2018-049 (762834) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-049 (762834) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 b.2. UNIT G18-049-GEN1 (762837) 0.7 kV #1 b.3. UNIT G18-108-GEN1 (763287) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT55-3PH | 3 Phase fault on GEN-2018-049 (762834) 345 kV Bus a. Apply fault at the GEN-2018-049 (762834) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-049 (762834) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 b.2. UNIT G18-049-GEN1 (762837) 0.7 kV #1 b.3. UNIT G18-108-GEN1 (763287) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT57-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT57-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT59-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT59-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT600-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to POSTROCK7 (530583) 345 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT600-SB | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345 kV to POSTROCK7 (530583) 345 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT601-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to G16-050-TAP (560082) 345 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT601-SB | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345 kV to G16-050-TAP (560082) 345 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT602-SB | Single Phase Fault with Stuck Breaker on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 b.3. UNIT CIMARON-GEN1 (531603) 0.7 kV #1 b.4. UNIT CIMARON_WTG1 (531605) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT602-SB | Single Phase Fault with Stuck Breaker on BUCKNER7 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 (531501) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 b.3. UNIT CIMARON-GEN1 (531603) 0.7 kV #1 b.4. UNIT CIMARON_WTG1 (531605) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT603-SB | Single Phase Fault with Stuck Breaker on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345 kV to GEN-2019-030 (763670) 345 kV Transmission Circuit #1 b.3. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.4. UNIT G19-030-GEN2 (763676) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT603-SB | Single Phase Fault with Stuck Breaker on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345 kV to SPERVIL7 (531469) 345 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345 kV to GEN-2019-030 (763670) 345 kV Transmission Circuit #1 b.3. UNIT G19-030-GEN1 (763673) 0.7 kV #1 b.4. UNIT G19-030-GEN2 (763676) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT604-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT604-SB | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345 kV to G16-046-TAP (560080) 345 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT605-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT605-SB | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT606-SB | Single Phase Fault with Stuck Breaker on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to MINGO 7 (531451) 345 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT606-SB | Single Phase Fault with Stuck Breaker on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345 kV to MINGO 7 (531451) 345 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345 kV to HOLCOMB7 (531449) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT607-SB | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to G18-030-TAP (762662) 345 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV Transmission Circuit #1 b.3. UNIT G18-030GEN1 (762661) 0.7 kV #1 b.4. UNIT BUFF_DUNES13 (523062) 0.7 kV #1 b.5. UNIT BUFF_DUNES23 (523061) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT607-SB | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345 kV to G18-030-TAP (762662) 345 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV Transmission Circuit #1 b.3. UNIT G18-030GEN1 (762661) 0.7 kV #1 b.4. UNIT BUFF_DUNES13 (523062) 0.7 kV #1 b.5. UNIT BUFF_DUNES23 (523061) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT608-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. Thistle7 (539801) to Buffalo7 (532782) 345kV CKT 1 line b.2. Thistle7 (539801) to CLARKCOUNTY7 (539800) 345kV CKT 1 line | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT608-SB | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. Thistle7 (539801) to Buffalo7 (532782) 345kV CKT 1 line b.2. Thistle7 (539801) to CLARKCOUNTY7 (539800) 345kV CKT 1 line | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT609-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT609-SB | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT610-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GUTHRIE7 (515961) 345 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345 kV to BOBCAT 7 (516106) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT610-SB | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GUTHRIE7 (515961) 345 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345 kV to BOBCAT 7 (516106) 345 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT611-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT611-SB | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT612-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT612-SB | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 16 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT61-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to DGRASSE4 (515853) 138 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT61-3PH | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345 kV to DGRASSE4 (515853) 138 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT614-SB | Single Phase Fault with Stuck Breaker on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345 kV to GEN-2016-046 (587310) 345 kV Transmission Circuit #1 b.3. UNIT G16-046-GEN2 (587317) 0.7 kV #1 b.4. UNIT G16-046-GEN1 (587313) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT614-SB | Single Phase Fault with Stuck Breaker on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345 kV to GEN-2016-046 (587310) 345 kV Transmission Circuit #1 b.3. UNIT G16-046-GEN2 (587317) 0.7 kV #1 b.4. UNIT G16-046-GEN1 (587313) 0.7 kV #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT62-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to DGRASSE7 (515852) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT62-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to DGRASSE7 (515852) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT64-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GUTHRIE7 (515961) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT64-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GUTHRIE7 (515961) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT65-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT65-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT67-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to G07621119-20 (515599) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT67-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to G07621119-20 (515599) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT68-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to BOBCAT 7 (516106) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT68-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to BOBCAT 7 (516106) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT700-MEM | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT700-MEM | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT701-MEM | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT701-MEM | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to BUCKNER7 (531501) 345 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT702-MEM | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 30 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT702-MEM | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115 kV to NFTDODG3 (539771) 115 kV Transmission Circuit #1 c. Wait 30 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to BVRCNTY7 (515554) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT70-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to BVRCNTY7 (515554) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT704-MEM | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 12 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 | P4 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25W | Transfer | G3_FLT704-MEM | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 12 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345 kV to SETAB 7 (531465) 345 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345 kV to FINNEY 7 (523853) 345 kV Transmission Circuit #1 | P4 | Yes | No | Yes | No | Yes | No | No | GEN-2018-030 and GEN-2008-018 (Buff Dunes) are unstable | Build a second 345 kV line from Holcomb to Finney 345 kV
03 - Central | 25S | Transfer | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT71-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT72-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GEN-2019-012 (763527) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT72-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to GEN-2019-012 (763527) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT73-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) 138 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT73-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) 138 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT74-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) 138 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT74-3PH | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) 138 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT75-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT75-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to THISTLE7 (539801) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT77-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT77-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to WICHITA7 (532796) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT79-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to KINGMAN7 (532783) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. G19-001_GEN (534033) 0.7 kV to Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT79-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to KINGMAN7 (532783) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. G19-001_GEN (534033) 0.7 kV to Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT80-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to GEN-2017-220 (760284) 345 kV Transmission Circuit #1 b.2. UNIT G17-220-GEN1 (760287) 0.6 kV #1 b.3. UNIT G17-221-GEN1 (760307) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT80-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to GEN-2017-220 (760284) 345 kV Transmission Circuit #1 b.2. UNIT G17-220-GEN1 (760287) 0.6 kV #1 b.3. UNIT G17-221-GEN1 (760307) 0.6 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT81-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to GEN-2016-073 (587500) 345 kV Transmission Circuit #1 b.2. UNIT G16-073-GEN1 (587503) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT81-3PH | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345 kV to GEN-2016-073 (587500) 345 kV Transmission Circuit #1 b.2. UNIT G16-073-GEN1 (587503) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT82-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. UNIT G19-001_GEN (534033) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT82-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. UNIT G19-001_GEN (534033) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT83-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to NINN1WF7 (532784) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. UNIT G19-001_GEN (534033) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT83-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to NINN1WF7 (532784) 345 kV Transmission Circuit #1 b.2. UNIT N1 WF 1 (534020) 0.7 kV #1 b.3. UNIT K1 WF 1 (534021) 0.7 kV #1 b.4. UNIT K2 WF 1 (534022) 0.7 kV #1 b.5. UNIT P1 WF 1 (534023) 0.7 kV #1 b.6. UNIT P1 WF 1 (534023) 0.7 kV #2 b.7. UNIT G19-001_GEN (534033) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT84-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to K1 LV 1 (534001) 34.5 kV to K1 WFTX1 (534031) 13.8 kV Three Winding #1 b.2. UNIT K1 WF 1 (534021) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT84-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to K1 LV 1 (534001) 34.5 kV to K1 WFTX1 (534031) 13.8 kV Three Winding #1 b.2. UNIT K1 WF 1 (534021) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT85-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to K2 LV 1 (534002) 34.5 kV to K2 WFTX1 (534032) 13.8 kV Three Winding #1 b.2. UNIT K2 WF 1 (534022) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT85-3PH | 3 Phase fault on KINGMAN7 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345 kV to K2 LV 1 (534002) 34.5 kV to K2 WFTX1 (534032) 13.8 kV Three Winding #1 b.2. UNIT K2 WF 1 (534022) 0.7 kV #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT86-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BUFFALO7 (532782) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT88-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to VIOLA 7 (532798) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT89-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to G14-001-TAP (562476) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT89-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to G14-001-TAP (562476) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT90-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT90-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to BENTON 7 (532791) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT91-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to RENO 7 (532771) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25W | Transfer | G3_FLT91-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to RENO 7 (532771) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2019-018 is unstable. Given the project is connected to 115kV and only 11.97MW, it should be a model parameter problem. Model needs to be validated
03 - Central | 25S | Transfer | G3_FLT92-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to EVANS N4 (533040) 138 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT92-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to EVANS N4 (533040) 138 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT93-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to EVANS N4 (533040) 138 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT93-3PH | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345 kV to EVANS N4 (533040) 138 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT94-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to GEN-2016-046 (587310) 345 kV Transmission Circuit #1 b.2. UNIT G16-046-GEN1 (587313) 0.7 kV #1 b.3. UNIT G16-046-GEN2 (587317) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT94-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to GEN-2016-046 (587310) 345 kV Transmission Circuit #1 b.2. UNIT G16-046-GEN1 (587313) 0.7 kV #1 b.3. UNIT G16-046-GEN2 (587317) 0.7 kV #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT95-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT95-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to CLARKCOUNTY7 (539800) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G3_FLT96-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G3_FLT96-3PH | 3 Phase fault on G16-046-TAP (560080) 345 kV Bus a. Apply fault at the G16-046-TAP (560080) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-046-TAP (560080) 345 kV to IRONWOOD7 (539803) 345 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0001_P4 | a. Apply SLG fault at SW SHV 7 (507760) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from SW SHV 7 (507760) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip SW SHV 7 (507760) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0002_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB #10610Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO NWTXARK7 (508072) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0003_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0004_P4 | a. Apply single-phase fault at WILKES 7 (508841) 345 kV Bus CB #1W10 Stuck b. 1. Run for 5 cycles, Trip branch from WILKES 7 (508841) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WILKES 7 (508841) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0005_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO PIRKEY 7 (508563) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0006_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 1N60 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0007_P4 | a. Apply single-phase fault on ONETA--7 (509807) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from ONETA--7 (509807) 345 kV Bus TO R.S.S.-7 (509782) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip ONETA--7 (509807) 345 kV Bus TO CLARKSV7 (509745) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0008_P4 | a. Apply single-phase fault at R.S.S.-7 (509782) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip R.S.S.-7 (509782) 345 kV Bus TO SAPLPRD7 (509870) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0009_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10280 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0010_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO 7SAREPTA% (337376) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0011_P4 | a. Apply single-phase fault at NEO SPA5 (505486) 161 kV Bus 16119 Stuck b. 1. Run for 5 cycles, Trip branch NEO SPA5 (505486) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 2. Run for 60 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 3. Run for 20 cycles, Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 4. Run for 3 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 5. Run for 37 cycles, Trip branch JOP389 5 (547483) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear Fault and run for 13 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 7. Drop Load 1 TIP292 5 (547472) 161 kV b. 8. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0012_P4 | a. Apply single-phase fault at ASB349 5 (547476) 161 kV Bus CB 16118 Stuck b. 1. Run for 5 cycles, Trip branch CAR395 5 (547485) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO PUR421 5 (547491) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 4. Clear fault and run for 15 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 6. Drop Load 1 Bus CAR395 5 (547485) 161 kV b. 7. Drop Load 1 Bus PUR421 5 (547491) 161 kV b. 8. Disconnect Bus CAR395 5 (547485) 161 kV b. 9. Disconnect Bus PUR421 5 (547491) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0013_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO NEOSHO 5 (532937) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch NEOSHO 5 (532937) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch HOC404 5 (547487) 161 kV Bus TO BAX488 5 (547729) 161 kV Bus CKT 1 b. 4. Clear fault after 86 cycles and Trip BAX488 5 (547729) 161 kV Bus TO HOC404 5 (547487) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0014_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 161120 Stuck b. 1. Run for 5 cycles, Trip branch ORO110 5 (547467) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 2. Run for 12 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 b. 3. Clear fault after 98 cycles and Trip branch STL439 5 (547498) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0015_P4 | a. Apply single-phase fault on TIP292 5 (547472) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch TIP292 5 (547472) 161 kV Bus TO JOP389 5 (547483) 161 kV Bus CKT 1 b. 2. Run for 60 cycles: b. 3. Trip branch TIP292 5 (547472) 161 kV Bus TO NEO SPA5 (505486) 161 kV Bus CKT 1 b. 4. Trip branch NEO SPA5 (505486) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 5. Run for 5 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear fault and run for 15 cycles: b. 7. Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 8. Drop Load 1 Bus TIP292 5 (547472) 161 kV b. 9. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0016_P4 | a. Apply single-phase fault on L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 1. Run for 5 cycles, Trip branch L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 2. Run for 12 cycles, Trip LAR382 5 ( 547479 ) 161 kV Bus TO MON383 5 ( 547480 ) 345 kV Bus CKT 1 b. 3. Clear fault and run for 95 cycles: b. 4. Trip branch MON383 5 ( 547480 ) 161 kV Bus TO LAR382 5 ( 547479 ) 345 kV Bus CKT 1 b. 5. Drop GENERATOR 1 BUS 547651 b. 6. Drop LOAD S1 BUS 547651 b. 7. Disconnect BUS 547651 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0018_P4 | a. Apply single-phase fault on LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 1. Run for 15 cycles, Trip branch LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 2. Clear fault after 15 cycles and Trip LEBROCK7 ( 508572 ) 161 kV Bus TO TENRUSK7 ( 508585 ) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0019_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Disconnect BUS 532791 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0020_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0021_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0022_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 13 cycles, Disconnect BUS 532831 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0023_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0024_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0025_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles: d. 2. Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 d. 3. Disconnect BUS 532962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0026_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543641 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0027_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543643 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0028_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0029_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0030_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0031_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542956 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0032_P4 | a. Apply single-phase fault on PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0033_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 3. Trip branch SWISVAL7 (532774) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0034_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 3. Trip branch STILWEL7 (542968) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0035_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Disconnect BUS 532831 c. Reclose the fault d. 1. Clear fault after 13 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0036_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69 kV Bus to TONECESTR2 (512756) 69 kV Bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69 kV Bus to ARKLIN2 (512728) 69 kV Bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69 kV Bus to SSNEWN2 (512747) 69 kV Bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69 kV Bus to SSNORT2 (512746) 69 kV Bus CKT 1 b. 5. Trip branch from SSNORT2 (512746) 69 kV Bus to SSLINC2 (512745) 69 kV Bus CKT 1 b. 6. Drop Load 1 at SSNORT2 (512746) 69 kV Bus b. 7. Drop Load 1 at SSLINC2 (512745) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0037_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT2-1 (506920) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0038_P1 | 3 phase fault on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD2 (505494) 69 kV Bus to 2ELWOOD (300669) 69 kV Bus CKT 1 b. 2. Trip branch from 2ELWOOD (300669) 69 kV Bus to 2ASHGRV (300657) 69 kV Bus CKT 1 b. 3. Drop Load 1 at 2ELWOOD (300669) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0039_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 5 (549956) 161 kV Bus to NICHOLS 2 (549925) 69 kV Bus to NICHOL XF1 1 (549940) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0040_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 5 (549956) 161 kV Bus to WEST BELT 5 (549957) 161 kV Bus CKT 1 b. 2. Trip branch from WEST BELT 5 (549957) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 b. 3. Drop Load W at WEST BELT 5 (549957) 161 kV Bus b. 4. Drop Load E at WEST BELT 5 (549957) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0041_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 1 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0042_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 2 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0043_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to GOLDEN 2 (549911) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0044_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to DAYTON 2 (549913) 69 kV Bus CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV Bus to FORT 2 (549914) 69 kV Bus CKT 1 b. 3. Trip branch from FORT 2 (549914) 69 kV Bus to SUNSET 2 (549907) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DAYTON 2 (549913) 69 kV Bus b. 5. Drop Load N at FORT 2 (549914) 69 kV Bus b. 6. Drop Load S at FORT 2 (549914) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0045_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to LAUREL 2 (549924) 69 kV Bus CKT 1 b. 2. Trip branch from LAUREL 2 (549924) 69 kV Bus to NICHOLS 2 (549925) 69 kV Bus CKT 1 b. 3. Drop Load N at LAUREL 2 (549924) 69 kV Bus b. 4. Drop Load S at LAUREL 2 (549924) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0046_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to COX 2 (549910) 69 kV Bus CKT 1 b. 2. Trip branch from COX 2 (549910) 69 kV Bus to PLAINVIEW 2 (549905) 69 kV Bus CKT 1 b. 3. Trip branch from PLAINVIEW 2 (549905) 69 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus CKT 1 b. 4. Drop Load N at COX 2 (549910) 69 kV Bus b. 5. Drop Load S at COX 2 (549910) 69 kV Bus b. 6. Drop Load E at PLAINVIEW 2 (549905) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0047_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to NIC170 2 (547542) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0048_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0049_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to FRISCO 2 (549926) 69 kV Bus CKT 1 b. 2. Trip branch from FRISCO 2 (549926) 69 kV Bus to N HWY13 2 (549927) 69 kV Bus CKT 1 b. 3. Trip branch from N HWY13 2 (549927) 69 kV Bus to NORTON 2 (549928) 69 kV Bus CKT 1 b. 4. Drop Load N at FRISCO 2 (549926) 69 kV Bus b. 5. Drop Load S at FRISCO 2 (549926) 69 kV Bus b. 6. Drop Load E at N HWY13 2 (549927) 69 kV Bus b. 7. Drop Load W at N HWY13 2 (549927) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0050_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to SED 80 2 (547529) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0051_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to NIX114 2 (547535) 69 kV Bus CKT 1 b. 2. Trip branch from NIX114 2 (547535) 69 kV Bus to BHJ415 2 (547604) 69 kV Bus CKT 1 b. 3. Drop Load 1 at NIX114 2 (547535) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0052_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to REP345 2 (547576) 69 kV Bus CKT 1 b. 2. Trip branch from REP345 2 (547576) 69 kV Bus to REP451 2 (547443) 69 kV Bus CKT 1 b. 3. Trip branch from REP451 2 (547443) 69 kV Bus to REP359 2 (547580) 69 kV Bus CKT 1 b. 4. Trip branch from REP359 2 (547580) 69 kV Bus to BIL221 2 (547546) 69 kV Bus CKT 1 b. 5. Drop Load 1 at REP345 2 (547576) 69 kV Bus b. 6. Drop Load 1 at REP451 2 (547443) 69 kV Bus b. 7. Drop Load 1 at REP359 2 (547580) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0053_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to SILSPWW5 (512642) 161 kV Bus CKT 1 b. 2. Trip branch from SILSPWW5 (512642) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 b. 3. Drop Load 1 at SILSPWW5 (512642) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0054_P1 | 3 phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161 kV Bus to WEDINGTON (506992) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0055_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to WEDINGTON5 (504275) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0056_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to FARMNGTN 5 (504020) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0058_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 7HUBEN (300042) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25S | Transfer | Group4_Fault_0059_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to GENTRY 5 (504201) 161 kV Bus CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV Bus to BEN279_5 (506960) 161 kV Bus CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV Bus to GREENHOUSE 5 (506990) 161 kV Bus CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 5. Drop Load A1 at GENTRY 5 (504201) 161 kV Bus b. 6. Drop Load 1 at BEN279_5 (506960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0061_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 5MORGANXF2 (301622) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25S | Transfer | Group4_Fault_0062_P1 | 3 phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGANXF2 (301622) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0063_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0064_P1 | 3 phase fault on EROGERS5 (506931) 161 kV Bus a. Apply Fault at the EROGERS5 (506931) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EROGERS5 (506931) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0065_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYESS1-1 (506914) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0066_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES2-1 (506915) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0067_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES3-1 (506916) 13.2 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0068_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to CARLEYRD 5 (504274) 161 kV Bus CKT 1 b. 2. Trip branch from CARLEYRD 5 (504274) 161 kV Bus to VANASCH5 (506939) 161 kV Bus CKT 1 b. 3. Trip branch from VANASCH5 (506939) 161 kV Bus to GREGGST5 (506983) 161 kV Bus CKT 1 b. 4. Trip branch from GREGGST5 (506983) 161 kV Bus to FAYETVL5 (506933) 161 kV Bus CKT 1 b. 5. Trip branch from FAYETVL5 (506933) 161 kV Bus to SFAYTVL5 (506947) 161 kV Bus CKT 1 b. 6. Drop Load A1 at CARLEYRD 5 (504274) 161 kV Bus b. 7. Drop Load 1 at VANASCH5 (506939) 161 kV Bus b. 8. Drop Load 1 at GREGGST5 (506983) 161 kV Bus b. 9. Drop Load 1 at FAYETVL5 (506933) 161 kV Bus b. 10. Drop Shunt 1 at VANASCH5 (506939) 161 kV Bus1 b. 11. Drop Shunt 1 at FAYETVL5 (506933) 161 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0069_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to SOSPRDL5 (506949) 161 kV Bus CKT 1 b. 2. Trip branch from SOSPRDL5 (506949) 161 kV Bus to OSBURN (506985) 161 kV Bus CKT 1 b. 3. Trip branch from OSBURN (506985) 161 kV Bus to EFAYETVL 5 (504015) 161 kV Bus CKT 1 b. 4. Drop Load 1 at SOSPRDL5 (506949) 161 kV Bus b. 5. Drop Load 1 at OSBURN (506985) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0070_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to DEC392 5 (547484) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0071_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to GROVE 5 (510411) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0072_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to NEO184 5 (547471) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0073_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NOL435 5 (547496) 161 kV Bus to NOL435 2 (547610) 69 kV Bus to NOL435 1 (547720) 12.5 kV Bus CKT 1 b. 2. Drop Shunt 1 at NOL435 1 (547720) 12.5 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0074_P1 | 3 phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply Fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161 kV Bus to 5CHOTEAU2 (301348) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0075_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR1 (512814) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0076_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR2 (512815) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0077_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLARMR 5 (512651) 161 kV Bus to 5KETONVL (300997) 161 kV Bus CKT 1 b. 2. Trip branch from 5KETONVL (300997) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5KETONVL (300997) 161 kV Bus b. 4. Drop Load 1 at 5KETONVL (300997) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0078_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR 5 (512700) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0079_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WAGNOR 5 (512700) 161 kV Bus to WAGNOR 2 (512697) 69 kV Bus to WAGNOR1 (512818) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0080_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to STOCKTN5 (505498) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0081_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to TONTITN5 (506957) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0082_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to DAD368 5 (547478) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0083_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to 2MORGAN (300782) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0084_P1 | 3 phase fault on SSSWTP2 (512737) 69 kV Bus a. Apply Fault at the SSSWTP2 (512737) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SSMOSS2 (512744) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0085_P1 | 3 phase fault on 5CHOTEAU2 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 (301348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU2 (301348) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0086_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 b. 2. Drop Load 1 at DRYGULCH5 (512629) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0087_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0088_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to 412SUB 5 (512637) 161 kV Bus CKT 1 b. 2. Trip branch from 412SUB 5 (512637) 161 kV Bus to KANSATP5 (512714) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 412SUB 5 (512637) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0089_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK1 5 (512770) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0090_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK4 5 (512771) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0091_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0092_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAMSP 5 (504202) 161 kV Bus CKT 1 b. 2. Trip branch from SILOAMSP 5 (504202) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 b. 3. Drop Load A1 at SILOAMSP 5 (504202) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0093_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0094_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER1 1 (512833) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0095_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER2 1 (512834) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0096_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161 kV Bus to 5ELMCRK (300993) 161 kV Bus CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5ELMCRK (300993) 161 kV Bus b. 4. Drop Load 2 at 5ELMCRK (300993) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0097_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIXA 5 (505496) 161 kV Bus to TABLE R5 (505472) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0098_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X2 1 (505499) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0099_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X1 1 (505497) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0100_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to CARTHAG5 (505488) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0101_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to MON383 5 (547480) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0102_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MILL 5 (549962) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0103_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0104_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MENTOR 5 (549963) 161 kV Bus CKT 1 b. 2. Trip branch from MENTOR 5 (549963) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 b. 3. Drop Load S at MENTOR 5 (549963) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0105_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to 5LOGAN (301161) 161 kV Bus CKT 1 b. 2. Trip branch from 5LOGAN (301161) 161 kV Bus to 5MANSFDMN (300095) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5LOGAN (301161) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0106_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus to JRPS XF2 1 (549945) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0107_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JAMES RIVER2 (549904) 69 kV Bus to JRPS XF1 1 (549944) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0108_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF1 1 (549936) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0109_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF2 1 (549938) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0110_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to MC CARTNEY 5 (549968) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0111_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to NORTON 5 (549967) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0112_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to KANSAS 5 (512716) 161 kV Bus CKT 1 b. 2. Trip three winding transformer from KANSAS 5 (512716) 161 kV Bus to KANSAS 2 (512715) 69 kV Bus to KANSAS1 (512736) 13.8 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0113_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2KANSASTP (301637) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0114_P1 | 3 phase fault on SHIPERD5 (506980) 161 kV Bus a. Apply Fault at the SHIPERD5 (506980) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHIPERD5 (506980) 161 kV Bus to CENTRTN5 (506952) 161 kV Bus CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 3. Drop Load 1 at CENTRTN5 (506952) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0115_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2WATTS (300987) 69 kV Bus CKT 1 b. 2. Trip branch from 2WATTS (300987) 69 kV Bus to 2WESTVIL (300988) 69 kV Bus CKT 1 b. 3. Trip branch from 2WESTVIL (300988) 69 kV Bus to 2BALDOR (300980) 69 kV Bus CKT 1 b. 4. Trip branch from 2BALDOR (300980) 69 kV Bus to STLWLGR2 (512721) 69 kV Bus CKT 1 b. 5. Drop Load 1 at 2WATTS (300987) 69 kV Bus b. 6. Drop Load 1 at 2WESTVIL (300988) 69 kV Bus b. 7. Drop Load 2 at 2WESTVIL (300988) 69 kV Bus b. 8. Drop Load 1 at 2BALDOR (300980) 69 kV Bus b. 9. Drop Shunt 1 at 2WESTVIL (300988) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0116_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2KANSASKM (301638) 69 kV Bus CKT 1 b. 2. Drop Load 2 at 2KANSASKM (301638) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0117_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2COLCOTP (301458) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0118_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0119_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY1 1 (512849) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0120_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE5 (512751) 161 kV Bus to TONNEC2 (512753) 69 kV Bus to TONNEC1 (512754) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0121_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY2 1 (512850) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0122_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA1 (512821) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRDA1 (512821) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0123_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA2 1 (512826) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRDA2 1 (512826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0124_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0125_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to GREC TAP5 (512865) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0126_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF1 1 (549988) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0127_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF2 1 (549989) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0128_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 7 (549984) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0129_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 5 (506948) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0130_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILOAM 5 (506948) 161 kV Bus to SILOAM 2 (506973) 69 kV Bus to SILOAM-1 (506917) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0131_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0132_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONTITN7 (506959) 345 kV Bus to TONTITN5 (506957) 161 kV Bus to TONTITN1 (506958) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0133_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0134_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEC392 5 (547484) 161 kV Bus to DEC392 2 (547594) 69 kV Bus to DEC392 1 (547714) 12.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0135_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 5 (547484) 161 kV Bus to NOL435 5 (547496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0136_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWES2 (512730) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0137_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWTP2 (512737) 69 kV Bus CKT 1 b. 2. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0138_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0139_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0140_P1 | 3 phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC TAP5 (512865) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0141_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE7 (512750) 345 kV Bus to TONECE5 (512751) 161 kV Bus to TONECE1 (512752) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0142_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0143_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to CLARMR 5 (512651) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0144_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WAGNOR 5 (512700) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0145_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WMAIN ST5 (512742) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0146_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 5 (512656) 161 kV Bus to GRDA1 2 (512727) 69 kV Bus to GRDA1 1 (512816) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0147_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0148_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to SPRGFLD5 (505492) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0149_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JTEC 5 (549954) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0150_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JUNCTION 5 (549955) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0151_P1 | 3 phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply Fault at the SILOAM 2 (506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 2 (506973) 69 kV Bus to LINCOLN2 (506972) 69 kV Bus CKT 1 b. 2. Trip branch from LINCOLN2 (506972) 69 kV Bus to PRGROVE2 (506941) 69 kV Bus CKT 1 b. 3. Trip branch from PRGROVE2 (506941) 69 kV Bus to GREENLD2 (506936) 69 kV Bus CKT 1 b. 4. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 b. 5. Drop Load A1 at LINCOLN2 (506972) 69 kV Bus b. 6. Drop Load 1 at PRGROVE2 (506941) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0152_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to GRDA1 7 (512650) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0153_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to ELMSPRGS 5 (504010) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0154_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to BRUSHCRK_5 (506991) 161 kV Bus CKT 1 b. 2. Trip branch from BRUSHCRK_5 (506991) 161 kV Bus to LOWELL 5 (506938) 161 kV Bus CKT 1 b. 3. Trip branch from LOWELL 5 (506938) 161 kV Bus to ROGERS 5 (506942) 161 kV Bus CKT 1 b. 4. Trip branch from ROGERS 5 (506942) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 5. Drop Load 1 at BRUSHCRK_5 (506991) 161 kV Bus b. 6. Drop Load 1 at LOWELL 5 (506938) 161 kV Bus b. 7. Drop Load 1 at ROGERS 5 (506942) 161 kV Bus b. 8. Drop Shunt 1 at ROGERS 5 (506942) 161 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0155_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELMSPRGS 5 (504010) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0156_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_1 2 (504011) 69 kV Bus to ELMSP_T1 1 (504012) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ELMSPG_1 2 (504011) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0157_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_2 2 (504013) 69 kV Bus to ELMSP_T2 1 (504014) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0158_P1 | 3 phase fault on TONTITN7 (506959) 345 kV Bus a. Apply Fault at the TONTITN7 (506959) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN7 (506959) 345 kV Bus to CHAMSPR7 (506945) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0159_P1 | 3 phase fault on DEC392 2 (547594) 69 kV Bus a. Apply Fault at the DEC392 2 (547594) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 2 (547594) 69 kV Bus to DEC467 2 (547569) 69 kV Bus CKT 1 b. 2. Trip branch from DEC467 2 (547569) 69 kV Bus to GRA700 2 (547617) 69 kV Bus CKT 1 b. 3. Trip branch from GRA700 2 (547617) 69 kV Bus to NOL435 2 (547610) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DEC467 2 (547569) 69 kV Bus b. 5. Drop Load 1 at GRA700 2 (547617) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0160_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_1 2 (504006) 69 kV Bus to ECENT_T1 1 (504007) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ECENT_1 2 (504006) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0161_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_2 2 (504008) 69 kV Bus to ECENT_T2 1 (504009) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0162_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR2-1 (506924) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0163_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to FLINTCR7 (506935) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0164_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR1-1 (506923) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0165_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV Bus to BENT_SL5 (506963) 161 kV Bus CKT 1 b. 2. Trip branch from BENT_SL5 (506963) 161 kV Bus to BENTVJ_5 (506962) 161 kV Bus CKT 1 b. 3. Trip branch from BENTVJ_5 (506962) 161 kV Bus to BENT ML5 (506955) 161 kV Bus CKT 1 b. 4. Trip branch from BENT ML5 (506955) 161 kV Bus to WROGERS 5 (504200) 161 kV Bus CKT 1 b. 5. Trip branch from WROGERS 5 (504200) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 6. Drop Load 1 at BENT_SL5 (506963) 161 kV Bus b. 7. Drop Load 1 at BENTVJ_5 (506962) 161 kV Bus b. 8. Drop Load 1 at BENT ML5 (506955) 161 kV Bus b. 9. Drop Load A1 at WROGERS 5 (504200) 161 kV Bus b. 10. Drop Load A2 at WROGERS 5 (504200) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0166_P1 | 3 phase fault on ECNTRTN2 (506928) 69 kV Bus a. Apply Fault at the ECNTRTN2 (506928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN2 (506928) 69 kV Bus to BENTNVL2 (506965) 69 kV Bus CKT 1 b. 2. Trip branch from BENTNVL2 (506965) 69 kV Bus to DIXLAND2 (506925) 69 kV Bus CKT 1 b. 3. Trip branch from DIXLAND2 (506925) 69 kV Bus to NROGERS2 (506940) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BENTNVL2 (506965) 69 kV Bus b. 5. Drop Load 1 at DIXLAND2 (506925) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0167_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV1 5 (513593) 161 kV Bus to IGLOTER1 1 (513592) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0168_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV2 5 (513595) 161 kV Bus to IGLOTER2 1 (513594) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0169_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0170_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0171_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0172_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0173_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to BROOKLINE 7 (549984) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0174_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0175_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0176_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to LOCSTGVKM 5 (513050) 161 kV Bus CKT 1 b. 2. Trip branch from LOCSTGVKM 5 (513050) 161 kV Bus to 5CDRCRST (301344) 161 kV Bus CKT 1 b. 3. Drop Load 1 at LOCSTGVKM 5 (513050) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0177_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER1 1 (512836) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0178_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER2 1 (512837) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0179_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0180_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to GERALDGAY5 (512760) 161 kV Bus CKT 1 b. 2. Trip branch from GERALDGAY5 (512760) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 b. 3. Drop Load 1 at GERALDGAY5 (512760) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0181_P1 | 3 phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply Fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WMAIN ST5 (512742) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0182_P1 | 3 phase fault on GRDA1 2 (512727) 69 kV Bus a. Apply Fault at the GRDA1 2 (512727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 2 (512727) 69 kV Bus to MAIDTP2 (512625) 69 kV Bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0183_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to NIXA 5 (505496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0184_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to SHIPERD7 (506979) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0185_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0186_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to CLAY 5 (549970) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0187_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to 5NIXA-1 (300678) 161 kV Bus CKT 1 b. 2. Trip branch from 5NIXA-1 (300678) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5NIXA-1 (300678) 161 kV Bus b. 4. Drop Load 2 at 5NIXA-1 (300678) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0188_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X1 1 (505491) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0189_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X2 1 (505493) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0190_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X3 1 (505495) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0191_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to LAR382 5 (547479) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0192_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0193_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to 5BTLFD (300348) 161 kV Bus CKT 1 b. 2. Trip branch from 5BTLFD (300348) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5BTLFD (300348) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0194_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to SW DISP PLT5 (549960) 161 kV Bus CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 b. 3. Drop Load W at SW DISP PLT5 (549960) 161 kV Bus b. 4. Drop Load E at SW DISP PLT5 (549960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0195_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT1-1 (506921) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0196_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to NICHOLS 5 (549956) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0197_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to PIC WEST 5 (549971) 161 kV Bus CKT 1 b. 2. Trip branch from PIC WEST 5 (549971) 161 kV Bus to SUMMIT 5 (549966) 161 kV Bus CKT 1 b. 3. Drop Load S at PIC WEST 5 (549971) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0198_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAMSPR7 (506945) 345 kV Bus to CHAMSPR5 (506944) 161 kV Bus to CHAMSPR1 (506919) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0199_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0200_P1 | 3 phase fault on IGLOOV1 5 (513593) 161 kV Bus a. Apply Fault at the IGLOOV1 5 (513593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV1 5 (513593) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0201_P1 | 3 phase fault on IGLOOV2 5 (513595) 161 kV Bus a. Apply Fault at the IGLOOV2 5 (513595) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV2 5 (513595) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0202_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to REDDEN 2 (512698) 69 kV Bus CKT 1 b. 2. Trip branch from REDDEN 2 (512698) 69 kV Bus to CASTING TAP2 (512685) 69 kV Bus CKT 1 b. 3. Trip branch from CASTING TAP2 (512685) 69 kV Bus to AMERCAST N2 (512683) 69 kV Bus CKT 1 b. 4. Drop Load 1 at REDDEN 2 (512698) 69 kV Bus b. 5. Drop Load 1 at AMERCAST N2 (512683) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0203_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to AMERCAST S2 (512681) 69 kV Bus CKT 1 b. 2. Trip branch from AMERCAST S2 (512681) 69 kV Bus to CPPTAP 2 (512661) 69 kV Bus CKT 1 b. 3. Trip branch from CPPTAP 2 (512661) 69 kV Bus to PRYORCHEM2 (512699) 69 kV Bus CKT 1 b. 4. Trip branch from PRYORCHEM2 (512699) 69 kV Bus to AIRPROD2 (512687) 69 kV Bus CKT 1 b. 5. Trip branch from AIRPROD2 (512687) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 b. 6. Drop Load 1 at AMERCAST S2 (512681) 69 kV Bus b. 7. Drop Load 1 at PRYORCHEM2 (512699) 69 kV Bus b. 8. Drop Load 1 at AIRPROD2 (512687) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0204_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD5 (549959) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0205_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BATTLEFIELD5 (549959) 161 kV Bus to BATTLEFIELD2 (549979) 69 kV Bus to BATLEFLDXF11 (549980) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0206_P4 | a. Apply single phase fault at FLINTCR7 (506935) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR7 (506935) 345 kV to TONECE7 (512750) 345 kV CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345 kV to SHIPERD7 (506979) 345 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from SHIPERD5 (506980) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 5. Trip branch from CENTRTN5 (506952) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 6. Drop Load 1 CENTRTN5 (506952) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0207_P4 | a. Apply single phase fault at SILMCTY5 (512643) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SILMCTY5 (512643) 161 kV to SILOAM 5 (506948) 161 kV CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161 kV to SILSPWW5 (512642) 161 kV CKT 1 b. 3. Trip branch from SILSPWW5 (512642) 161 kV to KANSATP5 (512714) 161 kV CKT 1 b. 4. Drop Load 1 SILSPWW5 (512642) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0208_P4 | a. Apply single phase fault at FLINTCR5 (506934) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR5 (506934) 161 kV to GENTRY 5 (504201) 161 kV CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV to BEN279_5 (506960) 161 kV CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV to GREENHOUSE 5 (506990) 161 kV CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 5. Trip branch from FLINTCR5 (506934) 161 kV to TONTITN5 (506957) 161 kV CKT 1 b. 6. Drop Load A1 GENTRY 5 (504201) 161 kV b. 7. Drop Load 1 BEN279_5 (506960) 161 kV b. 8. Drop Load 1 GREENHOUSE 5 (506990) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0210_P4 | a. Apply single phase fault at BROOKLINE 5 (549969) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV CKT 1 b. 2. Trip branch from BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0211_P4 | a. Apply single phase fault at TAHLQH 5 (512655) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TAHLQH 5 (512655) 161 kV to 5CDRCRST (301344) 161 kV CKT 1 b. 2. Trip branch from TAHLQH 5 (512655) 161 kV to 7CLANS 5 (515956) 161 kV CKT 1 b. 3. Trip branch from 7CLANS 5 (515956) 161 kV to KETOWAH5 (516027) 161 kV CKT 1 b. 4. Trip branch from KETOWAH5 (516027) 161 kV to MUSKOGE5 (515222) 161 kV CKT 1 b. 5. Drop Load 1 SILSPWW5 (512642) 161 kV b. 6. Drop Load 1 7CLANS 5 (515956) 161 kV b. 7. Drop Load 1 KETOWAH5 (516027) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0212_P4 | a. Apply single phase fault at CHAMSPR5 (506944) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CHAMSPR5 (506944) 161 kV to CHAMSPR7 (506945) kV to CHAMSPR1 (506919) 13.8 kV CKT1 b. 2. Trip branch from CHAMSPR5 (506944) 161 kV to TONTITN5 (506957) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0213_P4 | a. Apply single phase fault at ECNTRTN5 (506929) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV to SHIPERD5 (506980) 161 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from ECNTRTN5 (506929) 161 kV to BENT_SL5 (506963) 161 kV CKT 1 b. 5. Trip branch from BENT_SL5 (506963) 161 kV to BENTVJ_5 (506962) 161 kV CKT 1 b. 6. Trip branch from BENTVJ_5 (506962) 161 kV to BENT ML5 (506955) 161 kV CKT 1 b. 7. Trip branch from BENT ML5 (506955) 161 kV to WROGERS 5 (504200) 161 kV CKT 1 b. 8. Trip branch from WROGERS 5 (504200) 161 kV to EROGERS5 (506931) 161 kV CKT 1 b. 9. Drop Load 1 CENTRTN5 (506952) 161 kV b. 10. Drop Load 1 BENT_SL5 (506963) 161 kV b. 11. Drop Load 1 BENTVJ_5 (506962) 161 kV b. 12. Drop Load 1 BENT ML5 (506955) 161 kV b. 13. Drop Load A1 WROGERS 5 (504200) 161 kV b. 14. Drop Load A2 WROGERS 5 (504200) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0214_P4 | a. Apply single phase fault at STLWLGR2 (512721) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from STLWLGR2 (512721) 69 kV to STIWEL5 (512704) kV to STLWELL1 (512819) 13.8 kV CKT1 b. 2. Trip branch from STIWEL5 (512704) 161 kV to BRIGSKM 5 (513044) 161 kV CKT 1 b. 3. Trip branch from STLWLGR2 (512721) 69 kV to STILWELLCTY2 (512701) 69 kV CKT 1 b. 4. Drop Load 1 STILWELLCTY2 (512701) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0215_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to SOONER 7 (514803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0216_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MILLERT4 (514704) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0217_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to LBRTYLK4 (515373) 138 kV Bus CKT 1 b. 2. Trip branch from LBRTYLK4 (515373) 138 kV Bus to WATRLOO4 (514831) 138 kV Bus CKT 1 b. 3. Trip branch from WATRLOO4 (514831) 138 kV Bus to WHITESB4 (515467) 138 kV Bus CKT 1 b. 4. Trip branch from WHITESB4 (515467) 138 kV Bus to MITCHSB4 (515466) 138 kV Bus CKT 1 b. 5. Trip branch from MITCHSB4 (515466) 138 kV Bus to KETCHTP4 (514828) 138 kV Bus CKT 1 b. 6. Drop Load 1 at LBRTYLK4 (515373) 138 kV Bus b. 7. Drop Load 1 at WATRLOO4 (514831) 138 kV Bus b. 8. Drop Load 1 at WHITESB4 (515467) 138 kV Bus b. 9. Drop Load 1 at MITCHSB4 (515466) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0218_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to NORTWST4 (514879) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0219_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to KETCH 4 (514834) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0220_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0221_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to FAIRFLD4 (515468) 138 kV Bus CKT 1 b. 2. Trip branch from FAIRFLD4 (515468) 138 kV Bus to CHISHOM4 (515374) 138 kV Bus CKT 1 b. 3. Trip branch from CHISHOM4 (515374) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FAIRFLD4 (515468) 138 kV Bus b. 5. Drop Load 1 at CHISHOM4 (515374) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0222_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to PERRY 4 (514707) 138 kV Bus CKT 1 b. 2. Trip branch from PERRY 4 (514707) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0223_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to SNRPMPT4 (514798) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0224_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MORISNT4 (515447) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0225_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345 kV Bus to SAPLPRD7 (509870) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0226_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV Bus to WEKIWA-4 (509757) 138 kV Bus to WEKIW1-1 (509879) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0227_P1 | 3 phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PINTAIL7 (516010) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0228_P1 | 3 phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply Fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-119-TAP (587804) 345 kV Bus to SPRNGCK7 (514881) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0229_P1 | 3 phase fault on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345 kV Bus to ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0230_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to OPENSKY7 (515621) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0231_P1 | 3 phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEVLND7 (512694) 345 kV Bus to CLEVLND 4 (512729) 138 kV Bus to CLEVLND1 (512817) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0232_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to DMNCRKT4 (515412) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0233_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to OTOETAP4 (515978) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0234_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to OSAGE 4 (514743) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0235_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to SNRPMP 4 (514799) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SNRPMP 4 (514799) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0236_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to STILWTR4 (515011) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0237_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to MORRISN4 (515006) 138 kV Bus CKT 1 b. 2. Trip branch from MORRISN4 (515006) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0238_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SHEFFD-4 (509812) 138 kV Bus CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV Bus to S.S.---4 (509815) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHEFFD-4 (509812) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0239_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to WED-TAP4 (509823) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0240_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to P&P WTP4 (509851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0241_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0242_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SILVCTYGR4 (512726) 138 kV Bus CKT 1 b. 2. Trip branch from SILVCTYGR4 (512726) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0243_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to KEYSTON4 (505610) 138 kV Bus CKT 1 b. 2. Trip branch from KEYSTON4 (505610) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0244_P1 | 3 phase fault on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND 4 (512729) 138 kV Bus to 4CLEVLND (300138) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0245_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to PAWNSW4 (512749) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0246_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0247_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4JAVINE (300996) 138 kV Bus CKT 1 b. 2. Trip branch from 4JAVINE (300996) 138 kV Bus to 4SFORKKTP (301339) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0248_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0249_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0250_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD7 (509870) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0251_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SAPLPRD7 (509870) 345 kV Bus to SAPLPRD4 (509871) 138 kV Bus to SAPLPRD1 (509872) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0252_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G15-066T (560056) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0254_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to HUNTERS7 (515476) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0255_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0256_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV Bus to WOODRNG4 (514714) 138 kV Bus to WOODRNG1 (515770) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0257_P1 | 3 phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPRNGCK7 (514881) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0258_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0259_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0260_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0261_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH1 1 (532826) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH1 1 (532826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0262_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH5 1 (532827) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH5 1 (532827) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0263_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to PINTAIL7 (516010) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0264_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH3 1 (532831) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH3 1 (532831) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0265_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0266_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to DMANCRK4 (515400) 138 kV Bus CKT 1 b. 2. Drop Load 1 at DMANCRK4 (515400) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0267_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to 4REDRCK (301011) 138 kV Bus CKT 1 b. 2. Drop Load 1 at 4REDRCK (301011) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0268_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to OTOE 4 (514737) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OTOE 4 (514737) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0269_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COWCRK 4 (514706) 138 kV Bus to WRVALLY4 (514713) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0270_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COWCRK 4 (514706) 138 kV Bus to COWCRK 2 (514705) 69 kV Bus to COWCRK 1 (515717) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0271_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0272_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WEBBTAP4 (510376) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0273_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to MARLNDT4 (514770) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0274_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G16-119-TAP (587804) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0275_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 31 (515744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0276_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 41 (515745) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0277_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to STDBEAR4 (514758) 138 kV Bus CKT 1 b. 2. Trip branch from STDBEAR4 (514758) 138 kV Bus to CONORTH4 (514753) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0278_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to SPGVLLY4 (515574) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0279_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to MCELROY4 (515009) 138 kV Bus CKT 1 b. 2. Trip branch from MCELROY4 (515009) 138 kV Bus to UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 3. Trip branch from UNVRSTY4 (515181) 138 kV Bus to KINZE 4 (515008) 138 kV Bus CKT 1 b. 4. Drop Load 1 at MCELROY4 (515009) 138 kV Bus b. 5. Drop Load 1 at UNVRSTY4 (515181) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0280_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to PP----W4 (509805) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0281_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0282_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0283_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4BRISTOW (300137) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0284_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0285_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SOONER 7 (514803) 345 kV Bus to SOONER 4 (514802) 138 kV Bus to SOONER 1 (515760) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0286_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0287_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0288_P1 | 3 phase fault on 2CLEVLND (300927) 69 kV Bus a. Apply Fault at the 2CLEVLND (300927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CLEVLND (300927) 69 kV Bus to OSAGEK2 (512876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0289_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to 4FAIRFAX (300139) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0290_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to GLENCOKM 4 (513095) 138 kV Bus CKT 1 b. 2. Trip branch from GLENCOKM 4 (513095) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLENCOKM 4 (513095) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0291_P1 | 3 phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply Fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0292_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0293_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0294_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to OAKSWTP4 (509848) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0295_P1 | 3 phase fault on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345 kV Bus to G15-052T (560053) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0296_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to 72ELWOD4 (509888) 138 kV Bus CKT 1 b. 2. Trip branch from 72ELWOD4 (509888) 138 kV Bus to T.P.S.-4 (509788) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 72ELWOD4 (509888) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0297_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to JENKS--4 (509759) 138 kV Bus CKT 1 b. 2. Trip branch from JENKS--4 (509759) 138 kV Bus to 116JENK4 (509753) 138 kV Bus CKT 1 b. 3. Trip branch from 116JENK4 (509753) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 b. 4. Drop Load 1 at JENKS--4 (509759) 138 kV Bus b. 5. Drop Load 1 at 116JENK4 (509753) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0298_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to OTTER 4 (514708) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0299_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to FRMNTAP4 (514709) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0300_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to WAUKOTP4 (514711) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0301_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to MARSHL 4 (514733) 138 kV Bus CKT 1 b. 2. Trip branch from MARSHL 4 (514733) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 3. Trip branch from MARSHL 4 (514733) 138 kV Bus to MARSHAL4 (521006) 138 kV Bus CKT Z1 b. 4. Drop Load 1 at MARSHAL4 (521006) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0302_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0303_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0304_P1 | 3 phase fault on G15-066T (560056) 345 kV Bus a. Apply Fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0305_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to KINZEGR4 (512710) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0306_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to FITZGRD4 (514830) 138 kV Bus CKT 1 b. 2. Trip branch from FITZGRD4 (514830) 138 kV Bus to PINE ST4 (514829) 138 kV Bus CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FITZGRD4 (514830) 138 kV Bus b. 5. Drop Load 1 at PINE ST4 (514829) 138 kV Bus b. 6. Drop Load 2 at PINE ST4 (514829) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0307_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to NORTHTP4 (512731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0308_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to 19TH ST4 (512712) 138 kV Bus CKT 1 b. 2. Trip branch from 19TH ST4 (512712) 138 kV Bus to 4RAMSEY (300844) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 19TH ST4 (512712) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0309_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to KINZEGR2 (512713) 69 kV Bus CKT 1 b. 2. Trip branch from KINZEGR2 (512713) 69 kV Bus to ADMIRAL2 (512660) 69 kV Bus CKT 1 b. 3. Drop Shunt 1 at KINZEGR2 (512713) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0310_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to ARCADIA4 (514907) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0311_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to CRESENT4 (515377) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0312_P4 | a. Apply single phase fault at SOONER 4 (514802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SOONER 4 (514802) 138 kV to MORISNT4 (515447) 138 kV CKT 1 b. 2. Trip branch from SOONER 4 (514802) 138 kV to SNRPMPT4 (514798) 138 kV CKT 1 b. 3. Trip branch from SNRPMPT4 (514798) 138 kV to SNRPMP 4 (514799) 138 kV CKT 1 b. 4. Drop Load 1 SNRPMP 4 (514799) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0313_P4 | a. Apply single phase fault at T.NO.--4 (509817) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from T.NO.--4 (509817) 138 kV to T.NO.2-4 (509895) 138 kV CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138 kV to CDC-WT 4 (509842) 138 kV CKT 1 b. 3. Trip branch from CDC-WT 4 (509842) 138 kV to A.A.---4 (509784) 138 kV CKT 1 b. 4. Trip branch from CDC-WT 4 (509842) 138 kV to WHIRLPO4 (509840) 138 kV CKT 1 b. 5. Drop Load 1 WHIRLPO4 (509840) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0314_P4 | a. Apply single phase fault at MEMRIAL4 (514835) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MEMRIAL4 (514835) 138 kV to TENESTP4 (514837) 138 kV CKT 1 b. 2. Trip branch from MEMRIAL4 (514835) 138 kV to BRYANT 4 (514839) 138 kV CKT 1 b. 3. Trip branch from BRYANT 4 (514839) 138 kV to ACORN 4 (515459) 138 kV CKT 1 b. 4. Trip branch from ACORN 4 (515459) 138 kV to JONESSB4 (515480) 138 kV CKT 1 b. 5. Drop Load 1 BRYANT 4 (514839) 138 kV b. 6. Drop Load 1 ACORN 4 (515459) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0315_P4 | a. Apply single phase fault at S.S.---4 (509815) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S.S.---4 (509815) 138 kV to SHEFFD-4 (509812) 138 kV CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 b. 3. Trip branch from S.S.---4 (509815) 138 kV to PRATTV-4 (509758) 138 kV CKT 1 b. 4. Trip branch from PRATTV-4 (509758) 138 kV to BLUEBEL4 (515242) 138 kV CKT 1 b. 5. Drop Load 1 PRATTV-4 (509758) 138 kV b. 6. Drop Load 1 SHEFFD-4 (509812) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0316_P4 | a. Apply single phase fault at R.S.S.-4 (509783) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from R.S.S.-4 (509783) 138 kV to ORU ETP4 (509849) 138 kV CKT 1 b. 2. Trip branch from ORU ETP4 (509849) 138 kV to WARNTAP4 (509858) 138 kV CKT 1 b. 3. Trip branch from ORU ETP4 (509849) 138 kV to ORU E4 (509738) 138 kV CKT 1 b. 4. Trip branch from R.S.S.-4 (509783) 138 kV to ORU-WTP4 (509853) 138 kV CKT 1 b. 5. Trip branch from ORU-WTP4 (509853) 138 kV to SHILETP4 (509813) 138 kV CKT 1 b. 6. Trip branch from ORU-WTP4 (509853) 138 kV to ORU W4 (509732) 138 kV CKT 1 b. 7. Drop Load 1 ORU W4 (509732) 138 kV b. 8. Drop Shunt 1 ORU W4 (509732) 138 kV b. 9. Drop Load 1 ORU E4 (509738) 138 kV b. 10. Drop Shunt 1 ORU E4 (509738) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0317_P4 | a. Apply single phase fault at DVISION4 (514853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DVISION4 (514853) 138 kV to LAKESID4 (514849) 138 kV CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV to HEFNER 4 (514848) 138 kV CKT 1 b. 3. Trip branch from DVISION4 (514853) 138 kV to SLVRLAK4 (514852) 138 kV CKT 1 b. 4. Drop Load 1 LAKESID4 (514849) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0318_P4 | a. Apply single phase fault at T.NO.--7 (509852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV to T.NO.2-4 (509895) kV to TNO2-1 (509894) 34.5 kV CKT1 b. 2. Trip branch from T.NO.2-4 (509895) 138 kV to T.NO.--4 (509817) 138 kV CKT 1 b. 3. Trip branch from T.NO.--7 (509852) 345 kV to N.E.S.-7 (510406) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0319_P4 | a. Apply single phase fault at WEKIWA-4 (509757) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV to WEKIWA-4 (509757) kV to WEKIW1-1 (509879) 34.5 kV CKT1 b. 2. Trip branch from WEKIWA-4 (509757) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to 4SILVCTY (300140) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0320_P4 | a. Apply single phase fault at WOODRNG7 (514715) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) kV to WOODRNG1 (515770) 13.8 kV CKT1 b. 2. Trip branch from WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0321_P4 | a. Apply single phase fault at 4CLEVLND (300138) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4CLEVLND (300138) 138 kV to CLEVLND 4 (512729) 138 kV CKT Z1 b. 2. Trip three winding transformer from CLEVLND7 (512694) 345 kV to CLEVLND 4 (512729) kV to CLEVLND1 (512817) 13.8 kV CKT1 b. 3. Trip branch from 4CLEVLND (300138) 138 kV to PAWNSW4 (512749) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0322_P4 | a. Apply single phase fault at CTNWOOD4 (514827) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV to ARCADIA4 (514907) 138 kV CKT 1 b. 2. Trip branch from CTNWOOD4 (514827) 138 kV to PINE ST4 (514829) 138 kV CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV to FITZGRD4 (514830) 138 kV CKT 1 b. 4. Trip branch from FITZGRD4 (514830) 138 kV to KINZE 4 (515008) 138 kV CKT 1 b. 5. Drop Load 1 PINE ST4 (514829) 138 kV b. 6. Drop Load 2 PINE ST4 (514829) 138 kV b. 7. Drop Load 1 FITZGRD4 (514830) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0324_P4 | a. Apply single phase fault at SAPLPRD4 (509871) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SAPLPRD4 (509871) 138 kV to SAPLPRD7 (509870) kV to SAPLPRD1 (509872) 13.8 kV CKT1 b. 2. Trip branch from SAPLPRD4 (509871) 138 kV to OAKSWTP4 (509848) 138 kV CKT 1 b. 3. Trip branch from OAKSWTP4 (509848) 138 kV to OAKS W4 (509727) 138 kV CKT 1 b. 4. Trip branch from OAKSWTP4 (509848) 138 kV to T.P.S.-4 (509788) 138 kV CKT 1 b. 5. Drop Load 1 OAKS W4 (509727) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0325_P4 | a. Apply single phase fault at ARCADIA4 (514907) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA4 (514907) 138 kV to RNDBARN4 (515461) 138 kV CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV to BURGETT4 (514510) 138 kV CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV to DANFRTH4 (514833) 138 kV CKT 1 b. 4. Trip three winding transformer from ARCADIA4 (514907) 138 kV to ARCADIA7 (514908) kV to ARCADI41 (515700) 13.8 kV CKT1 b. 5. Drop Load 1 BURGETT4 (514510) 138 kV b. 6. Drop Load 1 RNDBARN4 (515461) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0326_P4 | a. Apply single phase fault at BV-SE--4 (510391) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BV-SE--4 (510391) 138 kV to RICE CK4 (510385) 138 kV CKT 1 b. 2. Trip branch from RICE CK4 (510385) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 3. Trip branch from BV-SE--4 (510391) 138 kV to BV-COM-4 (510390) 138 kV CKT 1 b. 4. Drop Load M1 RICE CK4 (510385) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0328_P4 | a. Apply single phase fault at NEOSHO 7 (532793) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV to G17-209-TAP (760921) 345 kV CKT 1 b. 2. Trip three winding transformer from NEOSHO 7 (532793) 345 kV to NEOSHO 5 (532937) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0329_P4 | a. Apply single phase fault at N.E.S.-4 (510396) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N.E.S.-4 (510396) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 2. Trip branch from OOLOGAHKM 4 (513124) 138 kV to CLARMR 4 (512707) 138 kV CKT 1 b. 3. Trip three winding transformer from CLARMR 4 (512707) 138 kV to CLARMR 5 (512651) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 4. Trip branch from N.E.S.-4 (510396) 138 kV to OWASO2_4 (509843) 138 kV CKT 1 b. 5. Trip branch from OWASO2_4 (509843) 138 kV to PCATSAT4 (509841) 138 kV CKT 1 b. 6. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0330_P4 | a. Apply single phase fault at NEOSHO 4 (533021) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHO 7 (532793) kV to N345 1 1 (532824) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 4 (533021) 138 kV to NEOSHON4 (533022) 138 kV CKT Z1 b. 3. Drop Shunt 1 N345 1 1 (532824) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0331_P4 | a. Apply single phase fault at NEOSHO 5 (532937) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV to NEOSHO 7 (532793) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 5 (532937) 161 kV to RIV4525 (547469) 161 kV CKT 1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0332_P4 | a. Apply single phase fault at NEOSHOS2 (533778) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHOS2 (533778) kV to NSES 2X1 (532710) 13.2 kV CKT1 b. 2. Trip branch from NEOSHOS2 (533778) 69 kV to BAKER 2 (532926) 69 kV CKT 1 b. 3. Trip branch from BAKER 2 (532926) 69 kV to SOPITT 2 (533773) 69 kV CKT 1 b. 4. Drop Load 1 BAKER 2 (532926) 69 kV b. 5. Drop Load 2 BAKER 2 (532926) 69 kV b. 6. Drop Load 3 BAKER 2 (532926) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0333_P4 | a. Apply single phase fault at ALTOONA4 (533001) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ALTOONA4 (533001) 138 kV to G17-022-TAP (588664) 138 kV CKT 1 b. 2. Trip branch from ALTOONA4 (533001) 138 kV to TAYLOR 4 (533006) 138 kV CKT 1 b. 3. Trip branch from TAYLOR 4 (533006) 138 kV to MONTGOM4 (533004) 138 kV CKT 1 b. 4. Drop Load 1 TAYLOR 4 (533006) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0334_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to DELWARE4 (510379) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0335_P1 | 3 phase fault on N.E.S.-7 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345 kV Bus to ONETA--7 (509807) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0336_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to 7BLACKBERRY (300739) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0337_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-009-TAP (532777) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0338_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-209-TAP (760921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0339_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 4 (533021) 138 kV Bus to N345 1 1 (532824) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 1 1 (532824) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0340_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 5 (532937) 161 kV Bus to N345 2 1 (532825) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 2 1 (532825) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0341_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0342_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHON4 (533022) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0343_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to FARML 4 (512734) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0344_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS4 (533020) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0345_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHO 4 (533021) 138 kV Bus to NEOSH4 1 (532958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0346_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS2 (533778) 69 kV Bus to NSES 2X1 (532710) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0347_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to MARMTNW5 (532935) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0348_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to RIV4525 (547469) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0349_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHOS4 (533020) 138 kV Bus to NEOSH5 1 (532959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0350_P1 | 3 phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138 kV Bus to TV1MNDV4 (533008) 138 kV Bus CKT 1 b. 2. Trip branch from TV1MNDV4 (533008) 138 kV Bus to LIBERTY4 (533003) 138 kV Bus CKT 1 b. 3. Drop Load K1 at TV1MNDV4 (533008) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0351_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0352_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHON4 (533022) 138 kV Bus to NEOSHON2 (533768) 69 kV Bus to NEC U3 (532711) 12 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0353_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0354_P1 | 3 phase fault on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DELWARE7 (510380) 345 kV Bus to DELWARE4 (510379) 138 kV Bus to DELAWAR1 (510370) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0355_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to NEOSHON2 (533768) 69 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0356_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to BAKER 2 (532926) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0357_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to CRAWFOR2 (533758) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0358_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to ORDNJCT2 (533703) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0359_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to DEARING4 (533002) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0360_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to NBVILLE4 (510386) 138 kV Bus CKT 1 b. 2. Trip branch from NBVILLE4 (510386) 138 kV Bus to BV-SE--4 (510391) 138 kV Bus CKT 1 b. 3. Drop Load M1 at NBVILLE4 (510386) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0361_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0362_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0363_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0364_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0365_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML 4 (512734) 138 kV Bus to SCOFCTY4 (510378) 138 kV Bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138 kV Bus to SCOFFEYV4 (510420) 138 kV Bus CKT 1 b. 3. Trip branch from SCOFCTY4 (510378) 138 kV Bus to COFFEYT4 (510422) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SCOFFEYV4 (510420) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0366_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA1-1 (509881) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0367_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA2-1 (509868) 34.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0368_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA5-1 (509874) 34.5 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0369_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0370_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0371_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0372_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0373_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV Bus to T.NO.2-4 (509895) 138 kV Bus to TNO2-1 (509894) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0374_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0375_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0376_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY2 (512741) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0377_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7JASPER (300949) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0378_P1 | 3 phase fault on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-209-TAP (760921) 345 kV Bus to LACYGNE7 (542981) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0379_P1 | 3 phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CANEYRV7 (532780) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0381_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARMTNW5 (532935) 161 kV Bus to MARMTNE5 (532934) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0382_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARMTNW5 (532935) 161 kV Bus to MARMATN2 (533639) 69 kV Bus to MARMATN1 (532955) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0383_P1 | 3 phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFOR2 (533758) 69 kV Bus to SE1GREE2 (533772) 69 kV Bus CKT 1 b. 2. Trip branch from SE1GREE2 (533772) 69 kV Bus to GIR JCT2 (533762) 69 kV Bus CKT 1 b. 3. Drop Load K1 at CRAWFOR2 (533758) 69 kV Bus b. 4. Drop Load 1 at CRAWFOR2 (533758) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0384_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 5JASPER (300950) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0385_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0387_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY1 (512740) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0388_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to NEOSHO 7 (532793) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0389_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0390_P4 | a. Apply single phase fault at SUNNYSD7 (515136) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV to SUNNYSD4 (515135) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip branch from SUNNYSD7 (515136) 345 kV to TERRYRD7 (511568) 345 kV CKT 1 b. 3. Drop Shunt SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0391_P4 | a. Apply single phase fault at ARBUCKL4 (515117) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARBUCKL4 (515117) 138 kV to VANOSTP4 (515531) 138 kV CKT 1 b. 2. Trip branch from ARBUCKL4 (515117) 138 kV to SULPHR 4 (515559) 138 kV CKT 1 b. 3. Trip branch from SULPHR 4 (515559) 138 kV to JOLLYVL4 (515118) 138 kV CKT 1 b. 4. Trip branch from JOLLYVL4 (515118) 138 kV to PRICESF4 (514814) 138 kV CKT 1 b. 5. Trip branch from PRICESF4 (514814) 138 kV to HONEYCK4 (515643) 138 kV CKT 1 b. 6. Drop Load 1 SULPHR 4 (515559) 138 kV b. 7. Drop Load 1 JOLLYVL4 (515118) 138 kV b. 8. Drop Load 1 PRICESF4 (514814) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0392_P4 | a. Apply single phase fault at FTSMTHW5 (515301) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FTSMTHW5 (515301) 161 kV to FTSMITH7 (515302) kV to FTSMTH51 (515728) 13.8 kV CKT5 b. 2. Trip branch from FTSMTHW5 (515301) 161 kV to ARKOMA 5 (515306) 161 kV CKT 1 b. 3. Trip branch from ARKOMA 5 (515306) 161 kV to 3RDST 5 (515308) 161 kV CKT 1 b. 4. Drop Shunt 1 ARKOMA 5 (515306) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0393_P4 | a. Apply single phase fault at PARKLN 4 (515178) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PARKLN 4 (515178) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to SEMINOL4 (515044) 138 kV CKT 1 b. 3. Trip branch from PARKLN 4 (515178) 138 kV to SOTHADA4 (515318) 138 kV CKT 1 b. 4. Trip branch from SOTHADA4 (515318) 138 kV to HARDEN 4 (515362) 138 kV CKT 1 b. 5. Trip branch from HARDEN 4 (515362) 138 kV to EFITSTP4 (515699) 138 kV CKT 1 b. 6. Trip branch from EFITSTP4 (515699) 138 kV to LULA 4 (515192) 138 kV CKT 1 b. 7. Trip branch from EFITSTP4 (515699) 138 kV to EFITTS 4 (515809) 138 kV CKT 1 b. 8. Drop Load 1 LKKONWA4 (515977) 138 kV b. 9. Drop Load 1 SOTHADA4 (515318) 138 kV b. 10. Drop Load 1 HARDEN 4 (515362) 138 kV b. 11. Drop Load 1 EFITTS 4 (515809) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0394_P4 | a. Apply single phase fault at LONEOAK4 (510897) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LONEOAK4 (510897) 138 kV to HARTSHN4 (520934) 138 kV CKT 1 b. 2. Trip branch from LONEOAK4 (510897) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 3. Trip branch from SMCALTP4 (510906) 138 kV to MCALEST4 (510908) 138 kV CKT 1 b. 4. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 5. Drop Load 1 S-MCALT4 (510865) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0395_P4 | a. Apply single phase fault at FTSMTHE5 (515300) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FTSMTHE5 (515300) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 2. Trip branch from QUANXTP5 (515310) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 4. Trip branch from BARLING5 (515311) 161 kV to MASSARD5 (515343) 161 kV CKT 1 b. 5. Trip branch from FTSMTHE5 (515300) 161 kV to COLONY 5 (515345) 161 kV CKT 1 b. 6. Trip branch from COLONY 5 (515345) 161 kV to BATTLEF5 (515349) 161 kV CKT 1 b. 7. Trip branch from BATTLEF5 (515349) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 8. Drop Load 1 BARLING5 (515311) 161 kV b. 9. Drop Load 1 QUANEXS5 (515474) 161 kV b. 10. Drop Load 1 COLONY 5 (515345) 161 kV b. 11. Drop Load 1 BATTLEF5 (515349) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0396_P4 | a. Apply single phase fault at WELETK4 (510902) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WELETK4 (510902) 138 kV to WELEETK4 (505592) 138 kV CKT 1 b. 2. Trip branch from WELETK4 (510902) 138 kV to EC.HEN-4 (510923) 138 kV CKT 1 b. 3. Trip branch from EC.HEN-4 (510923) 138 kV to OKMULGE4 (510898) 138 kV CKT 1 b. 4. Drop Load 1 EC.HEN-4 (510923) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0397_P4 | a. Apply single phase fault at MASSARD5 (515343) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MASSARD5 (515343) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 2. Trip branch from MASSARD5 (515343) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from BARLING5 (515311) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 4. Trip branch from QUANXTP5 (515310) 161 kV to FTSMTHE5 (515300) 161 kV CKT 1 b. 5. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 6. Drop Load 1 BARLING5 (515311) 161 kV b. 7. Drop Load 1 QUANEXS5 (515474) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0398_P4 | a. Apply single phase fault at ARCADIA7 (514908) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA7 (514908) 345 kV to REDBUD 7 (514909) 345 kV CKT 1 b. 2. Trip branch from ARCADIA7 (514908) 345 kV to NORTWST7 (514880) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0399_P4 | a. Apply single phase fault at DRAPER 7 (514934) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV to DRAPER 4 (514933) kV to DRAPER41 (515721) 13.8 kV CKT1 b. 2. Trip branch from DRAPER 7 (514934) 345 kV to NSUB345 (555234) kV CKT 1 b. 3. Drop Shunt 1 DRAPER41 (515721) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0400_P4 | a. Apply single phase fault at MUSKOGE7 (515224) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV to FTSMITH7 (515302) 345 kV CKT 1 b. 2. Trip branch from MUSKOGE7 (515224) 345 kV to H_SPRNG-TAP (588839) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0401_P4 | a. Apply single phase fault at SEMINOL4 (515044) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOL4 (515044) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to PARKLN 4 (515178) 138 kV CKT 1 b. 3. Trip branch from SEMINOL4 (515044) 138 kV to MAUD 4 (515055) 138 kV CKT 1 b. 4. Drop Load 1 LKKONWA4 (515977) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0402_P4 | a. Apply single phase fault at CHIKSAW4 (515171) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHIKSAW4 (515171) 138 kV to CARTER 4 (515138) 138 kV CKT 1 b. 2. Trip branch from CHIKSAW4 (515171) 138 kV to FNDTION4 (515162) 138 kV CKT 1 b. 3. Trip branch from FNDTION4 (515162) 138 kV to SPRNDAL4 (515172) 138 kV CKT 1 b. 4. Drop Load 1 FNDTION4 (515162) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0403_P4 | a. Apply single phase fault at SUNNYSD4 (515135) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNNYSD1 (515762) 13.8 kV CKT1 b. 3. Drop Shunt 1 SUNYSD 1 (515405) 13.8 kV b. 4. Drop Shunt 1 SUNNYSD1 (515762) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0404_P4 | a. Apply single phase fault at MCALEST4 (510908) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MCALEST4 (510908) 138 kV to TALAWANDA 4 (510951) 138 kV CKT 1 b. 2. Trip branch from TALAWANDA 4 (510951) 138 kV to MCALESTIND 4 (510909) 138 kV CKT 1 b. 3. Trip branch from TALAWANDA 4 (510951) 138 kV to C-RIVER4 (510946) 138 kV CKT 1 b. 4. Trip branch from MCALEST4 (510908) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 5. Trip branch from SMCALTP4 (510906) 138 kV to LONEOAK4 (510897) 138 kV CKT 1 b. 6. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 7. Drop Load 1 S-MCALT4 (510865) 138 kV b. 8. Drop Load 1 MCALESTIND 4 (510909) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0405_P4 | a. Apply single phase fault at S BROWN4 (505602) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S BROWN4 (505602) 138 kV to RUSSETT4 (521044) 138 kV CKT 1 b. 2. Trip branch from RUSSETT4 (521044) 138 kV to RUSSET-4 (515120) 138 kV CKT 1 b. 3. Trip branch from RUSSETT4 (521044) 138 kV to REAGAN 4 (520465) 138 kV CKT 1 b. 4. Trip branch from S BROWN4 (505602) 138 kV to COLBRTP4 (515159) 138 kV CKT 1 b. 5. Drop Load 1 RUSSETT4 (521044) 138 kV b. 6. Drop Load 1 REAGAN 4 (520465) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0406_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to C-RIVER7 (515422) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0407_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to HUGO 7 (521157) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0408_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN3-1 (510939) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0409_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN2-1 (510938) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0410_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 7 (514809) 345 kV Bus to SUNNYSD7 (515136) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0411_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JOHNCO 7 (514809) 345 kV Bus to JOHNCO 4 (514808) 138 kV Bus to JOHNCO11 (514810) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at JOHNCO11 (514810) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0412_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to ARCADIA7 (514908) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0413_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0414_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0415_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0416_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to SEMINOL7 (515045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0417_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO11 (515756) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO11 (515756) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0418_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO21 (515757) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO21 (515757) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0419_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from C-RIVER7 (515422) 345 kV Bus to C-RIVER4 (510946) 138 kV Bus to C-RIVER1 (510947) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0420_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0421_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT4 (510918) 138 kV Bus to VALIANT2 (510910) 69 kV Bus to VALN1-1 (510937) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0422_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to V-WEYCO4 (510866) 138 kV Bus CKT 1 b. 2. Drop Shunt 1 at V-WEYCO4 (510866) 138 kV Bus1 b. 3. Drop Load 1 at V-WEYCO4 (510866) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0423_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to IDABEL-4 (510886) 138 kV Bus CKT 1 b. 2. Trip branch from IDABEL-4 (510886) 138 kV Bus to B.BOWTP4 (510888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IDABEL-4 (510886) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0424_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO---4 (510901) 138 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0425_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO PP4 (520948) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0426_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to CANEYCK4 (515150) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0427_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to JOHNCO 7 (514809) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0428_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to RUSSET-4 (515120) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0429_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to SXMLCKT4 (515122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0430_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to VANOSTP4 (515531) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0431_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to PAOLI- 4 (515100) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0432_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to MAUD 4 (515055) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0433_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to LKKONWA4 (515977) 138 kV Bus CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV Bus to PARKLN 4 (515178) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0434_P1 | 3 phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply Fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER4 (510946) 138 kV Bus to TALAWANDA 4 (510951) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0435_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to WCITYTP2 (510870) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0436_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to KIPUMPT2 (510876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0437_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TURK 7 (507455) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0438_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0439_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 7 (507455) 345 kV Bus to TURK 4 (507454) 138 kV Bus to TURK 1 (507457) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0440_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX1-1 (508100) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NWTEX1-1 (508100) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0441_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX2-1 (508101) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at NWTEX2-1 (508101) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0442_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0443_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0444_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0445_P1 | 3 phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA 7 (508298) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0446_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO 7 (521157) 345 kV Bus to HUGOITC4 (520560) 138 kV Bus to HUGO TERTA (521189) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0447_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNNYSD1 (515762) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNNYSD1 (515762) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0448_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNYSD 1 (515405) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNYSD 1 (515405) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0449_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0450_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0451_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0452_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0453_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0454_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0455_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0456_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER21 (515792) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0457_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER41 (515721) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER41 (515721) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0458_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER31 (515720) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER31 (515720) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0459_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0460_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to TURK 7 (507455) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0461_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0462_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0463_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0464_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0465_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0466_P1 | 3 phase fault on HUGO---4 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO---4 (510901) 138 kV Bus to HUGO---2 (510893) 69 kV Bus to HUGO4-1 (510859) 13.8 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus b. 3. Drop Load 1 at HUGO---2 (510893) 69 kV Bus b. 4. Drop Shunt 1 at HUGO---2 (510893) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0467_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to HUGOITC4 (520560) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0468_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to VALLANT4 (521079) 138 kV Bus CKT 1 b. 2. Trip branch from VALLANT4 (521079) 138 kV Bus to GARVIN4 (520419) 138 kV Bus CKT 1 b. 3. Trip branch from GARVIN4 (520419) 138 kV Bus to IDABEL 4 (520953) 138 kV Bus CKT 1 b. 4. Drop Load 1 at VALLANT4 (521079) 138 kV Bus b. 5. Drop Load 1 at GARVIN4 (520419) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0469_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to FROGVIL4 (520918) 138 kV Bus CKT 1 b. 2. Trip branch from FROGVIL4 (520918) 138 kV Bus to WSBNKTP4 (521098) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0470_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to SAWYER4 (520411) 138 kV Bus CKT 1 b. 2. Trip branch from SAWYER4 (520411) 138 kV Bus to RATTAN 4 (521036) 138 kV Bus CKT 1 b. 3. Trip branch from RATTAN 4 (521036) 138 kV Bus to DARWIN 4 (520874) 138 kV Bus CKT 1 b. 4. Trip branch from DARWIN 4 (520874) 138 kV Bus to LANE 4 (520968) 138 kV Bus CKT 1 b. 5. Trip branch from LANE 4 (520968) 138 kV Bus to ATOKA--4 (510887) 138 kV Bus CKT 1 b. 6. Drop Load 1 at SAWYER4 (520411) 138 kV Bus b. 7. Drop Load 1 at RATTAN 4 (521036) 138 kV Bus b. 8. Drop Load 1 at DARWIN 4 (520874) 138 kV Bus b. 9. Drop Load 1 at LANE 4 (520968) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0471_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0472_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to RUSSETT4 (521044) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0473_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to GLASSES4 (515147) 138 kV Bus CKT 1 b. 2. Trip branch from GLASSES4 (515147) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASSES4 (515147) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0474_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to STIRLNG4 (515932) 138 kV Bus CKT 1 b. 2. Trip branch from STIRLNG4 (515932) 138 kV Bus to DRPSPRG4 (515873) 138 kV Bus CKT 1 b. 3. Trip branch from DRPSPRG4 (515873) 138 kV Bus to SPRNDAL4 (515172) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STIRLNG4 (515932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0475_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to HOWE 4 (521122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0476_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to MILLCKT4 (515121) 138 kV Bus CKT 1 b. 2. Trip branch from MILLCKT4 (515121) 138 kV Bus to MILLCRK4 (515196) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0477_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0478_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0479_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to LTLCITY4 (515151) 138 kV Bus CKT 1 b. 2. Trip branch from LTLCITY4 (515151) 138 kV Bus to BROWNTP4 (515152) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0480_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0481_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0482_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0483_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0484_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0485_P4 | a. Apply single phase fault at LYDIA 7 (508298) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LYDIA 7 (508298) 345 kV to WELSH 7 (508359) 345 kV CKT 1 b. 2. Trip branch from LYDIA 7 (508298) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0486_P4 | a. Apply single phase fault at DIANA 4 (508831) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DIANA 4 (508831) 138 kV to DIANA 7 (508832) kV to DIANA-N1 (508845) 13.8 kV CKT3 b. 2. Trip branch from DIANA 4 (508831) 138 kV to PERDUE 4 (508351) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0487_P4 | a. Apply single phase fault at BANN 4 (508054) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BANN 4 (508054) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip branch from BANN 4 (508054) 138 kV to REDSPRG4 (508075) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0488_P4 | a. Apply single phase fault at LONGWD 4 (508808) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from LONGWD 4 (508808) 138 kV to LONGWD 7 (508809) kV to LONGW1-1 (508819) 13.2 kV CKT1 b. 2. Trip branch from LONGWD 4 (508808) 138 kV to LIEBERM4 (508806) 138 kV CKT 1 b. 3. Drop Shunt 1 LONGW1-1 (508819) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0489_P4 | a. Apply single phase fault at SW SHV 4 (507759) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SW SHV 4 (507759) 138 kV to SW SHV 7 (507760) kV to SWSHV1-1 (507778) 13.8 kV CKT1 b. 2. Trip branch from SW SHV 4 (507759) 138 kV to LEASIDE 4 (507793) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0490_P4 | a. Apply single phase fault at PIRKEY 4 (508562) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV to EASTON 4 (509092) 138 kV CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV to BRANDYBR (508596) 138 kV CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV to KNOXLEE4 (508548) 138 kV CKT 1 b. 4. Trip branch from PIRKEY 4 (508562) 138 kV to HALLSVLS4 (508595) 138 kV CKT 1 b. 5. Trip branch from HALLSVLS4 (508595) 138 kV to WHITNEY4 (508575) 138 kV CKT 1 b. 6. Drop Load 1 EASTON 4 (509092) 138 kV b. 7. Drop Load 1 WHITNEY4 (508575) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0491_P4 | a. Apply single phase fault at NWTXARK7 (508072) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK7 (508072) 345 kV to TURK 7 (507455) 345 kV CKT 1 b. 2. Trip branch from NWTXARK7 (508072) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0492_P4 | a. Apply single phase fault at VALIANT7 (510911) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 1 b. 2. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0493_P4 | a. Apply single phase fault at NWTXARK4 (508071) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK4 (508071) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip three winding transformer from NWTXARK7 (508072) 345 kV to NWTXARK4 (508071) kV to NWTEX1-1 (508100) 13.8 kV CKT1 b. 3. Drop Shunt 1 NWTEX1-1 (508100) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0494_P4 | a. Apply single phase fault at PITTSB-7 (510907) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PITTSB-7 (510907) 345 kV to SEMINOL7 (515045) 345 kV CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0495_P4 | a. Apply single phase fault at VALIANT4 (510918) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT4 (510918) 138 kV to HUGO PP4 (520948) 138 kV CKT 1 b. 2. Trip branch from VALIANT4 (510918) 138 kV to IDABEL-4 (510886) 138 kV CKT 1 b. 3. Trip branch from IDABEL-4 (510886) 138 kV to B.BOWTP4 (510888) 138 kV CKT 1 b. 4. Trip branch from B.BOWTP4 (510888) 138 kV to CRAIGJT4 (510890) 138 kV CKT 1 b. 5. Trip branch from B.BOWTP4 (510888) 138 kV to B.BOW 4 (510864) 138 kV CKT 1 b. 6. Drop Load 1 IDABEL-4 (510886) 138 kV b. 7. Drop Load 1 B.BOW 4 (510864) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0496_P4 | a. Apply single phase fault at TURK 4 (507454) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV to TURK 7 (507455) kV to TURK 1 (507457) 13.8 kV CKT1 b. 2. Trip branch from TURK 4 (507454) 138 kV to MANDEVILTP4 (508105) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0497_P4 | a. Apply single phase fault at WILKES 4 (508840) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WILKES 4 (508840) 138 kV to WILKES 7 (508841) kV to WILKES-1 (508826) 13.2 kV CKT1 b. 2. Trip branch from WILKES 4 (508840) 138 kV to LSSOUTH4 (508297) 138 kV CKT 1 b. 3. Drop Shunt 1 WILKES-1 (508826) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0498_P4 | a. Apply single phase fault at PIRKEY 7 (508563) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 7 (508563) 345 kV to DIANA 7 (508832) 345 kV CKT 1 b. 2. Trip branch from PIRKEY 7 (508563) 345 kV to LEBROCK7 (508572) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0499_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-M1 (508843) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0500_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-N1 (508845) 13.8 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0501_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0502_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV Bus to TURK 3 (507456) 115 kV Bus to TURK1 1 (507458) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0503_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0504_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to SPPMAINBUS (5917) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0505_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0506_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-S1 (508844) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0507_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0508_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY4 (508575) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0509_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT1-1 (508589) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0510_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT2-1 (508590) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0511_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to OAKPH 4 (508816) 138 kV Bus CKT 1 b. 2. Trip branch from OAKPH 4 (508816) 138 kV Bus to FLOURNY4 (507727) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OAKPH 4 (508816) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0512_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to NORAM 4 (507774) 138 kV Bus CKT 1 b. 2. Trip branch from NORAM 4 (507774) 138 kV Bus to RAINES 4 (507749) 138 kV Bus CKT 1 b. 3. Trip branch from RAINES 4 (507749) 138 kV Bus to ARSHILL4 (507711) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NORAM 4 (507774) 138 kV Bus b. 5. Drop Load 1 at RAINES 4 (507749) 138 kV Bus b. 6. Drop Shunt 1 at RAINES 4 (507749) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0513_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0514_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLOURNY4 (507727) 138 kV Bus to FLOURNY2 (507726) 69 kV Bus to FLOURNY1 (507740) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0515_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138 kV Bus to GENMOTR4 (507732) 138 kV Bus CKT 1 b. 2. Trip branch from GENMOTR4 (507732) 138 kV Bus to SW SHV 4 (507759) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GENMOTR4 (507732) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0516_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WOOLWTP2 (507770) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0517_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to PINESRD2 (507747) 69 kV Bus CKT 1 b. 2. Trip branch from PINESRD2 (507747) 69 kV Bus to HARDY 2 (507734) 69 kV Bus CKT 1 b. 3. Drop Load 1 at PINESRD2 (507747) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0518_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WASKOM 2 (508839) 69 kV Bus CKT 1 b. 2. Trip branch from WASKOM 2 (508839) 69 kV Bus to MVPIPET2 (508825) 69 kV Bus CKT 1 b. 3. Drop Load 1 at WASKOM 2 (508839) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0519_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to FTHUMBG4 (507731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0520_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to MCWILLI4 (507742) 138 kV Bus CKT 1 b. 2. Trip branch from MCWILLI4 (507742) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MCWILLI4 (507742) 138 kV Bus b. 4. Drop Shunt 1 at MCWILLI4 (507742) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0521_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH1-1 (507712) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0522_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH2-1 (507714) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0523_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0524_P1 | 3 phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply Fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138 kV Bus to IPCJEFF4 (508833) 138 kV Bus CKT 1 b. 2. Trip branch from IPCJEFF4 (508833) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IPCJEFF4 (508833) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0526_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0527_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to TENRUSK7 (508585) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0528_P1 | 3 phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345 kV Bus to CROCKET7 (509241) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0529_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345 kV Bus to 7GRIMES% (334028) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0530_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to LEASIDE 4 (507793) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0531_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to S SHV 4 (507755) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0532_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to POWELL 4 (507748) 138 kV Bus CKT 1 b. 2. Trip branch from POWELL 4 (507748) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POWELL 4 (507748) 138 kV Bus b. 4. Drop Shunt 1 at POWELL 4 (507748) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0533_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to SPRIDGE4 (507757) 138 kV Bus CKT 1 b. 2. Trip branch from SPRIDGE4 (507757) 138 kV Bus to WLNTSPRINGS4 (509103) 138 kV Bus CKT 1 b. 3. Trip branch from WLNTSPRINGS4 (509103) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SPRIDGE4 (507757) 138 kV Bus b. 5. Drop Load 2 at SPRIDGE4 (507757) 138 kV Bus b. 6. Drop Load 1 at WLNTSPRINGS4 (509103) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0534_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to CARROLL6 (500140) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0535_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to REDBAYOU_6 (500255) 230 kV Bus CKT 1 b. 2. Trip branch from REDBAYOU_6 (500255) 230 kV Bus to MANCOMP 6 (500525) 230 kV Bus CKT 1 b. 3. Trip branch from MANCOMP 6 (500525) 230 kV Bus to J1673 POI (46734) 230 kV Bus CKT 1 b. 4. Drop Load IN at REDBAYOU_6 (500255) 230 kV Bus b. 5. Drop Load IN at MANCOMP 6 (500525) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0536_P1 | 3 phase fault on J1673 POI (46734) 230 kV Bus a. Apply Fault at the J1673 POI (46734) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from J1673 POI (46734) 230 kV Bus to FISHER 6 (500310) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0537_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0538_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0539_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to B.BOW 4 (510864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at B.BOW 4 (510864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0540_P1 | 3 phase fault on SUGARHL4 (508080) 138 kV Bus a. Apply Fault at the SUGARHL4 (508080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUGARHL4 (508080) 138 kV Bus to SUGARHL2 (508079) 69 kV Bus to SHILL1-1 (508103) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0541_P1 | 3 phase fault on HOPE 3 (507453) 115 kV Bus a. Apply Fault at the HOPE 3 (507453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOPE 3 (507453) 115 kV Bus to HOPESWI3 (507452) 115 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOPE 3 (507453) 115 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0542_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MANDEVILTP4 (508105) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0543_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MANDEVILTP4 (508105) 138 kV Bus to NE-TEXARK2 (504363) 69 kV Bus to NE-TEXARK1 (504364) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0544_P1 | 3 phase fault on OKAY 4 (507428) 138 kV Bus a. Apply Fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAY 4 (507428) 138 kV Bus to OKAY 2 (507427) 69 kV Bus to OKAY1-1 (507442) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0545_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN1-1 (508097) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0546_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN2-1 (508096) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0547_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to REDSPRG4 (508075) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0548_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0549_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0550_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CROCKET7 (509241) 345 kV Bus to CROCKET4 (509240) 138 kV Bus to CROCK-B1 (509243) 13.8 kV Bus CKT 1 b. 2. Trip branch from CROCKET4 (509240) 138 kV Bus to GRAPLND4 (509322) 138 kV Bus CKT 1 b. 3. Trip branch from GRAPLND4 (509322) 138 kV Bus to SLOCUM 4 (509326) 138 kV Bus CKT 1 b. 4. Trip branch from SLOCUM 4 (509326) 138 kV Bus to ALTO 4 (509320) 138 kV Bus CKT 1 b. 5. Trip branch from ALTO 4 (509320) 138 kV Bus to PINEGRV4 (509324) 138 kV Bus CKT 1 b. 6. Trip branch from PINEGRV4 (509324) 138 kV Bus to JACKSNV4 (509242) 138 kV Bus CKT 1 b. 7. Trip branch from JACKSNV4 (509242) 138 kV Bus to OVERTON4 (509080) 138 kV Bus CKT 1 b. 8. Drop Load 1 at GRAPLND4 (509322) 138 kV Bus b. 9. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 10. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 11. Drop Load 1 at ALTO 4 (509320) 138 kV Bus b. 12. Drop Load 1 at PINEGRV4 (509324) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0551_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 7ROCKYCRK% (334197) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0552_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_1 (334163) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at 1GRIMES_1 (334163) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0553_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_2 (334018) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at 1GRIMES_2 (334018) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0554_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 6GRIMES! (334027) 230 kV Bus CKT 1 b. 2. Trip branch from 6GRIMES! (334027) 230 kV Bus to 6PONDEROSA! (334088) 230 kV Bus CKT 1 b. 3. Trip three winding transformer from 6PONDEROSA! (334088) 230 kV Bus to 4PONDEROSA% (334087) 138 kV Bus to 1PONDEROSA (334094) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0555_P1 | 3 phase fault on 7ROCKYCRK% (334197) 345 kV Bus a. Apply Fault at the 7ROCKYCRK% (334197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7ROCKYCRK% (334197) 345 kV Bus to 6ROCKYCRK (334198) 230 kV Bus CKT 1 b. 2. Trip branch from 6ROCKYCRK (334198) 230 kV Bus to J1671 POI (46714) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0556_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LEASIDE 4 (507793) 138 kV Bus to LEASIDE 2 (507794) 69 kV Bus to LEASIDE 1-1 (507795) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0557_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to WESTELC4 (507767) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0558_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to STONWAL4 (509052) 138 kV Bus CKT 1 b. 2. Trip branch from STONWAL4 (509052) 138 kV Bus to KEATCHI4 (509050) 138 kV Bus CKT 1 b. 3. Trip branch from KEATCHI4 (509050) 138 kV Bus to GEORPAC4 (509064) 138 kV Bus CKT 1 b. 4. Trip branch from GEORPAC4 (509064) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 b. 5. Drop Load 1 at STONWAL4 (509052) 138 kV Bus b. 6. Drop Load 1 at KEATCHI4 (509050) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0559_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to LSSOUTH4 (508297) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0560_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WELSHRE4 (508355) 138 kV Bus CKT 1 b. 2. Trip branch from WELSHRE4 (508355) 138 kV Bus to CHAPELH4 (508337) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WELSHRE4 (508355) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0561_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0562_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0563_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WATLANT4 (508090) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0564_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to MUNZCTY4 (508064) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0565_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP1 (5921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0566_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP2 (5922) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0567_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP3 (5923) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0568_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-REAC1 (5924) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0569_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to WELSHDC1 (5919) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0570_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to 7SAREPTA% (337376) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0571_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0572_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LONGWD 7 (508809) 345 kV Bus to LONGWD 4 (508808) 138 kV Bus to LONGW1-1 (508819) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at LONGW1-1 (508819) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0573_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 2. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 3. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 5. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 6. Drop Load 1 at ALUMAX 4 (508091) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault b. 12. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 13. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 14. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0574_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to PATTERS4 (507431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0575_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0576_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0577_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to PITTSB_4 (508313) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0578_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to DIANA 4 (508831) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0579_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LSSOUTH4 (508297) 138 kV Bus to LSSOUTH2 (508296) 69 kV Bus to LSS-1 (508325) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0580_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to PETTY 4 (508310) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0581_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 7 (508841) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0582_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to CHAPLHL4 (509664) 138 kV Bus CKT 1 b. 2. Trip branch from CHAPLHL4 (509664) 138 kV Bus to LIBERTH4 (509643) 138 kV Bus CKT 1 b. 3. Trip branch from LIBERTH4 (509643) 138 kV Bus to ARGO 4 (509665) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHAPLHL4 (509664) 138 kV Bus b. 5. Drop Load 1 at LIBERTH4 (509643) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0583_P1 | 3 phase fault on ARGO 4 (509665) 138 kV Bus a. Apply Fault at the ARGO 4 (509665) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARGO 4 (509665) 138 kV Bus to ARGO 2 (509642) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0584_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to PERDUE 4 (508351) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0585_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to NGPLTAP4 (508837) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0586_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to DIANASW4 (509639) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0587_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to SPRHILL4 (508571) 138 kV Bus CKT 1 b. 2. Trip branch from SPRHILL4 (508571) 138 kV Bus to LLAMOND4 (508552) 138 kV Bus CKT 1 b. 3. Trip three winding transformer from LLAMOND4 (508552) 138 kV Bus to LLAMOND2 (508551) 69 kV Bus to LLAMON1- (508593) 13.8 kV Bus CKT 1 b. 4. Drop Load 1 at SPRHILL4 (508571) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0588_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY1-1 (508587) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0589_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY2-1 (508588) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0590_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0591_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV1-1 (507778) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SWSHV1-1 (507778) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0592_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV2-1 (507777) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at SWSHV2-1 (507777) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0593_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HUGO 7 (521157) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0594_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WILKES 7 (508841) 345 kV Bus to WILKES 4 (508840) 138 kV Bus to WILKES-1 (508826) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at WILKES-1 (508826) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0595_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0596_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0597_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to MANDEVILTP4 (508105) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0598_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWNR4 (507402) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWNR4 (507402) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWNR4 (507402) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0599_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWN_W 4 (504124) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWN_W 4 (504124) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWN_W 4 (504124) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0600_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN1-1 (507443) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0601_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN2-1 (507444) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0602_P1 | 3 phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply Fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWT-BNT4 (508070) 138 kV Bus to G18-003-TAP (762431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0603_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PERDUE 4 (508351) 138 kV Bus to PERDUE 2 (508350) 69 kV Bus to PERDUE 1 (508356) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0604_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to EXXONM 4 (508369) 138 kV Bus CKT 1 b. 2. Trip branch from EXXONM 4 (508369) 138 kV Bus to LHAWKIN4 (508358) 138 kV Bus CKT 1 b. 3. Drop Load 1 at EXXONM 4 (508369) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0605_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to BIGSAND4 (509603) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0606_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to NEWGLAD4 (508560) 138 kV Bus CKT 1 b. 2. Trip branch from NEWGLAD4 (508560) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 b. 3. Drop Load 1 at NEWGLAD4 (508560) 138 kV Bus b. 4. Drop Shunt 1 at NEWGLAD4 (508560) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0607_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to NGPL 4 (508827) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NGPL 4 (508827) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0608_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to PLILER 4 (508564) 138 kV Bus CKT 1 b. 2. Trip branch from PLILER 4 (508564) 138 kV Bus to LONGVHT4 (508554) 138 kV Bus CKT 1 b. 3. Trip branch from LONGVHT4 (508554) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PLILER 4 (508564) 138 kV Bus b. 5. Drop Load 1 at LONGVHT4 (508554) 138 kV Bus b. 6. Drop Shunt 1 at LONGVHT4 (508554) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0609_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to MARSHL-4 (508557) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0610_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to SABMINT4 (508566) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0611_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to HALLSVLS4 (508595) 138 kV Bus CKT 1 b. 2. Trip branch from HALLSVLS4 (508595) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HALLSVLS4 (508595) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0612_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to EASTON 4 (509092) 138 kV Bus CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV Bus to BRANDYBR (508596) 138 kV Bus CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 4. Drop Load 1 at EASTON 4 (509092) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0613_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#11 (508591) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0614_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#21 (508592) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0615_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARSHL-4 (508557) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0616_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to CHEROKE4 (509059) 138 kV Bus CKT 1 b. 2. Trip branch from CHEROKE4 (509059) 138 kV Bus to TATUM 4 (509087) 138 kV Bus CKT 1 b. 3. Trip branch from TATUM 4 (509087) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHEROKE4 (509059) 138 kV Bus b. 5. Drop Load 1 at TATUM 4 (509087) 138 kV Bus b. 6. Drop Load 2 at TATUM 4 (509087) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0617_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to OAK2HIL4 (509078) 138 kV Bus CKT 1 b. 2. Trip branch from OAK2HIL4 (509078) 138 kV Bus to OAK1HIL4 (509077) 138 kV Bus CKT 1 b. 3. Trip branch from OAK1HIL4 (509077) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 4. Drop Load 1 at OAK2HIL4 (509078) 138 kV Bus b. 5. Drop Load 1 at OAK1HIL4 (509077) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0618_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SABINEM4 (508577) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SABINEM4 (508577) 138 kV Bus b. 3. Drop Load 2 at SABINEM4 (508577) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0619_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SEMRSHL4 (508569) 138 kV Bus CKT 1 b. 2. Trip branch from SEMRSHL4 (508569) 138 kV Bus to SCOTTSV4 (508567) 138 kV Bus CKT 1 b. 3. Trip branch from SCOTTSV4 (508567) 138 kV Bus to LONGWD 4 (508808) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SEMRSHL4 (508569) 138 kV Bus b. 5. Drop Load 1 at SCOTTSV4 (508567) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0620_P4 | a. Apply single phase fault at 3SAREPTA! (337363) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3SAREPTA! (337363) 115 kV to 7SAREPTA% (337376) 345 kV CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115 kV to 3MINDEN_LA! (337361) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0621_P4 | a. Apply single phase fault at 3STERLING% (337415) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3STERLING% (337415) 115 kV to 8STERLING% (337420) kV to 1STERLING3 (337412) 13.8 kV CKT3 b. 2. Trip branch from 3STERLING% (337415) 115 kV to 8STERLING2% (337413) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0622_P4 | a. Apply single phase fault at 3STERL2% (337414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3STERL2% (337414) 115 kV to 3DREW_LA (337382) 115 kV CKT 1 b. 2. Trip branch from 3DREW_LA (337382) 115 kV to 3CHENIERE (337383) 115 kV CKT 1 b. 3. Trip branch from 3CHENIERE (337383) 115 kV to 3RISER (337384) 115 kV CKT 1 b. 4. Trip branch from 3RISER (337384) 115 kV to 3FROSTKRAFT! (337385) 115 kV CKT 1 b. 5. Trip branch from 3STERL2% (337414) 115 kV to 8STERLING2% (337413) 500 kV CKT 2 b. 6. Drop Load 1 3DREW_LA (337382) 115 kV b. 7. Drop Load 1 3CHENIERE (337383) 115 kV b. 8. Drop Load 1 3RISER (337384) 115 kV b. 9. Drop Shunt 1 3SHULER (337521) 115 kV b. 10. Drop Shunt 1 3RISER (337384) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0623_P4 | a. Apply single phase fault at 8EL DORADO% (337561) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8EL DORADO% (337561) 500 kV to 8MT_OLIVE% (337368) 500 kV CKT 1 b. 2. Trip branch from 8EL DORADO% (337561) 500 kV to 8STERLING% (337420) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0624_P4 | a. Apply single phase fault at LIEBERM4 (508806) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LIEBERM4 (508806) 138 kV to LONGWD 4 (508808) 138 kV CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138 kV to G16-167-TAP (588404) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0625_P4 | a. Apply single phase fault at 3MINDEN_LA! (337361) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3SAREPTA! (337363) 115 kV CKT 1 b. 2. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3MINDEN_LG (303302) 115 kV CKT 1 b. 3. Trip branch from 3MINDEN_LG (303302) 115 kV to 3ARCADIA (337367) 115 kV CKT 1 b. 4. Trip branch from 3ARCADIA (337367) 115 kV to 3REESE (337380) 115 kV CKT 1 b. 5. Trip branch from 3REESE (337380) 115 kV to 3TRUSSEL_CR (303310) 115 kV CKT 1 b. 6. Trip branch from 3TRUSSEL_CR (303310) 115 kV to 3VIENNA_LA! (337371) 115 kV CKT 1 b. 7. Drop Load 1 3MINDEN_LG (303302) 115 kV b. 8. Drop Load 1 3ARCADIA (337367) 115 kV b. 9. Drop Load LG 3ARCADIA (337367) 115 kV b. 10. Drop Load IN 3REESE (337380) 115 kV b. 11. Drop Load 1 3TRUSSEL_CR (303310) 115 kV b. 12. Drop Shunt 1 3MINDEN_LG (303302) 115 kV b. 13. Drop Load 1 3ARCADIA (337367) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0626_P4 | a. Apply single phase fault at 3EL DORADO! (337539) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3EL DORADO! (337539) 115 kV to 8EL DORADO% (337561) kV to 1EL DORADO1 (337564) 13.8 kV CKT1 b. 2. Trip branch from 3EL DORADO! (337539) 115 kV to 3ELDORADO.E! (337553) 115 kV CKT 1 b. 3. Drop Shunt 1 1EL DORADO1 (337564) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0627_P4 | a. Apply single phase fault at ARSHILL4 (507711) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARSHILL4 (507711) 138 kV to FTHUMBG4 (507731) 138 kV CKT 1 b. 2. Trip three winding transformer from ARSHILL4 (507711) 138 kV to ARSHILL2 (507710) kV to ARSH1-1 (507712) 12.47 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0628_P4 | a. Apply single phase fault at 3MCNEIL! (337516) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MCNEIL! (337516) 115 kV to 8MCNEIL% (337515) 500 kV CKT 1 b. 2. Trip branch from 3MCNEIL! (337516) 115 kV to 3MAGNOLIA.W (337519) 115 kV CKT 1 b. 3. Trip branch from 3MAGNOLIA.W (337519) 115 kV to 3MAGNOLIA.S (337520) 115 kV CKT 1 b. 4. Trip branch from 3MAGNOLIA.S (337520) 115 kV to 3SHULER (337521) 115 kV CKT 1 b. 5. Trip branch from 3SHULER (337521) 115 kV to 3WYATT! (337544) 115 kV CKT 1 b. 6. Drop Load IN 3MAGNOLIA.W (337519) 115 kV b. 7. Drop Load 1 3MAGNOLIA.S (337520) 115 kV b. 8. Drop Load IN 3SHULER (337521) 115 kV b. 9. Drop Load 1 3SHULER (337521) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0629_P4 | a. Apply single phase fault at 8STERLING2% (337413) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8STERLING2% (337413) 500 kV to 8PERRYVILLE% (337427) 500 kV CKT 1 b. 2. Trip branch from 8STERLING2% (337413) 500 kV to 8STERLING% (337420) 500 kV CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0630_P4 | a. Apply single phase fault at 8PERRYVILLE% (337427) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8BXTRWILSON% (336830) 500 kV CKT 1 b. 2. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8STERLING% (337420) 500 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0631_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G16-091-TAP (587744) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0632_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0633_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0634_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0635_P1 | 3 phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply Fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0636_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0637_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0638_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0639_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 b. 2. Drop Shunt 1 at OKLAUN HVDC7 (511565) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0640_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0641_P1 | 3 phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply Fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800]
04 - Southeast | 25S | Transfer | Group4_Fault_0642_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to G18-015-TAP (762467) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0643_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0644_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G17-171-TAP (760938) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0645_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0646_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NSUB345 (555234) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0647_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750000) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0648_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750001) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0649_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0650_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#4-1 (511414) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0651_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0652_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0653_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO11 (515714) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO11 (515714) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0654_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO21 (515715) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO21 (515715) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0655_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#5-1 (511411) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0656_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to FLETCHR4 (511422) 138 kV Bus CKT 1 b. 2. Drop Load 1 at FLETCHR4 (511422) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0657_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0658_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to L.E.S.-4 (511467) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0659_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to ELGINJT4 (511486) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0660_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to LWSTAP 4 (511439) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0661_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to SHERID4 (511474) 138 kV Bus CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV Bus to ARTVLTP4 (511537) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHERID4 (511474) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0662_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMMTAP4 (511494) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0663_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#1-1 (511416) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0664_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#2-1 (511415) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0665_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0666_P1 | 3 phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply Fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345 kV Bus to GRACMNT7 (515800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587773 [G16-095-GEN10.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0667_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0668_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0669_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to OMDUNCN4 (529304) 138 kV Bus CKT 1 b. 2. Trip branch from OMDUNCN4 (529304) 138 kV Bus to DUNCAN-4 (511453) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0670_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to G16-097-TAP (587794) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0671_P1 | 3 phase fault on COMANC-4 (511437) 138 kV Bus a. Apply Fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMANC-4 (511437) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0672_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to LWS S4 (511431) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LWS S4 (511431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0673_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to RPPAPER4 (511512) 138 kV Bus CKT 1 b. 2. Trip branch from RPPAPER4 (511512) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 b. 3. Drop Load 1 at RPPAPER4 (511512) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0674_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELGINJT4 (511486) 138 kV Bus to ELSWORTH 4 (511563) 138 kV Bus CKT 1 b. 2. Trip branch from ELSWORTH 4 (511563) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ELSWORTH 4 (511563) 138 kV Bus b. 4. Drop Load 2 at ELSWORTH 4 (511563) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0675_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELGINJT4 (511486) 138 kV Bus to ELGINJT2 (511487) 69 kV Bus to ELGJT1-1 (511412) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0676_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to SEQUOYAHJ4 (520422) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0677_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to MINCO 7 (514801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0678_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CLVLDSW4 (520508) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0679_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CHERRYRD 4 (521129) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0680_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to POCASET4 (521031) 138 kV Bus CKT 1 b. 2. Trip branch from POCASET4 (521031) 138 kV Bus to TUTLETP4 (521072) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POCASET4 (521031) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0681_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to GEORGIA4 (520923) 138 kV Bus CKT 1 b. 2. Trip branch from GEORGIA4 (520923) 138 kV Bus to FLETCH-4 (520912) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GEORGIA4 (520923) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0682_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANADARK4 (520814) 138 kV Bus to ANADARK2 (520810) 69 kV Bus to ADRKTERT (521181) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0683_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0685_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WASHITA4 (521089) 138 kV Bus to WASHITA2 (521088) 69 kV Bus to WASHTERT (521179) 7.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0686_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to ONEY 4 (521017) 138 kV Bus CKT 1 b. 2. Trip branch from ONEY 4 (521017) 138 kV Bus to BINGERJ4 (520827) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ONEY 4 (521017) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 599003 [BLUCAN2-WTG50.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0687_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to G16-037-TAP (560078) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0688_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0689_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 2. Trip branch from L.E.S.-4 (511467) 138 kV to COMMTAP4 (511494) 138 kV CKT 1 b. 3. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0690_P4 | a. Apply single phase fault at MINCO 7 (514801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MINCO 7 (514801) 345 kV to NSUB345 (555234) kV CKT 1 b. 2. Trip branch from MINCO 7 (514801) 345 kV to GRACMNT7 (515800) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0691_P4 | a. Apply single phase fault at GRACMNT4 (515802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GRACMNT4 (515802) 138 kV to GRACMNT7 (515800) kV to GRCMNT11 (515801) 13.8 kV CKT2 b. 2. Trip branch from GRACMNT4 (515802) 138 kV to ANADARK4 (520814) 138 kV CKT 1 b. 3. Drop Shunt 1 GRCMNT11 (515801) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0692_P4 | a. Apply single phase fault at L.E.S.-2 (511466) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-2 (511466) 69 kV to L.E.S.-4 (511467) kV to LES#1-1 (511416) 13.8 kV CKT1 b. 2. Trip branch from L.E.S.-2 (511466) 69 kV to LGORE-S2 (511470) 69 kV CKT 1 b. 3. Trip branch from LGORE-S2 (511470) 69 kV to LAW WC2 (511503) 69 kV CKT 1 b. 4. Drop Load 1 LGORE-S2 (511470) 69 kV b. 5. Drop Load 1 LAW WC2 (511503) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0693_P4 | a. Apply single phase fault at 112GORE4 (511488) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 112GORE4 (511488) 138 kV to COMANC-4 (511437) 138 kV CKT 1 b. 2. Trip branch from 112GORE4 (511488) 138 kV to LAIRGST4 (511510) 138 kV CKT 1 b. 3. Trip branch from LAIRGST4 (511510) 138 kV to CACHE4 (511500) 138 kV CKT 1 b. 4. Trip branch from LAIRGST4 (511510) 138 kV to L AIRGS4 (511429) 138 kV CKT 1 b. 5. Trip branch from CACHE4 (511500) 138 kV to G17-036_TAP (588779) 138 kV CKT 1 b. 6. Drop Load 1 CACHE4 (511500) 138 kV b. 7. Drop Load 1 L AIRGS4 (511429) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0694_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0696_P4 | a. Apply single phase fault at ELKCTY-4 (511458) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ELKCTY-4 (511458) 138 kV to CLINTJC4 (511485) 138 kV CKT 1 b. 2. Trip branch from ELKCTY-4 (511458) 138 kV to REDHLSW4 (521116) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0697_P4 | a. Apply single phase fault at WWRDEHV4 (515376) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WWRDEHV4 (515376) 138 kV to WWRDEHV7 (515375) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 2. Trip branch from WWRDEHV4 (515376) 138 kV to IODINE-4 (514796) 138 kV CKT 1 b. 3. Trip branch from IODINE-4 (514796) 138 kV to REDCLFT4 (515533) 138 kV CKT 1 b. 4. Trip branch from REDCLFT4 (515533) 138 kV to DEWEY 4 (514787) 138 kV CKT 1 b. 5. Trip branch from REDCLFT4 (515533) 138 kV to REDCLF 4 (515863) 138 kV CKT 1 b. 6. Drop Load 1 IODINE-4 (514796) 138 kV b. 7. Drop Load 1 REDCLF 4 (515863) 138 kV b. 8. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0698_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TOLK 6 (525531) 230 kV to TOLK 7 (525549) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 2. Trip branch from TOLK 6 (525531) 230 kV to PLANT_X 6 (525481) 230 kV CKT 2 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0699_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0700_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0701_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0702_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHEELER 6 (523777) 230 kV Bus to WHEELER 3 (523776) 115 kV Bus to WHEELER_TR11 (523774) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0703_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0704_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0705_P1 | 3 phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRAPEVINE 6 (523771) 230 kV Bus to GRAPEVINE 3 (523770) 115 kV Bus to GRAPEVN_TR11 (523769) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0706_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0707_P1 | 3 phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTTER_CO 7 (523961) 345 kV Bus to POTTER_CO 6 (523959) 230 kV Bus to POTTER_TR 1 (523957) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at POTTER_TR 1 (523957) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0708_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0709_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0710_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0711_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELKCITY6 (511490) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0712_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0713_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0714_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0715_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0716_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0717_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0718_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0719_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF3 (525539) kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0720_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0721_P4 | a. Apply single phase fault at CLARMR 5 (512651) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 4 (512707) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 4 (512707) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 3. Trip branch from OOLOGAHKM 4 (513124) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 4. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 2 (512679) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 5. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0722_P4 | a. Apply single phase fault at 4SILVCTY (300140) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4SILVCTY (300140) 138 kV to 4BRISTOW (300137) 138 kV CKT 1 b. 2. Trip branch from 4SILVCTY (300140) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0723_P4 | a. Apply single phase fault at GORE GR2 (512644) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GORE GR2 (512644) 69 kV to GORE 5 (505552) kV to GORTER1 (512832) 13.8 kV CKT1 b. 2. Trip branch from GORE GR2 (512644) 69 kV to 2VIAN (300879) 69 kV CKT 1 b. 3. Drop Load 1 2VIAN (300879) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0724_P4 | a. Apply single phase fault at CATSAGR5 (512638) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATSAGR5 (512638) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to COLINS 5 (512627) 161 kV CKT 1 b. 3. Trip branch from CATSAGR5 (512638) 161 kV to MAID 5 (512648) 161 kV CKT 1 b. 4. Drop Load 1 5ELMCRK (300993) 161 kV b. 5. Drop Load 2 5ELMCRK (300993) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0725_P4 | a. Apply single phase fault at CLARMR 2 (512679) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 2 (512679) 69 kV to CLARMR 5 (512651) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 2 (512679) 69 kV to CLARCTY4 2 (513014) 69 kV CKT 1 b. 3. Trip branch from CLARCTY4 2 (513014) 69 kV to CLARCTY1 2 (513010) 69 kV CKT 1 b. 4. Drop Load 1 CLARCTY4 2 (513014) 69 kV b. 5. Drop Load 1 CLARCTY1 2 (513010) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0726_P4 | a. Apply single phase fault at CATOOSA4 (509790) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATOOSA4 (509790) 138 kV to TERNITP4 (509835) 138 kV CKT 1 b. 2. Trip branch from TERNITP4 (509835) 138 kV to TER-NIT4 (509723) 138 kV CKT 1 b. 3. Trip branch from TERNITP4 (509835) 138 kV to VERDIGS4 (509854) 138 kV CKT 1 b. 4. Trip branch from VERDIGS4 (509854) 138 kV to CLARTOK4 (509864) 138 kV CKT 1 b. 5. Trip branch from CLARTOK4 (509864) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 6. Trip branch from CATOOSA4 (509790) 138 kV to INOLATP4 (509752) 138 kV CKT 1 b. 7. Trip branch from INOLATP4 (509752) 138 kV to INOLA 4 (509736) 138 kV CKT 1 b. 8. Trip branch from INOLATP4 (509752) 138 kV to ROCKPT-4 (510437) 138 kV CKT 1 b. 9. Trip branch from ROCKPT-4 (510437) 138 kV to CHOUTEA4 (510373) 138 kV CKT 1 b. 10. Trip branch from CHOUTEA4 (510373) 138 kV to EXCLART4 (510401) 138 kV CKT 1 b. 11. Drop Load 1 TER-NIT4 (509723) 138 kV b. 12. Drop Shunt 1 TER-NIT4 (509723) 138 kV b. 13. Drop Load M1 VERDIGS4 (509854) 138 kV b. 14. Drop Load M2 VERDIGS4 (509854) 138 kV b. 15. Drop Load 1 CLARTOK4 (509864) 138 kV b. 16. Drop Load 1 INOLA 4 (509736) 138 kV b. 17. Drop Load 1 ROCKPT-4 (510437) 138 kV b. 18. Drop Load 1 CHOUTEA4 (510373) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0727_P4 | a. Apply single phase fault at COLINS 5 (512627) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from COLINS 5 (512627) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to CATSAGR5 (512638) 161 kV CKT 1 b. 3. Trip branch from COLINS 5 (512627) 161 kV to 5KETONVL (300997) 161 kV CKT 1 b. 4. Trip branch from 5KETONVL (300997) 161 kV to CLARMR 5 (512651) 161 kV CKT 1 b. 5. Drop Load 2 5ELMCRK (300993) 161 kV b. 6. Drop Load 1 5KETONVL (300997) 161 kV b. 7. Drop Load 2 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0728_P4 | a. Apply single phase fault at HUNT 2 (512671) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HUNT 2 (512671) 69 kV to MAIDTP2 (512625) 69 kV CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV to GRDA1 2 (512727) 69 kV CKT 1 b. 3. Trip three winding transformer from GRDA1 2 (512727) 69 kV to GRDA1 5 (512656) kV to GRDA1 1 (512816) 13.8 kV CKT1 b. 4. Trip branch from HUNT 2 (512671) 69 kV to PRY0RC22 (512639) 69 kV CKT 1 b. 5. Trip branch from PRY0RC22 (512639) 69 kV to PRYORC32 (512622) 69 kV CKT 1 b. 6. Trip branch from PRYORC32 (512622) 69 kV to PRYORC12 (512810) 69 kV CKT 1 b. 7. Drop Load 1 PRY0RC22 (512639) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0729_P4 | a. Apply single phase fault at COLNSGR2 (512870) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from COLNSGR2 (512870) 69 kV to COLINS 5 (512627) kV to COLLIN3 1 (512840) 13.8 kV CKT2 b. 2. Trip branch from COLNSGR2 (512870) 69 kV to PARKMEDTP (512703) 69 kV CKT 1 b. 3. Trip branch from PARKMEDTP (512703) 69 kV to 2PARKMDWS (301999) 69 kV CKT 1 b. 4. Trip branch from PARKMEDTP (512703) 69 kV to SKIATTP2 (512871) 69 kV CKT 1 b. 5. Drop Load 1 2PARKMDWS (301999) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0730_P4 | a. Apply single phase fault at SPRGFLD5 (505492) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV to BROOKLINE 5 (549969) 161 kV CKT 1 b. 2. Trip branch from SPRGFLD5 (505492) 161 kV to CLAY 5 (549970) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0731_P4 | a. Apply single phase fault at JTEC 5 (549954) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JTEC 5 (549954) 161 kV to SW DISP PLT5 (549960) 161 kV CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 b. 3. Trip branch from JTEC 5 (549954) 161 kV to 5BTLFD (300348) 161 kV CKT 1 b. 4. Trip branch from 5BTLFD (300348) 161 kV to 5JAMESV (300089) 161 kV CKT 1 b. 5. Drop Load W SW DISP PLT5 (549960) 161 kV b. 6. Drop Load E SW DISP PLT5 (549960) 161 kV b. 7. Drop Load E 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0732_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to 2CDRCRST (301345) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0733_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0734_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0735_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0736_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to W.GRDNR7 (542965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0737_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFCRK7 (532797) 345 kV Bus to WOLFCRK2 (533653) 69 kV Bus to WOLFCRK1 (532962) 17 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0738_P1 | 3 phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0739_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0740_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 4 (512707) 138 kV Bus to CLARMR4 (512813) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0741_P1 | 3 phase fault on FT GIB 5 (505560) 161 kV Bus a. Apply Fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FT GIB 5 (505560) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0742_P1 | 3 phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply Fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAYGR 5 (512640) 161 kV Bus to OKAYGR 2 (512646) 69 kV Bus to OKAY1 (512848) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0743_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KETCHUM5 (512669) 161 kV Bus CKT 1 b. 2. Trip branch from KETCHUM5 (512669) 161 kV Bus to AFTON 5 (512632) 161 kV Bus CKT 1 b. 3. Drop Load 1 at KETCHUM5 (512669) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0744_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENSA 5 (512654) 161 kV Bus to PENSA 2 (512628) 69 kV Bus to PENSA 1 (512841) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0745_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to TAHLQH 5 (512655) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0746_P4 | a. Apply single phase fault at TATONGA7 (515407) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TATONGA7 (515407) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345 kV to WWRDEHV7 (515375) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0747_P4 | a. Apply single phase fault at HARPER 4 (539668) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HARPER 4 (539668) 138 kV to FLATRDG4 (539638) 138 kV CKT 1 b. 2. Trip branch from HARPER 4 (539668) 138 kV to MILANTP4 (539675) 138 kV CKT 1 b. 3. Trip branch from MILANTP4 (539675) 138 kV to CONWAY (539009) 138 kV CKT 1 b. 4. Trip branch from CONWAY (539009) 138 kV to VIOLA 4 (533075) 138 kV CKT 1 b. 5. Drop Load 1 CONWAY (539009) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0748_P4 | a. Apply single phase fault at DGRASSE7 (515852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0749_P4 | a. Apply single phase fault at MATHWSN7 (515497) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MATHWSN7 (515497) 345 kV to CIMARON7 (514901) 345 kV CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345 kV to TATONGA7 (515407) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0750_P4 | a. Apply single phase fault at BADGER 7 (515677) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 1 b. 2. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0751_P4 | a. Apply single phase fault at THISTLE7 (539801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0752_P4 | a. Apply single phase fault at DGRASSE4 (515853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0753_P4 | a. Apply single phase fault at CIMARON7 (514901) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CIMARON7 (514901) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from CIMARON7 (514901) 345 kV to NSUB345 (555234) kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0754_P4 | a. Apply single phase fault at CLARKCOUNTY7 (539800) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0755_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to WWDBORDT (755000) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0756_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV21 (515799) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at WWDEHV21 (515799) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0758_P1 | 3 phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FINNEY 7 (523853) 345 kV Bus to HOLCOMB7 (531449) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0761_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TR 1 (525537) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TOLK_TR 1 (525537) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0762_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF2 (525538) kV Bus CKT 2 b. 2. Drop Shunt 1 at TOLK_TF2 (525538) kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0763_P1 | 3 phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OCHILTREE 6 (523155) 230 kV Bus to OCHILTREE 3 (523154) 115 kV Bus to OCHLTRE_TR11 (523151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0764_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to HARPER 4 (539668) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0765_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0766_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV31 (515795) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at WWDEHV31 (515795) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0767_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0768_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to SETAB 7 (531465) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0769_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOLCOMB7 (531449) 345 kV Bus to HOLCOMB3 (531448) 115 kV Bus to HOLCTER1 (531450) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOLCTER1 (531450) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0770_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to BUCKNER7 (531501) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0771_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0772_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to CIM-PLT3 (539654) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0773_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0774_P1 | 3 phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply Fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from REDCLFT4 (515533) 138 kV Bus to REDCLF 4 (515863) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0775_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0776_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0777_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0778_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0779_P1 | 3 phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPERVIL7 (531469) 345 kV Bus to IRONWOOD7 (539803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0780_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to LAMB_CNTY 6 (525637) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_TR3 1 (525633) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0781_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0782_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0783_P1 | 3 phase fault on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIM-PLT3 (539654) 115 kV Bus to N-CIMRN3 (539749) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0784_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0785_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0786_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0787_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to BORDER 7 (515458) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0788_P1 | 3 phase fault on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BORDER 7 (515458) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0789_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0790_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0791_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0792_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345 kV Bus to GRAPEVINE (560035) 345 kV Bus CKT 1 b. 2. Trip branch from GRAPEVINE (560035) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0793_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0794_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0796_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0797_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0798_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0799_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS41 (514885) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS41 (514885) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0800_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS31 (515743) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS31 (515743) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0801_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS21 (515742) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS21 (515742) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0802_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0803_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to BVRCNTY7 (515554) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0804_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0805_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0806_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0807_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0808_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0809_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0810_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0811_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0812_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from THISTLE7 (539801) 345 kV Bus to THISTLE4 (539804) 138 kV Bus to THISTLE T1 (539802) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0813_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0814_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0815_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0816_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0817_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0818_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0819_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0820_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR21 (523094) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0821_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR01 (523091) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0822_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0823_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at CHISHOLM1 (511558) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0824_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to ELKCITY6 (511490) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0825_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to SWEETWT6 (511541) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0826_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to FINNEY 7 (523853) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0827_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 b. 2. Trip three winding transformer from HARBNGR7 (531512) 345 kV Bus to HARBNGR3 (531510) 115 kV Bus to HARBNGR-T (531511) 13.8 kV Bus CKT 1 b. 3. Trip branch from HARBNGR3 (531510) 115 kV Bus to WALKMYR3 (531405) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0828_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0829_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0830_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0831_P1 | 3 phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDNGTN7 (515875) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0832_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to OCHILTREE 6 (523155) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0833_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0834_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR11 (523092) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0835_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR41 (523098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0836_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0837_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0839_P1 | 3 phase fault on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE4 (539804) 138 kV Bus to FLATRDG4 (539638) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0840_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORLND4 (520999) 138 kV Bus to MOORLND2 (520995) 69 kV Bus to MLNDTERT (521180) 2.4 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0841_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to IODINE 4 (520957) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE 4 (520957) 138 kV Bus to FTSUPLY4 (520920) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE 4 (520957) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0842_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to SEILING4 (520553) 138 kV Bus CKT 1 b. 2. Trip branch from SEILING4 (520553) 138 kV Bus to TALOGA 4 (521065) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SEILING4 (520553) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0843_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to ASPEN 4 (520462) 138 kV Bus CKT 1 b. 2. Trip branch from ASPEN 4 (520462) 138 kV Bus to BEARCAT4 (520500) 138 kV Bus CKT 1 b. 3. Trip branch from BEARCAT4 (520500) 138 kV Bus to NINMLTP4 (521128) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ASPEN 4 (520462) 138 kV Bus b. 5. Drop Load 1 at BEARCAT4 (520500) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0844_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to PIC4 (520425) 138 kV Bus CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV Bus to CDRDLTP4 (520848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at PIC4 (520425) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0845_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0846_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0847_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0848_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0849_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0850_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 2. Trip branch from STLN-DEMARC6 (523779) 230 kV Bus to WHEELER 6 (523777) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0854_P1 | 3 phase fault on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LAMAR7 (599950) 345 kV Bus to G18-030-TAP (762662) 345 kV Bus CKT 1 b. 2. Drop Load 1 at LAMAR7 (599950) 345 kV Bus b. 3. Drop Shunt 1 at LAMAR7 (599950) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0855_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to COBRN_CREEK3 (523772) 115 kV Bus CKT 1 b. 2. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus b. 3. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0856_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to HOWARD 3 (523797) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0857_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR11 (524041) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0858_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR21 (524042) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0859_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HUTCHISON 6 (523551) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0860_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0861_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0862_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0863_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to BOWERS 3 (523748) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0864_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0865_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_N 3 (523544) 115 kV Bus to HUTCH_TR1N 1 (523540) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0866_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_S 3 (523546) 115 kV Bus to HUTCH_TR2S 1 (523541) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0867_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0868_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to EAST_PLANT 6 (524163) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0869_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0870_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0871_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0872_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0873_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0874_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to NEWHART 6 (525461) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0875_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0876_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0877_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0878_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to FAIN 3 (523339) 115 kV Bus CKT 1 b. 2. Trip branch from FAIN 3 (523339) 115 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FAIN 3 (523339) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0879_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO 3 (524016) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ASARCO 3 (524016) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0880_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO_TP 3 (524018) 115 kV Bus CKT 1 b. 2. Trip branch from ASARCO_TP 3 (524018) 115 kV Bus to HIGHLAND_TP3 (523931) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0881_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 5. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 6. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0882_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to CAMX/AGR TP3 (523485) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0883_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to HUTCH_S 3 (523546) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0884_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0885_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0886_P1 | 3 phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply Fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAN+TASCOS6 (523869) 230 kV Bus to XIT_INTG 6 (523221) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from XIT_INTG 6 (523221) 230 kV Bus to XIT_INTG 3 (523220) 115 kV Bus to XIT_INTG TR1 (523219) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0887_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to CAMEX/AGRM 3 (523486) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CAMEX/AGRM 3 (523486) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0888_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0889_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0890_P1 | 3 phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138 kV Bus to IODINE-4 (514796) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE-4 (514796) 138 kV Bus to REDCLFT4 (515533) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE-4 (514796) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0891_P4 | a. Apply single phase fault at MOORLND4 (520999) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MOORLND4 (520999) 138 kV to PIC4 (520425) 138 kV CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV to CDRDLTP4 (520848) 138 kV CKT 1 b. 3. Trip branch from CDRDLTP4 (520848) 138 kV to CEDRDAL4 (520507) 138 kV CKT 1 b. 4. Trip branch from CDRDLTP4 (520848) 138 kV to OKEENE 4 (521016) 138 kV CKT 1 b. 5. Trip branch from MOORLND4 (520999) 138 kV to ASPEN 4 (520462) 138 kV CKT 1 b. 6. Trip branch from ASPEN 4 (520462) 138 kV to BEARCAT4 (520500) 138 kV CKT 1 b. 7. Trip branch from BEARCAT4 (520500) 138 kV to NINMLTP4 (521128) 138 kV CKT 1 b. 8. Trip branch from NINMLTP4 (521128) 138 kV to NINMILE4 (520492) 138 kV CKT 1 b. 9. Trip branch from NINMLTP4 (521128) 138 kV to MORWODS4 (521001) 138 kV CKT 1 b. 10. Drop Load 1 CEDRDAL4 (520507) 138 kV b. 11. Drop Load 1 PIC4 (520425) 138 kV b. 12. Drop Load 1 ASPEN 4 (520462) 138 kV b. 13. Drop Load 1 BEARCAT4 (520500) 138 kV b. 14. Drop Load 1 NINMILE4 (520492) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0892_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0893_P1 | 3 phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138 kV Bus to AVARD 4 (520601) 138 kV Bus CKT 1 b. 2. Drop Load 1 at AVARD 4 (520601) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0894_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0895_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0896_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0897_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0898_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD4 (514785) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0899_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to ALVAOGE2 (514792) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0900_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to CZYCRVT2 (515560) 69 kV Bus CKT 1 b. 2. Trip branch from CZYCRVT2 (515560) 69 kV Bus to SALINE 2 (514716) 69 kV Bus CKT 1 b. 3. Trip branch from SALINE 2 (514716) 69 kV Bus to HELENAT2 (515371) 69 kV Bus CKT 1 b. 4. Drop Load 1 at CZYCRVT2 (515560) 69 kV Bus b. 5. Drop Shunt 1 at CZYCRVT2 (515560) 69 kV Bus1 b. 6. Drop Load 1 at SALINE 2 (514716) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0901_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0902_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0903_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODWRD4 (514785) 138 kV Bus to WODWRD 2 (514782) 69 kV Bus to WOODWR21 (515771) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0904_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to MORWODS4 (521001) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0905_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to NINMILE4 (520492) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NINMILE4 (520492) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0906_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0907_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to CURTIS 2 (520480) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CURTIS 2 (520480) 69 kV Bus b. 3. Drop Load 2 at CURTIS 2 (520480) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0908_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALVA 2 (520806) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0909_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALINETP2 (515803) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0910_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0911_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOCOR4 (514778) 138 kV Bus to CLEOPLT4 (515562) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0912_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEOCOR4 (514778) 138 kV Bus to CLEOCOR2 (514777) 69 kV Bus to CLEOCOR1 (515716) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0913_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to OKEENE 4 (521016) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0914_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to CEDRDAL4 (520507) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CEDRDAL4 (520507) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0915_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TALOGA 4 (521065) 138 kV Bus to TALOGA 2 (521064) 69 kV Bus to TLGTERT (521178) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0916_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TALOGA 4 (521065) 138 kV Bus to DEWEY 4 (514787) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0917_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERT (521170) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0918_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERTB (521182) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0919_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0920_P1 | 3 phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOBHIL4 (514795) 138 kV Bus to KNOBHIL2 (514794) 69 kV Bus to KNOBHIL1 (515732) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0921_P1 | 3 phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV Bus to SPERVIL7 (531469) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763895 [G19-058-GEN20.6000]
04 - Southeast | 25S | Transfer | Group4_Fault_0922_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to NEWGRTP2 (514776) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0923_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0924_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to CEDARAV2 (514781) 69 kV Bus CKT 1 b. 2. Trip branch from CEDARAV2 (514781) 69 kV Bus to TANGRTP2 (514775) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CEDARAV2 (514781) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0925_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to SALTPLN4 (520437) 138 kV Bus CKT 1 b. 2. Trip branch from SALTPLN4 (520437) 138 kV Bus to CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 3. Trip branch from CHRKCTY4 (520431) 138 kV Bus to DRIFTWD4 (521200) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SALTPLN4 (520437) 138 kV Bus b. 5. Drop Load 2 at SALTPLN4 (520437) 138 kV Bus b. 6. Drop Load 1 at CHRKCTY4 (520431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0926_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to MORWOOD4 (521002) 138 kV Bus CKT 1 b. 2. Trip branch from MORWOOD4 (521002) 138 kV Bus to BRANTLEY4 (520832) 138 kV Bus CKT 1 b. 3. Trip branch from BRANTLEY4 (520832) 138 kV Bus to DURHAM 4 (520885) 138 kV Bus CKT 1 b. 4. Trip branch from DURHAM 4 (520885) 138 kV Bus to SWEETWR4 (521060) 138 kV Bus CKT 1 b. 5. Trip branch from SWEETWR4 (521060) 138 kV Bus to BULOJ4 (520402) 138 kV Bus CKT 1 b. 6. Trip branch from BULOJ4 (520402) 138 kV Bus to ERICK 4 (520903) 138 kV Bus CKT 1 b. 7. Trip branch from ERICK 4 (520903) 138 kV Bus to SAYRE--4 (511504) 138 kV Bus CKT 1 b. 8. Trip branch from SAYRE--4 (511504) 138 kV Bus to FALCNRD4 (511511) 138 kV Bus CKT 1 b. 9. Trip branch from FALCNRD4 (511511) 138 kV Bus to ELKCTY-4 (511458) 138 kV Bus CKT 1 b. 10. Drop Load 1 at BRANTLEY4 (520832) 138 kV Bus b. 11. Drop Load 1 at DURHAM 4 (520885) 138 kV Bus b. 12. Drop Load 1 at SWEETWR4 (521060) 138 kV Bus b. 13. Drop Load 1 at BULOJ4 (520402) 138 kV Bus b. 14. Drop Load 1 at ERICK 4 (520903) 138 kV Bus b. 15. Drop Load 1 at SAYRE--4 (511504) 138 kV Bus b. 16. Drop Load 1 at FALCNRD4 (511511) 138 kV Bus b. 17. Drop Shunt 1 at SAYRE--4 (511504) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0927_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to ELLIS 4 (511561) 138 kV Bus CKT 1 b. 2. Trip branch from ELLIS 4 (511561) 138 kV Bus to CUSTER 4 (520459) 138 kV Bus CKT 1 b. 3. Trip branch from CUSTER 4 (520459) 138 kV Bus to REDHLSW4 (521116) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ELLIS 4 (511561) 138 kV Bus b. 5. Drop Load 1 at CUSTER 4 (520459) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0928_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MORWODS4 (521001) 138 kV Bus to MORWODS2 (521000) 69 kV Bus to MRWDTERT (521172) 13.8 kV Bus CKT 1 b. 2. Trip branch from MORWODS2 (521000) 69 kV Bus to BTLRJCT2 (520457) 69 kV Bus CKT 1 b. 3. Trip branch from BTLRJCT2 (520457) 69 kV Bus to BUTLER 2 (520458) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0929_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to FARGOJCT2 (521196) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0930_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to VICI 2 (521082) 69 kV Bus CKT 1 b. 2. Trip branch from VICI 2 (521082) 69 kV Bus to TALOGA 2 (521064) 69 kV Bus CKT 1 b. 3. Drop Load 1 at VICI 2 (521082) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0931_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRIFTWD4 (521200) 138 kV Bus to DRIFTWD2 (521201) 69 kV Bus to DRFTWDTERT (521185) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0932_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138 kV Bus to BYRONTP4 (520432) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0933_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to CLEO PL4 (515553) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO PL4 (515553) 138 kV Bus b. 3. Drop Shunt 1 at CLEO PL4 (515553) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0934_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to MENOTAP4 (514789) 138 kV Bus CKT 1 b. 2. Trip branch from MENOTAP4 (514789) 138 kV Bus to IMO 4 (514790) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MENOTAP4 (514789) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0935_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0936_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to ALINE 2 (514793) 69 kV Bus CKT 1 b. 2. Drop Load 1 at ALINE 2 (514793) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0937_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to CLEOTP 2 (515804) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0938_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEOCOR2 (514777) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0939_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEO 2 (514791) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO 2 (514791) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0940_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTBJ2 (521202) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTBJ2 (521202) 69 kV Bus to MEDLDGE2 (522396) 69 kV Bus CKT 1 b. 3. Trip branch from MEDLDGE2 (522396) 69 kV Bus to HAZELTN2 (520937) 69 kV Bus CKT 1 b. 4. Drop Load 1 at MEDLDGE2 (522396) 69 kV Bus b. 5. Drop Load 1 at HAZELTN2 (520937) 69 kV Bus b. 6. Drop Shunt 1 at HAZELTN2 (520937) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0941_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTAJ2 (520938) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTAJ2 (520938) 69 kV Bus to BRLNGTN2 (520833) 69 kV Bus CKT 1 b. 3. Trip branch from BRLNGTN2 (520833) 69 kV Bus to CHEROKS2 (520851) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BRLNGTN2 (520833) 69 kV Bus b. 5. Drop Load 2K at BRLNGTN2 (520833) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0942_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to WILKINS4 (514950) 138 kV Bus CKT 1 b. 2. Trip branch from WILKINS4 (514950) 138 kV Bus to OAKTRET4 (514930) 138 kV Bus CKT 1 b. 3. Trip branch from OAKTRET4 (514930) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Drop Load 1 at WILKINS4 (514950) 138 kV Bus b. 5. Drop Load 1 at OAKTRET4 (514930) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0943_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to OUBROOK4 (514903) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OUBROOK4 (514903) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0944_P1 | 3 phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply Fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from QUAILCK4 (514851) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0945_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to WRAIRPT4 (514889) 138 kV Bus CKT 1 b. 2. Trip branch from WRAIRPT4 (514889) 138 kV Bus to 36&MER 4 (514888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WRAIRPT4 (514889) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0946_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to SANTAFE4 (514926) 138 kV Bus CKT 1 b. 2. Trip branch from SANTAFE4 (514926) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SANTAFE4 (514926) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0947_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENN 4 (514925) 138 kV Bus to PENN 2 (514924) 69 kV Bus to PENN 1 (515751) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0948_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to TUTCONT4 (511425) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0949_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to EL-RENO4 (514819) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0950_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0951_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to HAYMAKR4 (514863) 138 kV Bus CKT 1 b. 2. Trip branch from HAYMAKR4 (514863) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HAYMAKR4 (514863) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0952_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to SARA 4 (514895) 138 kV Bus CKT 1 b. 2. Trip branch from SARA 4 (514895) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SARA 4 (514895) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0953_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to CZECHAL4 (514894) 138 kV Bus CKT 1 b. 2. Trip branch from CZECHAL4 (514894) 138 kV Bus to XEROX 4 (514893) 138 kV Bus CKT 1 b. 3. Trip branch from XEROX 4 (514893) 138 kV Bus to MORGAN 4 (514896) 138 kV Bus CKT 1 b. 4. Trip branch from MORGAN 4 (514896) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 b. 5. Drop Load 1 at CZECHAL4 (514894) 138 kV Bus b. 6. Drop Load 1 at XEROX 4 (514893) 138 kV Bus b. 7. Drop Load 1 at MORGAN 4 (514896) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0954_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0955_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to PIEDMNT4 (514864) 138 kV Bus CKT 1 b. 2. Trip branch from PIEDMNT4 (514864) 138 kV Bus to RICHRDS4 (514862) 138 kV Bus CKT 1 b. 3. Trip branch from RICHRDS4 (514862) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PIEDMNT4 (514864) 138 kV Bus b. 5. Drop Load 1 at RICHRDS4 (514862) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0956_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to LNEOAK 4 (514873) 138 kV Bus CKT 1 b. 2. Trip branch from LNEOAK 4 (514873) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LNEOAK 4 (514873) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0957_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to HOLLYWD4 (514953) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0958_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0959_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to TURNER 4 (514992) 138 kV Bus CKT 1 b. 2. Trip branch from TURNER 4 (514992) 138 kV Bus to SOGATE 4 (514928) 138 kV Bus CKT 1 b. 3. Trip branch from SOGATE 4 (514928) 138 kV Bus to SW134TP4 (514876) 138 kV Bus CKT 1 b. 4. Drop Load 1 at TURNER 4 (514992) 138 kV Bus b. 5. Drop Load 1 at SOGATE 4 (514928) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0960_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to CHERYCK4 (514957) 138 kV Bus CKT 1 b. 2. Trip branch from CHERYCK4 (514957) 138 kV Bus to BOYD 4 (514958) 138 kV Bus CKT 1 b. 3. Trip branch from BOYD 4 (514958) 138 kV Bus to CEDARLN4 (514948) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHERYCK4 (514957) 138 kV Bus b. 5. Drop Load 1 at BOYD 4 (514958) 138 kV Bus b. 6. Drop Shunt 1 at BOYD 4 (514958) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0961_P1 | 3 phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDBUD 7 (514909) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0962_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0963_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to INDNHIL4 (514954) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0964_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to STUBMAN4 (514952) 138 kV Bus CKT 1 b. 2. Trip branch from STUBMAN4 (514952) 138 kV Bus to MLENIUM4 (514932) 138 kV Bus CKT 1 b. 3. Trip branch from MLENIUM4 (514932) 138 kV Bus to OU TAP 4 (514931) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STUBMAN4 (514952) 138 kV Bus b. 5. Drop Load 1 at MLENIUM4 (514932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0965_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0966_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to WESTHSE4 (514904) 138 kV Bus CKT 1 b. 2. Drop Load 1 at WESTHSE4 (514904) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0967_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to INDIANH4 (515380) 138 kV Bus CKT 1 b. 2. Trip branch from INDIANH4 (515380) 138 kV Bus to MOORE 4 (514955) 138 kV Bus CKT 1 b. 3. Trip branch from MOORE 4 (514955) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 4. Drop Load 1 at INDIANH4 (515380) 138 kV Bus b. 5. Drop Load 1 at MOORE 4 (514955) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0968_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0969_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to LAKESID4 (514849) 138 kV Bus CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV Bus to HEFNER 4 (514848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LAKESID4 (514849) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0970_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to G17-152_TAP (914902) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0971_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to WESTMOR4 (514887) 138 kV Bus CKT 1 b. 2. Trip branch from WESTMOR4 (514887) 138 kV Bus to PENN 4 (514925) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WESTMOR4 (514887) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0972_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to TUTTLE4 (511501) 138 kV Bus CKT 1 b. 2. Trip branch from TUTTLE4 (511501) 138 kV Bus to LEONARD4 (511575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at TUTTLE4 (511501) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0973_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to CEMRD_TP4 (511576) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0974_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to T-CONCO4 (511424) 138 kV Bus CKT 1 b. 2. Drop Load 1 at T-CONCO4 (511424) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0975_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to CMTRYRD4 (515864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CMTRYRD4 (515864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0976_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0977_P1 | 3 phase fault on JENSENT4 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JENSENT4 (514820) 138 kV Bus to JENSEN 4 (514821) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0978_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to OMEGA 4 (515962) 138 kV Bus CKT 1 b. 2. Trip branch from OMEGA 4 (515962) 138 kV Bus to ROMNOSE4 (514823) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OMEGA 4 (515962) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0979_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EL-RENO4 (514819) 138 kV Bus to ELRENO 2 (514818) 69 kV Bus to EL RENO1 (515722) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0980_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to JNSKAMO4 (514906) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0981_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to RNDBARN4 (515461) 138 kV Bus CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV Bus to BURGETT4 (514510) 138 kV Bus CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 b. 4. Drop Load 1 at RNDBARN4 (515461) 138 kV Bus b. 5. Drop Load 1 at BURGETT4 (514510) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0982_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to LGARBER4 (515465) 138 kV Bus CKT 1 b. 2. Trip branch from LGARBER4 (515465) 138 kV Bus to CHTWOOD4 (514842) 138 kV Bus CKT 1 b. 3. Trip branch from CHTWOOD4 (514842) 138 kV Bus to JONESSB4 (515480) 138 kV Bus CKT 1 b. 4. Drop Load 1 at LGARBER4 (515465) 138 kV Bus b. 5. Drop Load 1 at CHTWOOD4 (514842) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0983_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to BARNES 4 (515003) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0984_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0985_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0986_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to GM 4 (514961) 138 kV Bus CKT 1 b. 2. Trip branch from GM 4 (514961) 138 kV Bus to AIRDEPT4 (515457) 138 kV Bus CKT 1 b. 3. Trip branch from AIRDEPT4 (515457) 138 kV Bus to WILDMRY4 (514984) 138 kV Bus CKT 1 b. 4. Trip branch from WILDMRY4 (514984) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 5. Drop Load 1 at GM 4 (514961) 138 kV Bus b. 6. Drop Load 1 at AIRDEPT4 (515457) 138 kV Bus b. 7. Drop Load 1 at WILDMRY4 (514984) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0987_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from R.S.S.-7 (509782) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0989_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T1 4 (509773) 138 kV Bus to RSST1 T1 (509882) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T1 4 (509773) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0990_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T2 4 (509875) 138 kV Bus to RSST2 T1 (509876) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T2 4 (509875) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0991_P1 | 3 phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply Fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FRNKLNS4 (520917) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0992_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to DAYTON 4 (514892) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0993_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to SW 5TH 4 (514920) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0994_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to COUNCIL4 (514865) 138 kV Bus CKT 1 b. 2. Trip branch from COUNCIL4 (514865) 138 kV Bus to WESTOAK4 (514866) 138 kV Bus CKT 1 b. 3. Trip branch from WESTOAK4 (514866) 138 kV Bus to MERIDAN4 (514867) 138 kV Bus CKT 1 b. 4. Trip branch from MERIDAN4 (514867) 138 kV Bus to DOUGLTP4 (514868) 138 kV Bus CKT 1 b. 5. Drop Load 1 at COUNCIL4 (514865) 138 kV Bus b. 6. Drop Load 1 at WESTOAK4 (514866) 138 kV Bus b. 7. Drop Load 1 at MERIDAN4 (514867) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0995_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MUSTANG4 (514861) 138 kV Bus to MSTANG 2 (514860) 69 kV Bus to MUSTANG1 (515740) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0996_P1 | 3 phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply Fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARAUTO2 (508576) 69 kV Bus to MARSHAL2 (508556) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0997_P1 | 3 phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply Fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JEFFRSN4 (508835) 138 kV Bus to LAKEPIN4 (509624) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0998_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to HARRISN4 (508544) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0999_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to NMINEOL4 (508349) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1000_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to REDSPRW4 (508366) 138 kV Bus CKT 1 b. 2. Trip branch from REDSPRW4 (508366) 138 kV Bus to PECANHL4 (508365) 138 kV Bus CKT 1 b. 3. Trip branch from PECANHL4 (508365) 138 kV Bus to GARDVAL4 (508364) 138 kV Bus CKT 1 b. 4. Trip branch from GARDVAL4 (508364) 138 kV Bus to KENSULI4 (508363) 138 kV Bus CKT 1 b. 5. Trip branch from KENSULI4 (508363) 138 kV Bus to BENWHEL4 (508362) 138 kV Bus CKT 1 b. 6. Trip branch from BENWHEL4 (508362) 138 kV Bus to STARR 4 (508361) 138 kV Bus CKT 1 b. 7. Trip branch from STARR 4 (508361) 138 kV Bus to EBURGES4 (508360) 138 kV Bus CKT 1 b. 8. Trip branch from EBURGES4 (508360) 138 kV Bus to BURGEST4 (508357) 138 kV Bus CKT 1 b. 9. Drop Load 1 at REDSPRW4 (508366) 138 kV Bus b. 10. Drop Load 1 at PECANHL4 (508365) 138 kV Bus b. 11. Drop Load 1 at GARDVAL4 (508364) 138 kV Bus b. 12. Drop Load 1 at KENSULI4 (508363) 138 kV Bus b. 13. Drop Load 1 at BENWHEL4 (508362) 138 kV Bus b. 14. Drop Load 1 at STARR 4 (508361) 138 kV Bus b. 15. Drop Load 1 at EBURGES4 (508360) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1001_P1 | 3 phase fault on BURGEST4 (508357) 138 kV Bus a. Apply Fault at the BURGEST4 (508357) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BURGEST4 (508357) 138 kV Bus to MORTONST 4 (508373) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1002_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to (763010) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1003_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to SOTXEST4 (508570) 138 kV Bus CKT 1 b. 2. Trip branch from SOTXEST4 (508570) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SOTXEST4 (508570) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1004_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOXLEE4 (508548) 138 kV Bus to KNOXLEE2 (508547) 69 kV Bus to KXLEE-1 (508584) 12.47 kV Bus CKT 1 b. 2. Trip branch from KNOXLEE2 (508547) 69 kV Bus to SELONGV2 (508568) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1005_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN1-1 (509095) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1006_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN2-1 (509096) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1007_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to MONROCR2 (508558) 69 kV Bus CKT 1 b. 2. Trip branch from MONROCR2 (508558) 69 kV Bus to WHITNEY2 (508574) 69 kV Bus CKT 1 b. 3. Drop Load 1 at MONROCR2 (508558) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1008_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to HOWELL 2 (508545) 69 kV Bus CKT 1 b. 2. Trip branch from HOWELL 2 (508545) 69 kV Bus to SABINE 2 (508565) 69 kV Bus CKT 1 b. 3. Trip branch from SABINE 2 (508565) 69 kV Bus to SPIPETP2 (508573) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HOWELL 2 (508545) 69 kV Bus b. 5. Drop Load 1 at SABINE 2 (508565) 69 kV Bus b. 6. Drop Shunt 1 at HOWELL 2 (508545) 69 kV Bus1 b. 7. Drop Shunt 1 at SABINE 2 (508565) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1009_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON1-1 (509097) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1010_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to SVCPIPE2 (508578) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SVCPIPE2 (508578) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1011_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to CLARKSV2 (508540) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1012_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1013_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1014_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON2-1 (509098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1015_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1016_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1017_P1 | 3 phase fault on LIBCYTP4 (508550) 138 kV Bus a. Apply Fault at the LIBCYTP4 (508550) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIBCYTP4 (508550) 138 kV Bus to LIBCITY4 (508535) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LIBCITY4 (508535) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1018_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL1-1 (509090) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1019_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL2-1 (509091) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1020_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL4 (509083) 138 kV Bus to NEWPROS4 (509102) 138 kV Bus CKT 1 b. 2. Trip branch from NEWPROS4 (509102) 138 kV Bus to CARTPOD4 (509057) 138 kV Bus CKT 1 b. 3. Trip branch from CARTPOD4 (509057) 138 kV Bus to HULLTAP4 (509099) 138 kV Bus CKT 1 b. 4. Trip branch from HULLTAP4 (509099) 138 kV Bus to CARTHGT4 (509060) 138 kV Bus CKT 1 b. 5. Drop Load 1 at NEWPROS4 (509102) 138 kV Bus b. 6. Drop Load 1 at CARTPOD4 (509057) 138 kV Bus b. 7. Drop Load 1 at HULLTAP4 (509099) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1021_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to BIG3TAP2 (508539) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1022_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1023_P1 | 3 phase fault on G19-065-TAP (763010) kV Bus a. Apply Fault at the G19-065-TAP (763010) kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) kV Bus to LONDON 4 (509072) 138 kV Bus CKT 1 b. 2. Trip branch from LONDON 4 (509072) 138 kV Bus to FRIARSW4 (509062) 138 kV Bus CKT 1 b. 3. Trip branch from FRIARSW4 (509062) 138 kV Bus to FRIRSWR4 (509063) 138 kV Bus CKT 1 b. 4. Trip branch from FRIRSWR4 (509063) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LONDON 4 (509072) 138 kV Bus b. 6. Drop Load 1 at FRIARSW4 (509062) 138 kV Bus b. 7. Drop Load 1 at FRIRSWR4 (509063) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1024_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to EVENSID2 (509061) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1025_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1026_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1027_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to LEVERET4 (509069) 138 kV Bus CKT 1 b. 2. Trip branch from LEVERET4 (509069) 138 kV Bus to KILGORR4 (509067) 138 kV Bus CKT 1 b. 3. Trip branch from KILGORR4 (509067) 138 kV Bus to MONROER4 (509073) 138 kV Bus CKT 1 b. 4. Trip branch from MONROER4 (509073) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LEVERET4 (509069) 138 kV Bus b. 6. Drop Load 1 at KILGORR4 (509067) 138 kV Bus b. 7. Drop Load 1 at MONROER4 (509073) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1028_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1029_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVUE2 (508555) 69 kV Bus CKT 1 b. 2. Trip branch from LONGVUE2 (508555) 69 kV Bus to GATES 2 (508541) 69 kV Bus CKT 1 b. 3. Trip branch from GATES 2 (508541) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 b. 4. Drop Load 1 at LONGVUE2 (508555) 69 kV Bus b. 5. Drop Shunt 1 at LONGVUE2 (508555) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1030_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to KILGORE2 (508546) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1031_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes